04 - Southeast | 25W | Transfer | MARSHL_4__JEFFRSN4_7 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MARSHL_4__MARSHAL4_7 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MARSHL_4__PIRKEY_4_7 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO PIRKEY 4 138.0 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NORTWST7__MATHWSN7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | MATHWSN7__TRAVERSE3_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MCARBDE4__G20_092_TAP_7 | 3 Phase fault on MCARBDE4 (510366) 138 kV Bus a. Apply fault at the MCARBDE4 (510366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 138.0 KV 510366 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MCARBDE4__PRY_CRK4_7 | 3 Phase fault on MCARBDE4 (510366) 138 kV Bus a. Apply fault at the MCARBDE4 (510366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 138.0 KV 510366 TO PRY_CRK4 138.0 KV 510431 CKT 1 b.2. LOAD 1 510431 b.3. EXCLART4 138.0 KV 510401 TO PRY_CRK4 138.0 KV 510431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MCNAB_____3__TURK___3_7 | 3 Phase fault on MCNAB 3 (504122) 115 kV Bus a. Apply fault at the MCNAB 3 (504122) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCNAB 3 115.0 KV 504122 TO TURK 3 115.0 KV 507456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MDCPRK4__CACHEJ4_7 | 3 Phase fault on MDCPRK4 (520404) 138 kV Bus a. Apply fault at the MDCPRK4 (520404) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MDCPRK4 138.0 KV 520404 TO CACHEJ4 138.0 KV 521190 CKT 1 b.2. MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 b.3. LOAD 1 521024 b.4. PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MENOTAP4__IMO____4_7 | 3 Phase fault on MENOTAP4 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1 b.2. LOAD 1 514790 b.3. MENOTAP4 138.0 KV 514789 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MILLCKT4__SXMLCKT4_7 | 3 Phase fault on MILLCKT4 (515121) 138 kV Bus a. Apply fault at the MILLCKT4 (515121) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MILLERT4__SOONER_4_7 | 3 Phase fault on MILLERT4 (514704) 138 kV Bus a. Apply fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 138.0 KV 514704 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MINCO__7__CIMARON7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MINCO__7__GEN_2017_233_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MINCO__7__GRACMNT7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MINCO__7__MCNOWND7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MINCO__7__MNCWND37_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MINCO__7__NORMHLL7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MINCO__7__NSUB345_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MNCWND37__MNCWND47_6 | 3 Phase fault on MNCWND37 (515549) 345 kV Bus a. Apply fault at the MNCWND37 (515549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND37 345.0 KV 515549 TO MNCWND47 345.0 KV 515939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MOORLND2__CRTSJCT2_7 | 3 Phase fault on MOORLND2 (520995) 69 kV Bus a. Apply fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND2 69.0 KV 520995 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MOORLND4__GEN_2016_020_7 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MORWODS4__MORWOOD4_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 138.0 KV 521001 TO MORWOOD4 138.0 KV 521002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MORWODS4__NINMLTP4_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 138.0 KV 521001 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MRIETA_2__ROCKYPT4_7 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 b.2. MRIETA 2 138.0 KV 515160 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MRIETA_4__MARIETA4_7 | 3 Phase fault on MRIETA 4 (520455) 138 kV Bus a. Apply fault at the MRIETA 4 (520455) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 4 138.0 KV 520455 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MTNVIEW2__MTNVWTP2_7 | 3 Phase fault on MTNVIEW2 (520490) 69 kV Bus a. Apply fault at the MTNVIEW2 (520490) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTNVIEW2 69.0 KV 520490 TO MTNVWTP2 69.0 KV 521003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MTNVWTP2__PINERTP2_7 | 3 Phase fault on MTNVWTP2 (521003) 69 kV Bus a. Apply fault at the MTNVWTP2 (521003) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTNVWTP2 69.0 KV 521003 TO PINERTP2 69.0 KV 521027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MUNZCTY4__DUGLASV4_7 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO DUGLASV4 138.0 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MUNZCTY4__WILKES_4_7 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NASH___4__ALUMAX_4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO ALUMAX 4 138.0 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NASH___4__BANN___4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO BANN 4 138.0 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NASH___4__NWTXARK4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NAVAJO_2__NAVJOTP2_7 | 3 Phase fault on NAVAJO 2 (520491) 69 kV Bus a. Apply fault at the NAVAJO 2 (520491) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAVAJO 2 69.0 KV 520491 TO NAVJOTP2 69.0 KV 521009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NEO184_5__NOL435_5_7 | 3 Phase fault on NEO184 5 (547471) 161 kV Bus a. Apply fault at the NEO184 5 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 161.0 KV 547471 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NEO_SPA5__NEO184_5_7 | 3 Phase fault on NEO SPA5 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 161.0 KV 505486 TO NEO184 5 161.0 KV 547471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NEWBOST2__NNBOSTN2_7 | 3 Phase fault on NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69.0 KV 508067 TO NNBOSTN2 69.0 KV 508068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NEWGRTP2__WODWRD_2_7 | 3 Phase fault on NEWGRTP2 (514776) 69 kV Bus a. Apply fault at the NEWGRTP2 (514776) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWGRTP2 69.0 KV 514776 TO WODWRD 2 69.0 KV 514782 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NE_ENID4__ENIDINT4_7 | 3 Phase fault on NE ENID4 (514769) 138 kV Bus a. Apply fault at the NE ENID4 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 138.0 KV 514769 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NINMILE4__NINMLTP4_7 | 3 Phase fault on NINMILE4 (520492) 138 kV Bus a. Apply fault at the NINMILE4 (520492) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NINMILE4 138.0 KV 520492 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NKNGFSH4__DOVERSW4_7 | 3 Phase fault on NKNGFSH4 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NNBOSTN4__G18_003_TAP_7 | 3 Phase fault on NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NOL435_2__GRA700_2_7 | 3 Phase fault on NOL435 2 (547610) 69 kV Bus a. Apply fault at the NOL435 2 (547610) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 2 69.0 KV 547610 TO GRA700 2 69.0 KV 547617 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NOL443_2__NOL435_2_7 | 3 Phase fault on NOL443 2 (547561) 69 kV Bus a. Apply fault at the NOL443 2 (547561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL443 2 69.0 KV 547561 TO NOL435 2 69.0 KV 547610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NORAM__4__LONGWD_4_7 | 3 Phase fault on NORAM 4 (507774) 138 kV Bus a. Apply fault at the NORAM 4 (507774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORAM 4 138.0 KV 507774 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NORTWST7__ARCADIA7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | NORTWST7__CIMARON7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MATHWSN7__REDNGTN7_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | NORTWST7__SPRNGCK7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | NWTXARK4__SUGARHL4_7 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138.0 KV 508071 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NWTXARK7__G20_020_TAP_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NWTXARK7__LYDIA__7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NWTXARK7__WELSH__7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NWTXARK7__WILKES_7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NWT_BNT4__G18_003_TAP_7 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NWT_BNT4__NWTXARK4_7 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | O.K.U._7__G18_092_PROX_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-092-PROX 345.0 KV 763215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | O.K.U._7__G20_009_TAP_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | O.K.U._7__GEN_2017_033_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | O.K.U._7__OKLAUN_HVDC7_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OKAY___4__TURK___4_7 | 3 Phase fault on OKAY 4 (507428) 138 kV Bus a. Apply fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 4 138.0 KV 507428 TO TURK 4 138.0 KV 507454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OTTER__4__ARMFTWD4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO ARMFTWD4 138.0 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OTTER__4__WOODRNG4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OTTER__4__WRVALLY4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OVERTON4__JACKSNV4_7 | 3 Phase fault on OVERTON4 (509080) 138 kV Bus a. Apply fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OVERTON4 138.0 KV 509080 TO JACKSNV4 138.0 KV 509242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PATTERS4__NWTXARK4_7 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PATTERS4__SNASHVL4_7 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO SNASHVL4 138.0 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PCP_TAP2__PRYORC12_7 | 3 Phase fault on PCP-TAP2 (510408) 69 kV Bus a. Apply fault at the PCP-TAP2 (510408) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCP-TAP2 69.0 KV 510408 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PERDUE_4__DIANA__4_7 | 3 Phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERDUE 4 138.0 KV 508351 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PERRY__4__SOONER_4_7 | 3 Phase fault on PERRY 4 (514707) 138 kV Bus a. Apply fault at the PERRY 4 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRY 4 138.0 KV 514707 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PETTY__4__CHAPELH4_7 | 3 Phase fault on PETTY 4 (508310) 138 kV Bus a. Apply fault at the PETTY 4 (508310) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138.0 KV 508310 TO CHAPELH4 138.0 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIC4__CDRDLTP4_7 | 3 Phase fault on PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138.0 KV 520425 TO CDRDLTP4 138.0 KV 520848 CKT 1 b.2. PIC4 138.0 KV 520425 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PINTAIL7__KINGWD_7_6 | 3 Phase fault on PINTAIL7 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345.0 KV 516010 TO KINGWD 7 345.0 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIRKEY_4__HALLSVLS4_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO HALLSVLS4 138.0 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138.0 KV 508575 TO HALLSVLS4 138.0 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIRKEY_4__SABMINT4_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO SABMINT4 138.0 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIRKEY_7__DIANA__7_6 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIRKEY_7__LEBROCK7_6 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PITTSB_7__C_RIVER7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PITTSB_7__GEN_2018_082_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO GEN-2018-082 345.0 KV 763131 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PITTSB_7__JOHNCO_7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 - Southeast | 25W | Transfer | PITTSB_7__KIOWA__7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PITTSB_7__SEMINOL7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PITTSB_7__VALIANT7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 - Southeast | 25W | Transfer | POCASET4__TUTLETP4_7 | 3 Phase fault on POCASET4 (521031) 138 kV Bus a. Apply fault at the POCASET4 (521031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 138.0 KV 521031 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | POOLVIL4__CARTRCO4_7 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | POTTER_CO__7__SPNSPUR_WND7_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | POTTER_CO__7__TOLK_______7_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PRICESF4__HONEYCK4_7 | 3 Phase fault on PRICESF4 (514814) 138 kV Bus a. Apply fault at the PRICESF4 (514814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRICESF4 138.0 KV 514814 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PRYORC32__PRYORC12_7 | 3 Phase fault on PRYORC32 (512622) 69 kV Bus a. Apply fault at the PRYORC32 (512622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRYORC32 69.0 KV 512622 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PRY_JCT2__PRYORC12_7 | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 69.0 KV 510400 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PRY_JCT4__G20_092_TAP_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 138.0 KV 510419 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PRY_JCT4__GEN_2017_074_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 138.0 KV 510419 TO GEN-2017-074 138.0 KV 589120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RANCHRD7__FRNTWND7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNTWND7 345.0 KV 515688 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RANCHRD7__G18_071_TAP_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO G18-071_TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RANCHRD7__OMCDLEC7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OMCDLEC7 345.0 KV 529200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RANCHRD7__OPENSKY7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OPENSKY7 345.0 KV 515621 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RANDLET4__GRNDFLD4_7 | 3 Phase fault on RANDLET4 (520602) 138 kV Bus a. Apply fault at the RANDLET4 (520602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDLET4 138.0 KV 520602 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RATLIFF4__CARTRCO4_7 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDCLFT4__REDCLF_4_7 | 3 Phase fault on REDCLFT4 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138.0 KV 515533 TO REDCLF 4 138.0 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDHLSW4__RHWIND_4_7 | 3 Phase fault on REDHLSW4 (521116) 138 kV Bus a. Apply fault at the REDHLSW4 (521116) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDHLSW4 138.0 KV 521116 TO RHWIND 4 138.0 KV 521117 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDNGTN7__REDDIRT7_6 | 3 Phase fault on REDNGTN7 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 345.0 KV 515875 TO REDDIRT7 345.0 KV 515877 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDSPRG4__EYLAU__4_7 | 3 Phase fault on REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDSPRG4 138.0 KV 508075 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDWATR4__EYLAU__4_7 | 3 Phase fault on REDWATR4 (509654) 138 kV Bus a. Apply fault at the REDWATR4 (509654) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWATR4 138.0 KV 509654 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RENFROW4__GRANTCO4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO GRANTCO4 138.0 KV 515546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RENFROW4__MDFRDTP4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO MDFRDTP4 138.0 KV 515569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RENFROW4__WFEC_RNFRO4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO WFEC_RNFRO4 138.0 KV 520409 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RENFROW7__G18_128_TAP_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RENFROW7__GEN_2017_203_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GEN-2017-203 345.0 KV 760809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RENFROW7__GRNTWD_7_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GRNTWD 7 345.0 KV 515646 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ROCKYPT2__SCMMRCT2_7 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 69.0 KV 515163 TO SCMMRCT2 69.0 KV 515420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ROCKYPT4__SPRNDAL4_7 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | ROMNOSE4__GEARYTP4_7 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ROMNOSE4__OMEGA__4_7 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO OMEGA 4 138.0 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ROSVTAP2__HOBART_2_7 | 3 Phase fault on ROSVTAP2 (511444) 69 kV Bus a. Apply fault at the ROSVTAP2 (511444) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSVTAP2 69.0 KV 511444 TO HOBART-2 69.0 KV 511465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ROSVTAP2__TOMSTEED2_7 | 3 Phase fault on ROSVTAP2 (511444) 69 kV Bus a. Apply fault at the ROSVTAP2 (511444) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSVTAP2 69.0 KV 511444 TO TOMSTEED2 69.0 KV 511495 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RUSHSPR7__GEN_2015_092_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2015-092 345.0 KV 563259 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RUSHSPR7__GEN_2018_055_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | RUSHSPT4__SANTAFE4_7 | 3 Phase fault on RUSHSPT4 (511491) 138 kV Bus a. Apply fault at the RUSHSPT4 (511491) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSPT4 138.0 KV 511491 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RUSHSP_4__RUSHSPT4_7 | 3 Phase fault on RUSHSP 4 (511426) 138 kV Bus a. Apply fault at the RUSHSP 4 (511426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSP 4 138.0 KV 511426 TO RUSHSPT4 138.0 KV 511491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RUSSELL2__OMMANGM2_7 | 3 Phase fault on RUSSELL2 (521042) 69 kV Bus a. Apply fault at the RUSSELL2 (521042) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL2 69.0 KV 521042 TO OMMANGM2 69.0 KV 529342 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RUSSELL2__VERNON_2_7 | 3 Phase fault on RUSSELL2 (521042) 69 kV Bus a. Apply fault at the RUSSELL2 (521042) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL2 69.0 KV 521042 TO VERNON 2 69.0 KV 521081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RUSSET_4__GLASSES4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO GLASSES4 138.0 KV 515147 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RUSSET_4__RUSSETT4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RUSSET_4__STIRLNG4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO STIRLNG4 138.0 KV 515932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | R_AMOCO2__ROSVTAP2_7 | 3 Phase fault on R-AMOCO2 (511432) 69 kV Bus a. Apply fault at the R-AMOCO2 (511432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R-AMOCO2 69.0 KV 511432 TO ROSVTAP2 69.0 KV 511444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SABMINT4__SABINEM4_7 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SABINEM4 138.0 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 - Southeast | 25W | Transfer | SABMINT4__SEMRSHL4_7 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SEMRSHL4 138.0 KV 508569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SCOTTSV4__LONGWD_4_7 | 3 Phase fault on SCOTTSV4 (508567) 138 kV Bus a. Apply fault at the SCOTTSV4 (508567) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SEILING4__G20_010_TAP_7 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SEILING4__MOORLND4_7 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SEMINOL7__G17_092_TAP_6 | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO G17-092-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SEQUOYAHJ4__ANADARK4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SEQUOYAHJ4__CKSHATP4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SEQUOYAHJ4__SEQOYAH4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO SEQOYAH4 138.0 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SFOREMAN__4__NNBOSTN4_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO NNBOSTN4 138.0 KV 508069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SFOREMAN__4__PATTERS4_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SHERID4__ARTVLTP4_7 | 3 Phase fault on SHERID4 (511474) 138 kV Bus a. Apply fault at the SHERID4 (511474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SKELTON7__GEN_2016_128_6 | 3 Phase fault on SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 345.0 KV 515990 TO GEN-2016-128 345.0 KV 588190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNRPMPT4__SOONER_4_7 | 3 Phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 138.0 KV 514798 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_2__TIPTONJ2_7 | 3 Phase fault on SNYDER 2 (521051) 69 kV Bus a. Apply fault at the SNYDER 2 (521051) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 2 69.0 KV 521051 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_2__TOMSTEED2_7 | 3 Phase fault on SNYDER-2 (511475) 69 kV Bus a. Apply fault at the SNYDER-2 (511475) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-2 69.0 KV 511475 TO TOMSTEED2 69.0 KV 511495 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_4__G17_036_TAP_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO G17-036_TAP 138.0 KV 588779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_4__G20_012_TAP_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_4__G20_016_TAP_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4 (521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 138.0 KV 521052 TO G20-016-TAP 138.0 KV 764505 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_4__GEN_2015_013_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4 (521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 138.0 KV 521052 TO GEN-2015-013 138.0 KV 562683 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_4__SNYDER_4_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO SNYDER 4 138.0 KV 521052 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDRSB2__NAVJOTP2_7 | 3 Phase fault on SNYDRSB2 (520541) 69 kV Bus a. Apply fault at the SNYDRSB2 (520541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDRSB2 69.0 KV 520541 TO NAVJOTP2 69.0 KV 521009 CKT 1 b.2. SNYDRSB2 69.0 KV 520541 TO SNYDER 2 69.0 KV 521051 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SO4TH__2__CHSTNTT2_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 69.0 KV 514730 TO CHSTNTT2 69.0 KV 515456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SO4TH__4__BRECKNR4_7 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SO4TH__4__IMO____4_7 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SOONER_4__MORISNT4_7 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 138.0 KV 514802 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MATHWSN7__REDNGTN7_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | SOONER_7__G16_119_TAP_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CIMARON7__MATHWSN7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CIMARON7__MATHWSN7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SOONER_7__THUNDER7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO THUNDER7 345.0 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SOUTHRD4__CANTNLK4_7 | 3 Phase fault on SOUTHRD4 (514822) 138 kV Bus a. Apply fault at the SOUTHRD4 (514822) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHRD4 138.0 KV 514822 TO CANTNLK4 138.0 KV 515964 CKT 1 b.2. LOAD 1 515964 b.3. DEWEY 4 138.0 KV 514787 TO CANTNLK4 138.0 KV 515964 CKT 1 b.4. LOAD 1 515964 b.5. SOUTHRD4 138.0 KV 514822 TO ROMNOSE4 138.0 KV 514823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SPNKY_CK4__CATOOSA4_7 | 3 Phase fault on SPNKY CK4 (509722) 138 kV Bus a. Apply fault at the SPNKY CK4 (509722) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNKY CK4 138.0 KV 509722 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SPPMAINBUS__WELSH__7_6 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SPRHILL4__DIANA__4_7 | 3 Phase fault on SPRHILL4 (508571) 138 kV Bus a. Apply fault at the SPRHILL4 (508571) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRHILL4 138.0 KV 508571 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SPRNDAL4__DRPSPRG4_7 | 3 Phase fault on SPRNDAL4 (515172) 138 kV Bus a. Apply fault at the SPRNDAL4 (515172) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SPRNGCK7__G16_119_TAP_6 | 3 Phase fault on SPRNGCK7 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 345.0 KV 514881 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | STALOGA2__TALOGA_2_7 | 3 Phase fault on STALOGA2 (520454) 69 kV Bus a. Apply fault at the STALOGA2 (520454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 b.2. STALOGA2 69.0 KV 520454 TO PUTNAM 2 69.0 KV 521033 CKT 1 b.3. LOAD 1 521033 b.4. HM-BTTP2 69.0 KV 520942 TO PUTNAM 2 69.0 KV 521033 CKT 1 b.5. LOAD 1 521033 b.6. ARAPAHO2 69.0 KV 520815 TO HM-BTTP2 69.0 KV 520942 CKT 1 b.7. ARAPAHO2 69.0 KV 520815 TO INDPARK2 69.0 KV 520955 CKT 1 b.8. LOAD 1 520955 b.9. WCORDELLJ2 69.0 KV 520424 TO INDPARK2 69.0 KV 520955 CKT 1 b.10. LOAD 1 520955 b.11. WCORDELLJ2 69.0 KV 520424 TO CORDELL2 69.0 KV 520866 CKT 1 b.12. LOAD 1 520866 b.13. CORDELL2 69.0 KV 520866 TO GOTEBO 2 69.0 KV 520925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | STOCKHOLM2__FTSUPLY2_7 | 3 Phase fault on STOCKHOLM2 (520421) 69 kV Bus a. Apply fault at the STOCKHOLM2 (520421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKHOLM2 69.0 KV 520421 TO FTSUPLY2 69.0 KV 520919 CKT 1 b.2. STOCKHOLM2 69.0 KV 520421 TO BUFBEAR2 69.0 KV 521120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUNNYSD4__CARTRCO4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUNNYSD4__LONEGRV4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | SUNNYSD4__ROCKYPT4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUNNYSD4__UNIROY_4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | SUNNYSD7__G16_063_TAP_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | SUNNYSD7__G20_074_TAP_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUNNYSD7__GEN_2017_167_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-167 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SWC414_2__NOL435_2_7 | 3 Phase fault on SWC414 2 (547428) 69 kV Bus a. Apply fault at the SWC414 2 (547428) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWC414 2 69.0 KV 547428 TO NOL435 2 69.0 KV 547610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SWEETWT6__CHISHOLM6_7 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SWS_4__ANADARK4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SWS_4__ELSWORTH___4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SWS_4__G16_097_TAP_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SWS_4__NORGE__4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SWS_4__WASHITA4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SW_SHV_7__DIANA__7_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SW_SHV_7__LONGWD_7_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SXMLCKT4__HOWE___4_7 | 3 Phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXMLCKT4 138.0 KV 515122 TO HOWE 4 138.0 KV 521122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TALOGA_2__VICI___2_7 | 3 Phase fault on TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICI 2 69.0 KV 521082 TO WOODWRD2 69.0 KV 521096 CKT 1 b.2. LOAD 1 521096 b.3. TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TALOGA_4__G20_010_TAP_7 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 138.0 KV 521065 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TATONGA7__CRSRDSW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TATONGA7__MAMTHPW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TATONGA7__MATHWSN7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TATONGA7__SLNGWND7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TENRUSK7__CROCKET7_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TENRUSK7__GEN_2020_081_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO GEN-2020-081 345.0 KV 764120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TENRUSK7__TENGEN_7_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO TENGEN 7 345.0 KV 508586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TERRYRD7__G17_171_TAP_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045 & GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | TERRYRD7__G20_074_TAP_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045 & GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | TERRYRD7__RUSHSPR7_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | THISTLE7__GEN_2017_018_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2017-018 345.0 KV 588630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | THISTLE7__GEN_2018_049_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2018-049 345.0 KV 762834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TIPTCTY2__TIPTON_2_7 | 3 Phase fault on TIPTCTY2 (511479) 69 kV Bus a. Apply fault at the TIPTCTY2 (511479) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTCTY2 69.0 KV 511479 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TIPTE_T2__SNYDER_2_7 | 3 Phase fault on TIPTE T2 (511472) 69 kV Bus a. Apply fault at the TIPTE T2 (511472) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTE T2 69.0 KV 511472 TO SNYDER-2 69.0 KV 511475 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TIPTE_T2__TIPTON_2_7 | 3 Phase fault on TIPTE T2 (511472) 69 kV Bus a. Apply fault at the TIPTE T2 (511472) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTE T2 69.0 KV 511472 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TIPTN_T2__TIPTON_2_7 | 3 Phase fault on TIPTN T2 (511543) 69 kV Bus a. Apply fault at the TIPTN T2 (511543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTN T2 69.0 KV 511543 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TIPTON_2__TIPTONJ2_7 | 3 Phase fault on TIPTON-2 (521069) 69 kV Bus a. Apply fault at the TIPTON-2 (521069) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTON-2 69.0 KV 521069 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TOMSTEED2__ROSEVLT2_7 | 3 Phase fault on TOMSTEED2 (511495) 69 kV Bus a. Apply fault at the TOMSTEED2 (511495) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOMSTEED2 69.0 KV 511495 TO ROSEVLT2 69.0 KV 520528 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TOTAL__4__CHIKSAW4_7 | 3 Phase fault on TOTAL 4 (515165) 138 kV Bus a. Apply fault at the TOTAL 4 (515165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOTAL 4 138.0 KV 515165 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TRAVERSE3__TRW2_TRW3_6 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 345.0 KV 900001 TO TRW2-TRW3 345.0 KV 900004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TREASILD7__G20_075_TAP_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings GEN-2015-045 trips on voltage protection settings GEN-2020-009 trips on voltage protection settings | Disabling instantaneous voltage & frequency protection settings for GEN-2016-095, GEN-2015-045 & GEN-2020-009 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | TREASILD7__GEN_2016_091_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TREASILD7__GEN_2016_095_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TREASILD7__GRACMNT7_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings GEN-2015-045 trips on voltage protection settings GEN-2017-171 trips on voltage protection settings GEN-2017-172 trips on voltage protection settings GEN-2017-173 trips on voltage protection settings GEN-2018-055 trips on voltage protection settings | Disabling instantaneous voltage & frequency protection settings for GEN-2016-095, GEN-2015-045, GEN-2017-171, GEN-2017-172, GEN-2017-173, GEN-2018-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | TUCO_INT___7__CRAWFISH_DR_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO CRAWFISH_DR 345.0 KV 560022 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | TURK___4__MANDEVILTP4_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO MANDEVILTP4 138.0 KV 508105 CKT 1 b.2. LOAD A1 508105 b.3. SETEXAR4 138.0 KV 508078 TO MANDEVILTP4 138.0 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TURK___4__SUGARHL4_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TURK___7__NWTXARK7_6 | 3 Phase fault on TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TURK___7__VALIANT7_6 | 3 Phase fault on TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TUTTLE_4__TUTLETP4_7 | 3 Phase fault on TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VALIANT7__G20_020_TAP_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VALIANT7__HUGO___7_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VANCE__2__SO4TH__2_7 | 3 Phase fault on VANCE 2 (514718) 69 kV Bus a. Apply fault at the VANCE 2 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 69.0 KV 514718 TO SO4TH 2 69.0 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VERDEN_4__SWS_4_7 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VINEOTP2__ESH_TP_2_7 | 3 Phase fault on VINEOTP2 (512673) 69 kV Bus a. Apply fault at the VINEOTP2 (512673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINEOTP2 69.0 KV 512673 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VINITA_2__ESH_TP_2_7 | 3 Phase fault on VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69.0 KV 510404 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VINITA_2__VINTAJC2_7 | 3 Phase fault on VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69.0 KV 510404 TO VINTAJC2 69.0 KV 510418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VIOLA___7__G18_128_TAP_6 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 345.0 KV 532798 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATLANT4__CASSTP4_7 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATLANT4__WILKES_4_7 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATNGSW4__CALUMET4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATNGSW4__OKEENE_4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATNGSW4__OMEGA__4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OMEGA 4 138.0 KV 520964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATNGSW4__WATONGA4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO WATONGA4 138.0 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WAUKOMI4__WAUKOTP4_7 | 3 Phase fault on WAUKOMI4 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 b.2. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WAUKOTP4__SO4TH__4_7 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WAUKOTP4__WOODRNG4_7 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WEKIWA_7__SAPLPRD7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WEKIWA_7__SOONER_7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WEKIWA_7__T.NO.__7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WELSH__7__DIANA__7_6 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WELSH__7__WILKES_7_6 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WHITNEY4__EASTEX_4_7 | 3 Phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138.0 KV 508575 TO EASTEX 4 138.0 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WINDFRM4__FPLWIND4_7 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO FPLWIND4 138.0 KV 515786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WINDFRM4__MOORLND4_7 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WODWRD_2__WOODWRD2_7 | 3 Phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 69.0 KV 514782 TO WOODWRD2 69.0 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOLFCRK4__CHEEKTP4_7 | 3 Phase fault on WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG4__MARSHL_4_7 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG7__GEN_2017_164_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG7__GEN_2020_023_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2020-023 345.0 KV 764525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG7__HUNTERS7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG7__PINTAIL7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG7__REDNGTN7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG7__SKELTON7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODWRD2__CRTSJCT2_7 | 3 Phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69.0 KV 521096 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODWRD2__FARGOJCT2_7 | 3 Phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69.0 KV 521096 TO FARGOJCT2 69.0 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODWRD4__CENT___4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO CENT 4 138.0 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODWRD4__WINDFRM4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WINDFRM4 138.0 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODWRD4__WWRDEHV4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWRDEHV4 138.0 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WRVALLY4__WARREN_4_7 | 3 Phase fault on WRVALLY4 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRVALLY4 138.0 KV 514713 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV4__KEENAN_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV4__OUSPRT_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO OUSPRT 4 138.0 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV4__WWDPST_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV7__BECKHAM7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV7__BOBCAT_7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BOBCAT 7 345.0 KV 516106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV7__BVRCNTY7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BVRCNTY7 345.0 KV 515554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV7__DGRASSE7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV7__G07621119_20_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV7__GEN_2019_012_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV7__GUTHRIE7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV7__TATONGA7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 7GRIMES__3340260_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES%( 334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 334028 TO 4GRIMES% 334026 TO 1GRIMES_1 334163 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ALTUSJT2__5114400_7 | 3 Phase fault on ALTUSJT2 (511441) 69 kV Bus a. Apply fault at the ALTUSJT2( 511441) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT2 511441 TO ALTUSJT4 511440 TO ALTUS2-1 511420 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANADARK4__5208100_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARMFTWD4__5156950_7 | 3 Phase fault on ARMFTWD4 (515694) 138 kV Bus a. Apply fault at the ARMFTWD4( 515694) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMFTWD4 515694 TO ARMFTL11 515695 TO ARMFTT11 515698 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___2__5080540_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2( 508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BUFBEAR2__5211390_7 | 3 Phase fault on BUFBEAR2 (521120) 69 kV Bus a. Apply fault at the BUFBEAR2( 521120) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFBEAR2 521120 TO BUFFBR CL1 521139 TO BUFFBR TERT 521150 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CATOOSA2__5097900_7 | 3 Phase fault on CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2( 509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA2 509799 TO CATOOSA4 509790 TO CATOO1-1 509867 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CATSAGR5__5097900_7 | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5( 512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 512638 TO CATOOSA4 509790 TO 512835 CKT 3 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CENT___4__5153650_7 | 3 Phase fault on CENT 4 (515363) 138 kV Bus a. Apply fault at the CENT 4( 515363) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENT 4 515363 TO CENT 21 515365 TO CENT 11 515364 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHIKSAW2__5151710_7 | 3 Phase fault on CHIKSAW2 (515170) 69 kV Bus a. Apply fault at the CHIKSAW2( 515170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKSAW2 515170 TO CHIKSAW4 515171 TO CHIKSA21 515711 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHISHOLM6__5115530_7 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHLDR2WT__5121010_7 | 3 Phase fault on CHLDR2WT (512100) 69 kV Bus a. Apply fault at the CHLDR2WT( 512100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHLDR2WT 512100 TO CHILD4WT 512101 TO WC2TERT 512102 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHSHLMV7__5154790_6 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVE1 515479 TO CHSHMVET 515482 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHSHLMV7__5154840_6 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVW1 515484 TO CHSHMVWT 515485 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CIMARON4__5149010_7 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEOCOR2__5147780_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2( 514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 514777 TO CLEOCOR4 514778 TO CLEOCOR1 515716 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COWCRK_2__5147060_7 | 3 Phase fault on COWCRK 2 (514705) 69 kV Bus a. Apply fault at the COWCRK 2( 514705) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 514705 TO COWCRK 4 514706 TO COWCRK 1 515717 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COWSKIN_4__5127170_7 | 3 Phase fault on COWSKIN 4 (512719) 138 kV Bus a. Apply fault at the COWSKIN 4( 512719) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN 4 512719 TO COWSKIN2 512717 TO COWSKIN1 512738 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CROCKET4__5092410_7 | 3 Phase fault on CROCKET4 (509240) 138 kV Bus a. Apply fault at the CROCKET4( 509240) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROCKET4 509240 TO CROCKET7 509241 TO CROCK-B1 509243 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | C_RIVER7__5109460_6 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7( 515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DEC392_5__5475940_7 | 3 Phase fault on DEC392 5 (547484) 161 kV Bus a. Apply fault at the DEC392 5( 547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 547484 TO DEC392 2 547594 TO DEC392 1 547714 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DGRASSE4__5158520_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4( 515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DIANA__4__5088320_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DMNDSPG7__5160040_6 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL11 516004 TO DMNDST11 516008 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DMNDSPG7__5160050_6 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL21 516005 TO DMNDST21 516007 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOVERSW4__5208810_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DUNCAN_2__5114530_7 | 3 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2( 511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 511452 TO DUNCAN-4 511453 TO DUNC2-1 511410 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELGINJT2__5114860_7 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELKCTY_2__5114580_7 | 3 Phase fault on ELKCTY-2 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2( 511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 511459 TO ELKCTY-4 511458 TO ELKC4-1 511493 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELKCTY_4__5114900_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4( 511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 511458 TO ELKCITY6 511490 TO ELKC2-1 511482 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELRENO_2__5148190_7 | 3 Phase fault on ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2( 514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAULT_04_DOVERSW4__5208810_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAULT_04_IMO____2__5147900_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2( 514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAULT_04_SO4TH__2__5147310_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAULT_05_CHISHOLM6__5115530_7 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAULT_05_CIMARON4__5149010_7 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAULT_05_GRACMNT4__5158000_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAULT_05_LES_2__5114670_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAULT_05_LES_4__5114680_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAULT_05_VALIANT4__5109110_7 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAULT_06_DIANA__4__5088320_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAULT_06_PIRKEY_4__5085630_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAULT_06_SW_SHV_7__5077590_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FLETCH_4__5209110_7 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4( 520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FPLWIND4__5157870_7 | 3 Phase fault on FPLWIND4 (515786) 138 kV Bus a. Apply fault at the FPLWIND4( 515786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FPLWIND4 515786 TO FPLWND11 515787 TO FLPWND21 515790 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSUPLY4__5209190_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4( 520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 520920 TO FTSUPLY2 520919 TO FTSUPTERTB 521182 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRACMNT4__5158000_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRNDFLD4__5209260_7 | 3 Phase fault on GRNDFLD4 (521106) 138 kV Bus a. Apply fault at the GRNDFLD4( 521106) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFLD4 521106 TO GRANFLD2 520926 TO GRNDTERT 521184 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GROVE__4__5104110_7 | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4( 510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 510402 TO GROVE 5 510411 TO GROVE1-1 510368 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HOB_JCT2__5114630_7 | 3 Phase fault on HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2( 511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HUGO___7__5205600_6 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | IMO____2__5147900_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2( 514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JOHNCO_4__5148090_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KEENAN_1__5153940_7 | 3 Phase fault on KEENAN 1 (515393) 34.5 kV Bus a. Apply fault at the KEENAN 1( 515393) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEENAN 1 515393 TO KEENAN 4 515394 TO KEENAN T 515392 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KERR_BRK1_5__5126340_7 | 3 Phase fault on KERR BRK1 5 (512770) 161 kV Bus a. Apply fault at the KERR BRK1 5( 512770) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK1 5 512770 TO KERR GR3 512634 TO KERR1 1 512846 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KERR_BRK4_5__5126340_7 | 3 Phase fault on KERR BRK4 5 (512771) 161 kV Bus a. Apply fault at the KERR BRK4 5( 512771) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK4 5 512771 TO KERR GR3 512634 TO KERR2 1 512847 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KINGWD_7__5160170_6 | 3 Phase fault on KINGWD 7 (516019) 345 kV Bus a. Apply fault at the KINGWD 7( 516019) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGWD 7 516019 TO KNGWDL11 516017 TO KNGWDT11 516020 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KINGWD_7__5160180_6 | 3 Phase fault on KINGWD 7 (516019) 345 kV Bus a. Apply fault at the KINGWD 7( 516019) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGWD 7 516019 TO KNGWDL21 516018 TO KNGWDT21 516021 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LAKEP2WT__5121100_7 | 3 Phase fault on LAKEP2WT (512111) 69 kV Bus a. Apply fault at the LAKEP2WT( 512111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP2WT 512111 TO LAKEP4WT 512110 TO LP2TERT 512112 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LES_2__5114670_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LES_4__5114680_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGWD_4__5088090_7 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4( 508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LSSOUTH2__5082970_7 | 3 Phase fault on LSSOUTH2 (508296) 69 kV Bus a. Apply fault at the LSSOUTH2( 508296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MANDEVILTP4__5043630_7 | 3 Phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply fault at the MANDEVILTP4( 508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDEVILTP4 508105 TO NE-TEXARK2 504363 TO NE-TEXARK1 504364 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MARAUTO2__5085570_7 | 3 Phase fault on MARAUTO2 (508576) 69 kV Bus a. Apply fault at the MARAUTO2( 508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARAUTO2 508576 TO MARSHL-4 508557 TO MRSH4#21 508592 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MARIETA4__5209870_7 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4( 520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 520988 TO MARIETA2 520987 TO MARSWTERT 521171 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MOORLND4__5209950_7 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4( 520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 520999 TO MOORLND2 520995 TO MLNDTERT 521180 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MORWODS4__5210000_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4( 521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 521001 TO MORWODS2 521000 TO MRWDTERT 521172 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NEO184_5__5475430_7 | 3 Phase fault on NEO184 5 (547471) 161 kV Bus a. Apply fault at the NEO184 5( 547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 547471 TO NEO184 2 547543 TO NEO184B1 547709 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NE_ENID2__5147690_7 | 3 Phase fault on NE ENID2 (514732) 69 kV Bus a. Apply fault at the NE ENID2( 514732) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID2 514732 TO NE ENID4 514769 TO NE ENID1 515741 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NNBOSTN2__5080690_7 | 3 Phase fault on NNBOSTN2 (508068) 69 kV Bus a. Apply fault at the NNBOSTN2( 508068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN2 508068 TO NNBOSTN4 508069 TO NNBT2-1 508099 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NOL435_5__5476100_7 | 3 Phase fault on NOL435 5 (547496) 161 kV Bus a. Apply fault at the NOL435 5( 547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 5 547496 TO NOL435 2 547610 TO NOL435 1 547720 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NORMHLL7__5160970_6 | 3 Phase fault on NORMHLL7 (516096) 345 kV Bus a. Apply fault at the NORMHLL7( 516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 516096 TO NORMHLL4 516097 TO NORMHL21 516099 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NORTWST4__5148800_7 | 3 Phase fault on NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4( 514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTXARK4__5080720_7 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4( 508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OKAY___2__5074280_7 | 3 Phase fault on OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2( 507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 2 507427 TO OKAY 4 507428 TO OKAY1-1 507442 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OKEENE_4__5210150_7 | 3 Phase fault on OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4( 521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PATTERS2__5074310_7 | 3 Phase fault on PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2( 507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 507429 TO PATTERS4 507431 TO PATTN2-1 507444 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIRKEY_4__5085630_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PLVALLY4__5552340_7 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4( 514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 514929 TO NSUB345 555234 TO NEWBUS13.8 750001 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | POTTER_CO__7__5239590_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7( 523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PRY_JCT2__5104190_7 | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2( 510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 510400 TO PRY-JCT4 510419 TO PRYJT2-1 510369 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PRY_JCT4__5104070_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4( 510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 510419 TO PRY-JCT3 510407 TO PRYJT1-1 510371 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDDIRT7__5158780_6 | 3 Phase fault on REDDIRT7 (515877) 345 kV Bus a. Apply fault at the REDDIRT7( 515877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDDIRT7 515877 TO RDDIRT11 515878 TO RDDRTT11 515884 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDDIRT7__5158790_6 | 3 Phase fault on REDDIRT7 (515877) 345 kV Bus a. Apply fault at the REDDIRT7( 515877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDDIRT7 515877 TO RDDIRT21 515879 TO RDDRTT21 515885 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RENFROW4__5155430_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4( 515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 515544 TO RENFROW7 515543 TO RENFRO11 515545 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RKY_RDG4__5119620_7 | 3 Phase fault on RKY_RDG4 (511554) 138 kV Bus a. Apply fault at the RKY_RDG4( 511554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKY_RDG4 511554 TO RKYRDGW1-2CB 511962 TO RKYRDG2-1 511555 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RKY_RDG4__5119630_7 | 3 Phase fault on RKY_RDG4 (511554) 138 kV Bus a. Apply fault at the RKY_RDG4( 511554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKY_RDG4 511554 TO RKYRDGW1-1CB 511963 TO RKYRDG1-1 511556 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROCKYPT2__5151640_7 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RUSHSPR7__5119650_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | RUSSELL4__5210420_7 | 3 Phase fault on RUSSELL4 (521043) 138 kV Bus a. Apply fault at the RUSSELL4( 521043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL4 521043 TO RUSSELL2 521042 TO RSLTERT 521175 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEMINOL4__5150450_7 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4( 515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SETEXAR2__5080780_7 | 3 Phase fault on SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2( 508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 508077 TO SETEXAR4 508078 TO SETEX1-1 508102 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SFOREMAN__4__5040300_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4( 504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 504029 TO SFORE_1 2 504030 TO SFORE_T1 1 504031 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SKELTON7__5159910_6 | 3 Phase fault on SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7( 515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 515990 TO SKELTL11 515991 TO SKELTT11 515992 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SLEEPBR4__5211410_7 | 3 Phase fault on SLEEPBR4 (520922) 138 kV Bus a. Apply fault at the SLEEPBR4( 520922) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLEEPBR4 520922 TO SLP BR CL1 521141 TO SLP BR TERT 521151 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_2__5114350_7 | 3 Phase fault on SNYDER-2 (511475) 69 kV Bus a. Apply fault at the SNYDER-2( 511475) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-2 511475 TO SNYDER-4 511435 TO SNYDRTER 511419 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_4__5210510_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4( 521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 521052 TO SNYDER 2 521051 TO SNYDTERT 521176 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SO4TH__2__5147310_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SOONER_4__5148030_7 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4( 514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUGARHL2__5080800_7 | 3 Phase fault on SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2( 508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNDANC4__5160240_7 | 3 Phase fault on SUNDANC4 (516025) 138 kV Bus a. Apply fault at the SUNDANC4( 516025) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDANC4 516025 TO SUNDCL11 516024 TO SUNDCT11 516026 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD4__5151360_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | SUNNYSD7__5151350_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | SWS_2__5114770_7 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SWS_4__5118490_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SW_SHV_7__5077590_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TALOGA_4__5210640_7 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4( 521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 521065 TO TALOGA 2 521064 TO TLGTERT 521178 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | THISTLE7__5398040_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7( 539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | THUNDER7__5158900_6 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL11 515890 TO THNDRT11 515892 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | THUNDER7__5158910_6 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL21 515891 TO THNDRT21 515893 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TLGAWND1__5153900_7 | 3 Phase fault on TLGAWND1 (515389) 34.5 kV Bus a. Apply fault at the TLGAWND1( 515389) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TLGAWND1 515389 TO TLGAWND4 515390 TO TLGAWNDT 515388 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TRAVERSE3__5873010_6 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3( 900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 900001 TO G16-045XFMR1 587301 TO TRAV3 TER1 900011 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TURK___3__5074540_7 | 3 Phase fault on TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3( 507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 3 507456 TO TURK 4 507454 TO TURK1 1 507458 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TURK___4__5074550_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4( 507454) 138 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VALIANT4__5109110_7 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VINTAJC2__5104170_7 | 3 Phase fault on VINTAJC2 (510418) 69 kV Bus a. Apply fault at the VINTAJC2( 510418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 510418 TO VINTAJC4 510417 TO VINJT1-1 510367 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATLANT2__5080900_7 | 3 Phase fault on WATLANT2 (508089) 69 kV Bus a. Apply fault at the WATLANT2( 508089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WEKIWA_4__5097550_7 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4( 509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WHITNEY2__5085750_7 | 3 Phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply fault at the WHITNEY2( 508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WILKES_4__5088410_7 | 3 Phase fault on WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4( 508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG4__5147150_7 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4( 514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODWRD4__5147820_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4( 514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV4__5153750_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 7GRIMES__3340260_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES%( 334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 334028 TO 4GRIMES% 334026 TO 1GRIMES_1 334163 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ALTUSJT2__5114400_7 | 3 Phase fault on ALTUSJT2 (511441) 69 kV Bus a. Apply fault at the ALTUSJT2( 511441) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT2 511441 TO ALTUSJT4 511440 TO ALTUS2-1 511420 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ANADARK4__5208100_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARMFTWD4__5156950_7 | 3 Phase fault on ARMFTWD4 (515694) 138 kV Bus a. Apply fault at the ARMFTWD4( 515694) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMFTWD4 515694 TO ARMFTL11 515695 TO ARMFTT11 515698 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN___2__5080540_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2( 508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BUFBEAR2__5211390_7 | 3 Phase fault on BUFBEAR2 (521120) 69 kV Bus a. Apply fault at the BUFBEAR2( 521120) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFBEAR2 521120 TO BUFFBR CL1 521139 TO BUFFBR TERT 521150 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CATOOSA2__5097900_7 | 3 Phase fault on CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2( 509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA2 509799 TO CATOOSA4 509790 TO CATOO1-1 509867 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CATSAGR5__5097900_7 | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5( 512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 512638 TO CATOOSA4 509790 TO 512835 CKT 3 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CENT___4__5153650_7 | 3 Phase fault on CENT 4 (515363) 138 kV Bus a. Apply fault at the CENT 4( 515363) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENT 4 515363 TO CENT 21 515365 TO CENT 11 515364 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHIKSAW2__5151710_7 | 3 Phase fault on CHIKSAW2 (515170) 69 kV Bus a. Apply fault at the CHIKSAW2( 515170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKSAW2 515170 TO CHIKSAW4 515171 TO CHIKSA21 515711 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHISHOLM6__5115530_7 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHLDR2WT__5121010_7 | 3 Phase fault on CHLDR2WT (512100) 69 kV Bus a. Apply fault at the CHLDR2WT( 512100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHLDR2WT 512100 TO CHILD4WT 512101 TO WC2TERT 512102 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHSHLMV7__5154790_6 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVE1 515479 TO CHSHMVET 515482 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHSHLMV7__5154840_6 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVW1 515484 TO CHSHMVWT 515485 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CIMARON4__5149010_7 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEOCOR2__5147780_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2( 514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 514777 TO CLEOCOR4 514778 TO CLEOCOR1 515716 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COWCRK_2__5147060_7 | 3 Phase fault on COWCRK 2 (514705) 69 kV Bus a. Apply fault at the COWCRK 2( 514705) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 514705 TO COWCRK 4 514706 TO COWCRK 1 515717 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COWSKIN_4__5127170_7 | 3 Phase fault on COWSKIN 4 (512719) 138 kV Bus a. Apply fault at the COWSKIN 4( 512719) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN 4 512719 TO COWSKIN2 512717 TO COWSKIN1 512738 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CROCKET4__5092410_7 | 3 Phase fault on CROCKET4 (509240) 138 kV Bus a. Apply fault at the CROCKET4( 509240) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROCKET4 509240 TO CROCKET7 509241 TO CROCK-B1 509243 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | C_RIVER7__5109460_6 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7( 515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DEC392_5__5475940_7 | 3 Phase fault on DEC392 5 (547484) 161 kV Bus a. Apply fault at the DEC392 5( 547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 547484 TO DEC392 2 547594 TO DEC392 1 547714 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DGRASSE4__5158520_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4( 515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DIANA__4__5088320_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DMNDSPG7__5160040_6 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL11 516004 TO DMNDST11 516008 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DMNDSPG7__5160050_6 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL21 516005 TO DMNDST21 516007 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOVERSW4__5208810_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DUNCAN_2__5114530_7 | 3 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2( 511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 511452 TO DUNCAN-4 511453 TO DUNC2-1 511410 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELGINJT2__5114860_7 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELKCTY_2__5114580_7 | 3 Phase fault on ELKCTY-2 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2( 511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 511459 TO ELKCTY-4 511458 TO ELKC4-1 511493 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELKCTY_4__5114900_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4( 511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 511458 TO ELKCITY6 511490 TO ELKC2-1 511482 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELRENO_2__5148190_7 | 3 Phase fault on ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2( 514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAULT_04_DOVERSW4__5208810_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAULT_04_IMO____2__5147900_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2( 514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAULT_04_SO4TH__2__5147310_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAULT_05_CHISHOLM6__5115530_7 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAULT_05_CIMARON4__5149010_7 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAULT_05_GRACMNT4__5158000_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAULT_05_LES_2__5114670_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAULT_05_LES_4__5114680_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAULT_05_VALIANT4__5109110_7 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAULT_06_DIANA__4__5088320_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAULT_06_PIRKEY_4__5085630_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAULT_06_SW_SHV_7__5077590_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FLETCH_4__5209110_7 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4( 520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FPLWIND4__5157870_7 | 3 Phase fault on FPLWIND4 (515786) 138 kV Bus a. Apply fault at the FPLWIND4( 515786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FPLWIND4 515786 TO FPLWND11 515787 TO FLPWND21 515790 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSUPLY4__5209190_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4( 520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 520920 TO FTSUPLY2 520919 TO FTSUPTERTB 521182 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRACMNT4__5158000_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRNDFLD4__5209260_7 | 3 Phase fault on GRNDFLD4 (521106) 138 kV Bus a. Apply fault at the GRNDFLD4( 521106) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFLD4 521106 TO GRANFLD2 520926 TO GRNDTERT 521184 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GROVE__4__5104110_7 | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4( 510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 510402 TO GROVE 5 510411 TO GROVE1-1 510368 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HOB_JCT2__5114630_7 | 3 Phase fault on HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2( 511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HUGO___7__5205600_6 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | IMO____2__5147900_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2( 514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JOHNCO_4__5148090_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KEENAN_1__5153940_7 | 3 Phase fault on KEENAN 1 (515393) 34.5 kV Bus a. Apply fault at the KEENAN 1( 515393) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEENAN 1 515393 TO KEENAN 4 515394 TO KEENAN T 515392 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KERR_BRK1_5__5126340_7 | 3 Phase fault on KERR BRK1 5 (512770) 161 kV Bus a. Apply fault at the KERR BRK1 5( 512770) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK1 5 512770 TO KERR GR3 512634 TO KERR1 1 512846 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KERR_BRK4_5__5126340_7 | 3 Phase fault on KERR BRK4 5 (512771) 161 kV Bus a. Apply fault at the KERR BRK4 5( 512771) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK4 5 512771 TO KERR GR3 512634 TO KERR2 1 512847 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KINGWD_7__5160170_6 | 3 Phase fault on KINGWD 7 (516019) 345 kV Bus a. Apply fault at the KINGWD 7( 516019) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGWD 7 516019 TO KNGWDL11 516017 TO KNGWDT11 516020 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KINGWD_7__5160180_6 | 3 Phase fault on KINGWD 7 (516019) 345 kV Bus a. Apply fault at the KINGWD 7( 516019) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGWD 7 516019 TO KNGWDL21 516018 TO KNGWDT21 516021 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LAKEP2WT__5121100_7 | 3 Phase fault on LAKEP2WT (512111) 69 kV Bus a. Apply fault at the LAKEP2WT( 512111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP2WT 512111 TO LAKEP4WT 512110 TO LP2TERT 512112 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LES_2__5114670_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LES_4__5114680_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGWD_4__5088090_7 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4( 508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LSSOUTH2__5082970_7 | 3 Phase fault on LSSOUTH2 (508296) 69 kV Bus a. Apply fault at the LSSOUTH2( 508296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MANDEVILTP4__5043630_7 | 3 Phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply fault at the MANDEVILTP4( 508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDEVILTP4 508105 TO NE-TEXARK2 504363 TO NE-TEXARK1 504364 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MARAUTO2__5085570_7 | 3 Phase fault on MARAUTO2 (508576) 69 kV Bus a. Apply fault at the MARAUTO2( 508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARAUTO2 508576 TO MARSHL-4 508557 TO MRSH4#21 508592 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MARIETA4__5209870_7 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4( 520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 520988 TO MARIETA2 520987 TO MARSWTERT 521171 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MOORLND4__5209950_7 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4( 520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 520999 TO MOORLND2 520995 TO MLNDTERT 521180 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MORWODS4__5210000_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4( 521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 521001 TO MORWODS2 521000 TO MRWDTERT 521172 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NEO184_5__5475430_7 | 3 Phase fault on NEO184 5 (547471) 161 kV Bus a. Apply fault at the NEO184 5( 547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 547471 TO NEO184 2 547543 TO NEO184B1 547709 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NE_ENID2__5147690_7 | 3 Phase fault on NE ENID2 (514732) 69 kV Bus a. Apply fault at the NE ENID2( 514732) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID2 514732 TO NE ENID4 514769 TO NE ENID1 515741 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NNBOSTN2__5080690_7 | 3 Phase fault on NNBOSTN2 (508068) 69 kV Bus a. Apply fault at the NNBOSTN2( 508068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN2 508068 TO NNBOSTN4 508069 TO NNBT2-1 508099 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NOL435_5__5476100_7 | 3 Phase fault on NOL435 5 (547496) 161 kV Bus a. Apply fault at the NOL435 5( 547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 5 547496 TO NOL435 2 547610 TO NOL435 1 547720 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NORMHLL7__5160970_6 | 3 Phase fault on NORMHLL7 (516096) 345 kV Bus a. Apply fault at the NORMHLL7( 516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 516096 TO NORMHLL4 516097 TO NORMHL21 516099 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NORTWST4__5148800_7 | 3 Phase fault on NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4( 514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NWTXARK4__5080720_7 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4( 508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OKAY___2__5074280_7 | 3 Phase fault on OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2( 507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 2 507427 TO OKAY 4 507428 TO OKAY1-1 507442 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OKEENE_4__5210150_7 | 3 Phase fault on OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4( 521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PATTERS2__5074310_7 | 3 Phase fault on PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2( 507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 507429 TO PATTERS4 507431 TO PATTN2-1 507444 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIRKEY_4__5085630_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PLVALLY4__5552340_7 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4( 514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 514929 TO NSUB345 555234 TO NEWBUS13.8 750001 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | POTTER_CO__7__5239590_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7( 523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PRY_JCT2__5104190_7 | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2( 510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 510400 TO PRY-JCT4 510419 TO PRYJT2-1 510369 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PRY_JCT4__5104070_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4( 510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 510419 TO PRY-JCT3 510407 TO PRYJT1-1 510371 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDDIRT7__5158780_6 | 3 Phase fault on REDDIRT7 (515877) 345 kV Bus a. Apply fault at the REDDIRT7( 515877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDDIRT7 515877 TO RDDIRT11 515878 TO RDDRTT11 515884 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDDIRT7__5158790_6 | 3 Phase fault on REDDIRT7 (515877) 345 kV Bus a. Apply fault at the REDDIRT7( 515877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDDIRT7 515877 TO RDDIRT21 515879 TO RDDRTT21 515885 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RENFROW4__5155430_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4( 515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 515544 TO RENFROW7 515543 TO RENFRO11 515545 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RKY_RDG4__5119620_7 | 3 Phase fault on RKY_RDG4 (511554) 138 kV Bus a. Apply fault at the RKY_RDG4( 511554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKY_RDG4 511554 TO RKYRDGW1-2CB 511962 TO RKYRDG2-1 511555 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RKY_RDG4__5119630_7 | 3 Phase fault on RKY_RDG4 (511554) 138 kV Bus a. Apply fault at the RKY_RDG4( 511554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKY_RDG4 511554 TO RKYRDGW1-1CB 511963 TO RKYRDG1-1 511556 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ROCKYPT2__5151640_7 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RUSHSPR7__5119650_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | RUSSELL4__5210420_7 | 3 Phase fault on RUSSELL4 (521043) 138 kV Bus a. Apply fault at the RUSSELL4( 521043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL4 521043 TO RUSSELL2 521042 TO RSLTERT 521175 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SEMINOL4__5150450_7 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4( 515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SETEXAR2__5080780_7 | 3 Phase fault on SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2( 508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 508077 TO SETEXAR4 508078 TO SETEX1-1 508102 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SFOREMAN__4__5040300_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4( 504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 504029 TO SFORE_1 2 504030 TO SFORE_T1 1 504031 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SKELTON7__5159910_6 | 3 Phase fault on SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7( 515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 515990 TO SKELTL11 515991 TO SKELTT11 515992 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SLEEPBR4__5211410_7 | 3 Phase fault on SLEEPBR4 (520922) 138 kV Bus a. Apply fault at the SLEEPBR4( 520922) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLEEPBR4 520922 TO SLP BR CL1 521141 TO SLP BR TERT 521151 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_2__5114350_7 | 3 Phase fault on SNYDER-2 (511475) 69 kV Bus a. Apply fault at the SNYDER-2( 511475) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-2 511475 TO SNYDER-4 511435 TO SNYDRTER 511419 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_4__5210510_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4( 521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 521052 TO SNYDER 2 521051 TO SNYDTERT 521176 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SO4TH__2__5147310_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SOONER_4__5148030_7 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4( 514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUGARHL2__5080800_7 | 3 Phase fault on SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2( 508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUNDANC4__5160240_7 | 3 Phase fault on SUNDANC4 (516025) 138 kV Bus a. Apply fault at the SUNDANC4( 516025) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDANC4 516025 TO SUNDCL11 516024 TO SUNDCT11 516026 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUNNYSD4__5151360_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | SUNNYSD7__5151350_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | SWS_2__5114770_7 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SWS_4__5118490_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SW_SHV_7__5077590_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TALOGA_4__5210640_7 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4( 521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 521065 TO TALOGA 2 521064 TO TLGTERT 521178 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | THISTLE7__5398040_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7( 539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | THUNDER7__5158900_6 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL11 515890 TO THNDRT11 515892 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | THUNDER7__5158910_6 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL21 515891 TO THNDRT21 515893 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TLGAWND1__5153900_7 | 3 Phase fault on TLGAWND1 (515389) 34.5 kV Bus a. Apply fault at the TLGAWND1( 515389) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TLGAWND1 515389 TO TLGAWND4 515390 TO TLGAWNDT 515388 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TRAVERSE3__5873010_6 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3( 900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 900001 TO G16-045XFMR1 587301 TO TRAV3 TER1 900011 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TURK___3__5074540_7 | 3 Phase fault on TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3( 507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 3 507456 TO TURK 4 507454 TO TURK1 1 507458 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TURK___4__5074550_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4( 507454) 138 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VALIANT4__5109110_7 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VINTAJC2__5104170_7 | 3 Phase fault on VINTAJC2 (510418) 69 kV Bus a. Apply fault at the VINTAJC2( 510418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 510418 TO VINTAJC4 510417 TO VINJT1-1 510367 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATLANT2__5080900_7 | 3 Phase fault on WATLANT2 (508089) 69 kV Bus a. Apply fault at the WATLANT2( 508089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WEKIWA_4__5097550_7 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4( 509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WHITNEY2__5085750_7 | 3 Phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply fault at the WHITNEY2( 508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WILKES_4__5088410_7 | 3 Phase fault on WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4( 508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG4__5147150_7 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4( 514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODWRD4__5147820_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4( 514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV4__5153750_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 112GORE4_511488 | Apply single-phase fault on: 112GORE4 138.0 KV 511488 TO COMANC-4 138.0 KV 511437 CKT 1, near 112GORE4 138 kV for 7 cycles with stuck breaker at 112GORE4 138 kV. Clear Fault after 10 cycles and trip: 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ALTUSJT4_511440 | Apply single-phase fault on: ALTUSJT4 138.0 KV 511440 TO RUSSELL4 138.0 KV 521043 CKT 1, near ALTUSJT4 138 kV for 7 cycles with stuck breaker at ALTUSJT4 138 kV. Clear Fault after 10 cycles and trip: ALTUSJT4 138.0 KV 511440 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___4_508054 | Apply single-phase fault on: BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1, near BANN 4 138 kV for 7 cycles with stuck breaker at BANN 4 138 kV. Clear Fault after 10 cycles and trip: BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CACHEJ4_521190 | Apply single-phase fault on: CACHEJ4 138.0 KV 521190 TO G20-016-TAP 138.0 KV 764505 CKT 1, near CACHEJ4 138 kV for 7 cycles with stuck breaker at CACHEJ4 138 kV. Clear Fault after 10 cycles and trip: CACHEJ4 138.0 KV 521190 TO MDCPRK4 138.0 KV 520404 CKT 1 LOAD 1 520404 MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 LOAD 1 521024 PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEOCOR4_514778 | Apply single-phase fault on: CLEOCOR4 138.0 KV 514778 TO CLEOPLT4 138.0 KV 515562 CKT 1, near CLEOCOR4 138 kV for 7 cycles with stuck breaker at CLEOCOR4 138 kV. Clear Fault after 10 cycles and trip: CLEOCOR4 138.0 KV 514778 TO SUNDANC4 138.0 KV 516025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEOPLT4_515562 | Apply single-phase fault on: CLEOPLT4 138.0 KV 515562 TO CLEO PL4 138.0 KV 515553 CKT 1, near CLEOPLT4 138 kV for 7 cycles with stuck breaker at CLEOPLT4 138 kV. Clear Fault after 10 cycles and trip: CLEOPLT4 138.0 KV 515562 TO MENOTAP4 138.0 KV 514789 CKT 1 LOAD 1 514789 MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COMMTAP4_511494 | Apply single-phase fault on: COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1, near COMMTAP4 138 kV for 7 cycles with stuck breaker at COMMTAP4 138 kV. Clear Fault after 10 cycles and trip: COMMTAP4 138.0 KV 511494 TO L.E.S.-4 138.0 KV 511467 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CROCKET7_509241 | Apply single-phase fault on: CROCKET7 345.0 KV 509241 TO 7GRIMES% 345.0 KV 334028 CKT 1, near CROCKET7 345 kV for 6 cycles with stuck breaker at CROCKET7 345 kV. Clear Fault after 10 cycles and trip: CROCKET7 345.0 KV 509241 TO TENRUSK7 345.0 KV 508585 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DEWEY__4_514787 | Apply single-phase fault on: DEWEY 4 138.0 KV 514787 TO TALOGA 4 138.0 KV 521065 CKT 1, near DEWEY 4 138 kV for 7 cycles with stuck breaker at DEWEY 4 138 kV. Clear Fault after 10 cycles and trip: REDCLFT4 138.0 KV 515533 TO DEWEY 4 138.0 KV 514787 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EXCLART4_510401 | Apply single-phase fault on: EXCLART4 138.0 KV 510401 TO 510373 CKT 1 510373 TO 510437 CKT 1 509752 TO 510437 CKT 1, near EXCLART4 138 kV for 7 cycles with stuck breaker at EXCLART4 138 kV. Clear Fault after 10 cycles and trip: EXCLART4 138.0 KV 510401 TO PRY_CRK4 138.0 KV 510431 CKT 1 LOAD 1 510431 PRY_CRK4 138.0 KV 510431 TO MCARBDE4 138.0 KV 510366 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FRMNTAP4_514709_0 | Apply single-phase fault on: WOODRNG4 138.0 KV 514714 TO FRMNTAP4 138.0 KV 514709 CKT 1, near FRMNTAP4 138 kV for 7 cycles with stuck breaker at FRMNTAP4 138 kV. Clear Fault after 10 cycles and trip: FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 LOAD 1 514712 FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 LOAD 1 515641 PLNSMEN4 138.0 KV 515641 TO BRECKNR4 138.0 KV 514815 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSUPLY2_520919 | Apply single-phase fault on: FTSUPLY2 69.0 KV 520919 TO STOCKHOLM2 69.0 KV 520421 CKT 1 LOAD 1 520421 STOCKHOLM2 69.0 KV 520421 TO BUFBEAR2 69.0 KV 521120 CKT 1, near FTSUPLY2 69 kV for 7 cycles with stuck breaker at FTSUPLY2 69 kV. Clear Fault after 10 cycles and trip: FTSUPLY2 69.0 KV 520919 TO FTSPLY 2 69.0 KV 520456 CKT 1 LOAD 1 520456 LOAD 2 520456 FTSPLY 2 69.0 KV 520456 TO FARGOJCT2 69.0 KV 521196 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSUPLY4_520920 | Apply single-phase fault on: FTSUPLY4 138.0 KV 520920 TO SLEEPBR4 138.0 KV 520922 CKT 1, near FTSUPLY4 138 kV for 7 cycles with stuck breaker at FTSUPLY4 138 kV. Clear Fault after 10 cycles and trip: FTSUPLY4 138.0 KV 520920 TO IODINE 4 138.0 KV 520957 CKT 1 LOAD 1 520957 IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G176_TAP_588779 | Apply single-phase fault on: G17-036_TAP 138.0 KV 588779 TO GEN-2017-036 138.0 KV 588780 CKT 1, near G17-036_TAP 138 kV for 7 cycles with stuck breaker at G17-036_TAP 138 kV. Clear Fault after 10 cycles and trip: SNYDER-4 138.0 KV 511435 TO G17-036_TAP 138.0 KV 588779 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G185_TAP_762467 | Apply single-phase fault on: G18-015-TAP 345.0 KV 762467 TO G17-151TAP 345.0 KV 762216 CKT 1, near G18-015-TAP 345 kV for 6 cycles with stuck breaker at G18-015-TAP 345 kV. Clear Fault after 10 cycles and trip: G18-015-TAP 345.0 KV 762467 TO L.E.S.-7 345.0 KV 511468 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G18_092_PROX_763215 | Apply single-phase fault on: G18-092-PROX 345.0 KV 763215 TO CRAWFISH_DR 345.0 KV 560022 CKT 2, near G18-092-PROX 345 kV for 6 cycles with stuck breaker at G18-092-PROX 345 kV. Clear Fault after 10 cycles and trip: G18-092-PROX 345.0 KV 763215 TO O.K.U.-7 345.0 KV 511456 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GOTEBO_2_520925 | Apply single-phase fault on: GOTEBO 2 69.0 KV 520925 TO LTELKSW2 69.0 KV 521137 CKT 1, near GOTEBO 2 69 kV for 7 cycles with stuck breaker at GOTEBO 2 69 kV. Clear Fault after 10 cycles and trip: STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 STALOGA2 69.0 KV 520454 TO PUTNAM 2 69.0 KV 521033 CKT 1 LOAD 1 521033 HM-BTTP2 69.0 KV 520942 TO PUTNAM 2 69.0 KV 521033 CKT 1 LOAD 1 521033 ARAPAHO2 69.0 KV 520815 TO HM-BTTP2 69.0 KV 520942 CKT 1 ARAPAHO2 69.0 KV 520815 TO INDPARK2 69.0 KV 520955 CKT 1 LOAD 1 520955 WCORDELLJ2 69.0 KV 520424 TO INDPARK2 69.0 KV 520955 CKT 1 LOAD 1 520955 WCORDELLJ2 69.0 KV 520424 TO CORDELL2 69.0 KV 520866 CKT 1 LOAD 1 520866 CORDELL2 69.0 KV 520866 TO GOTEBO 2 69.0 KV 520925 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRACMNT7_515800 | Apply single-phase fault on: GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1, near GRACMNT7 345 kV for 6 cycles with stuck breaker at GRACMNT7 345 kV. Clear Fault after 10 cycles and trip: GRACMNT7 345.0 KV 515800 TO MINCO 7 345.0 KV 514801 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GROVE__4_510402 | Apply single-phase fault on: PRY-JCT4 138.0 KV 510419 TO BIRDHOL4 138.0 KV 510398 CKT 1 LOAD 1 510398 BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 LOAD 1 510421 JAY 4 138.0 KV 510421 TO GROVE 4 138.0 KV 510402 CKT 1, near GROVE 4 138 kV for 7 cycles with stuck breaker at GROVE 4 138 kV. Clear Fault after 10 cycles and trip: GROVE 4 138.0 KV 510402 TO COWSKIN 4 138.0 KV 512719 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HOB_JCT4_511463 | Apply single-phase fault on: HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1, near HOB-JCT4 138 kV for 7 cycles with stuck breaker at HOB-JCT4 138 kV. Clear Fault after 10 cycles and trip: HOB-JCT4 138.0 KV 511463 TO CL-AFTP4 138.0 KV 511446 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HUNTERS7_515476 | Apply single-phase fault on: HUNTERS7 345.0 KV 515476 TO WOODRNG7 345.0 KV 514715 CKT 1, near HUNTERS7 345 kV for 6 cycles with stuck breaker at HUNTERS7 345 kV. Clear Fault after 10 cycles and trip: HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | IMO____4_514790 | Apply single-phase fault on: CLEOPLT4 138.0 KV 515562 TO MENOTAP4 138.0 KV 514789 CKT 1 LOAD 1 514789 MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1, near IMO 4 138 kV for 7 cycles with stuck breaker at IMO 4 138 kV. Clear Fault after 10 cycles and trip: IMO 4 138.0 KV 514790 TO GLENWD 4 138.0 KV 514734 CKT 1 LOAD 1 514734 GLENWD 4 138.0 KV 514734 TO NE ENID4 138.0 KV 514769 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JOHNCO_7_514809 | Apply single-phase fault on: JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1, near JOHNCO 7 345 kV for 6 cycles with stuck breaker at JOHNCO 7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO PITTSB-7 345.0 KV 510907 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LEBROCK7_508572 | Apply single-phase fault on: LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1, near LEBROCK7 345 kV for 6 cycles with stuck breaker at LEBROCK7 345 kV. Clear Fault after 10 cycles and trip: LEBROCK7 345.0 KV 508572 TO PIRKEY 7 345.0 KV 508563 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LES4_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LES7_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO G18-015-TAP 345.0 KV 762467 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LWS_NTP4_511471 | Apply single-phase fault on: LWS-NTP4 138.0 KV 511471 TO LWS N4 138.0 KV 511430 CKT 1, near LWS-NTP4 138 kV for 7 cycles with stuck breaker at LWS-NTP4 138 kV. Clear Fault after 10 cycles and trip: LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LYDIA__7_508298 | Apply single-phase fault on: LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1, near LYDIA 7 345 kV for 6 cycles with stuck breaker at LYDIA 7 345 kV. Clear Fault after 10 cycles and trip: LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MOORLND4_520999 | Apply single-phase fault on: MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1, near MOORLND4 138 kV for 7 cycles with stuck breaker at MOORLND4 138 kV. Clear Fault after 10 cycles and trip: MOORLND4 138.0 KV 520999 TO GLASMTN4 138.0 KV 514788 CKT 1 LOAD 1 514788 LOAD 2 514788 GLASMTN4 138.0 KV 514788 TO CLEOCOR4 138.0 KV 514778 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MORWODS4_521001 | Apply single-phase fault on: MORWODS4 138.0 KV 521001 TO ELLIS 4 138.0 KV 511561 CKT 1 LOAD 1 511561 ELLIS 4 138.0 KV 511561 TO CUSTER 4 138.0 KV 520459 CKT 1 LOAD 1 520459 CUSTER 4 138.0 KV 520459 TO 521116 CKT 1, near MORWODS4 138 kV for 7 cycles with stuck breaker at MORWODS4 138 kV. Clear Fault after 10 cycles and trip: MORWODS4 138.0 KV 521001 TO MORWOOD4 138.0 KV 521002 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NINMLTP4_521128 | Apply single-phase fault on: NINMLTP4 138.0 KV 521128 TO MORWODS4 138.0 KV 521001 CKT 1, near NINMLTP4 138 kV for 7 cycles with stuck breaker at NINMLTP4 138 kV. Clear Fault after 10 cycles and trip: NINMLTP4 138.0 KV 521128 TO BEARCAT4 138.0 KV 520500 CKT 1 LOAD 1 520500 BEARCAT4 138.0 KV 520500 TO ASPEN 4 138.0 KV 520462 CKT 1 LOAD 1 520462 ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTXARK4_508071 | Apply single-phase fault on: NWTXARK4 138.0 KV 508071 TO NASH 4 138.0 KV 508049 CKT 1, near NWTXARK4 138 kV for 7 cycles with stuck breaker at NWTXARK4 138 kV. Clear Fault after 10 cycles and trip: NWTXARK4 138.0 KV 508071 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTXARK7_508072 | Apply single-phase fault on: NWTXARK7 345.0 KV 508072 TO TURK 7 345.0 KV 507455 CKT 1, near NWTXARK7 345 kV for 6 cycles with stuck breaker at NWTXARK7 345 kV. Clear Fault after 10 cycles and trip: NWTXARK7 345.0 KV 508072 TO WILKES 7 345.0 KV 508841 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWT_BNT4_508070 | Apply single-phase fault on: NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1, near NWT-BNT4 138 kV for 7 cycles with stuck breaker at NWT-BNT4 138 kV. Clear Fault after 10 cycles and trip: BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OKEENE_4_521016 | Apply single-phase fault on: OKEENE 4 138.0 KV 521016 TO CDRDLTP4 138.0 KV 520848 CKT 1, near OKEENE 4 138 kV for 7 cycles with stuck breaker at OKEENE 4 138 kV. Clear Fault after 10 cycles and trip: OKEENE 4 138.0 KV 521016 TO WATNGSW4 138.0 KV 520536 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PINTAIL7_516010 | Apply single-phase fault on: PINTAIL7 345.0 KV 516010 TO WOODRNG7 345.0 KV 514715 CKT 1, near PINTAIL7 345 kV for 6 cycles with stuck breaker at PINTAIL7 345 kV. Clear Fault after 10 cycles and trip: PINTAIL7 345.0 KV 516010 TO SOONER 7 345.0 KV 514803 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIRKEY_7_508563 | Apply single-phase fault on: PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1, near PIRKEY 7 345 kV for 6 cycles with stuck breaker at PIRKEY 7 345 kV. Clear Fault after 10 cycles and trip: LEBROCK7 345.0 KV 508572 TO PIRKEY 7 345.0 KV 508563 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PRY_JCT2_510400 | Apply single-phase fault on: PRY-JCT2 69.0 KV 510400 TO ADAIR--2 69.0 KV 510387 CKT 1 LOAD 1 510387 ADAIR--2 69.0 KV 510387 TO VINITA-2 69.0 KV 510404 CKT 1, near PRY-JCT2 69 kV for 7 cycles with stuck breaker at PRY-JCT2 69 kV. Clear Fault after 10 cycles and trip: PRY-JCT2 69.0 KV 510400 TO PRYORC12 69.0 KV 512810 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PRY_JCT4_510419 | Apply single-phase fault on: PRY-JCT4 138.0 KV 510419 TO BIRDHOL4 138.0 KV 510398 CKT 1 LOAD 1 510398 BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 LOAD 1 510421 JAY 4 138.0 KV 510421 TO GROVE 4 138.0 KV 510402 CKT 1, near PRY-JCT4 138 kV for 7 cycles with stuck breaker at PRY-JCT4 138 kV. Clear Fault after 10 cycles and trip: PRY-JCT4 138.0 KV 510419 TO G20-092-TAP 138.0 KV 764160 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROMNOSE4_514823_0 | Apply single-phase fault on: ROMNOSE4 138.0 KV 514823 TO SOUTHRD4 138.0 KV 514822 CKT 1 LOAD 1 514822 LOAD 2 514822 SOUTHRD4 138.0 KV 514822 TO CANTNLK4 138.0 KV 515964 CKT 1 LOAD 1 515964 CANTNLK4 138.0 KV 515964 TO DEWEY 4 138.0 KV 514787 CKT 1, near ROMNOSE4 138 kV for 7 cycles with stuck breaker at ROMNOSE4 138 kV. Clear Fault after 10 cycles and trip: ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RUSSELL4_521043 | Apply single-phase fault on: RUSSELL4 138.0 KV 521043 TO 512110 CKT 1, near RUSSELL4 138 kV for 7 cycles with stuck breaker at RUSSELL4 138 kV. Clear Fault after 10 cycles and trip: RUSSELL4 138.0 KV 521043 TO ALTUSJT4 138.0 KV 511440 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_2_511475 | Apply single-phase fault on: SNYDER-2 69.0 KV 511475 TO TOMSTEED2 69.0 KV 511495 CKT 1, near SNYDER-2 69 kV for 7 cycles with stuck breaker at SNYDER-2 69 kV. Clear Fault after 10 cycles and trip: SNYDER-2 69.0 KV 511475 TO TIPTE T2 69.0 KV 511472 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_2_521051 | Apply single-phase fault on: SNYDER 2 69.0 KV 521051 TO SNYDRSB2 69.0 KV 520541 CKT Z1 LOAD 1 520541 SNYDRSB2 69.0 KV 520541 TO NAVJOTP2 69.0 KV 521009 CKT 1, near SNYDER 2 69 kV for 7 cycles with stuck breaker at SNYDER 2 69 kV. Clear Fault after 10 cycles and trip: SNYDER 2 69.0 KV 521051 TO TIPTONJ2 69.0 KV 521070 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_4_511435 | Apply single-phase fault on: SNYDER-4 138.0 KV 511435 TO SNYDER 4 138.0 KV 521052 CKT 1, near SNYDER-4 138 kV for 7 cycles with stuck breaker at SNYDER-4 138 kV. Clear Fault after 10 cycles and trip: SNYDER-4 138.0 KV 511435 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_4_521052 | Apply single-phase fault on: SNYDER 4 138.0 KV 521052 TO G20-016-TAP 138.0 KV 764505 CKT 1, near SNYDER 4 138 kV for 7 cycles with stuck breaker at SNYDER 4 138 kV. Clear Fault after 10 cycles and trip: SNYDER 4 138.0 KV 521052 TO SNYDER-4 138.0 KV 511435 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD4_515135 | Apply single-phase fault on: SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 LOAD 1 515137 UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 LOAD 1 515372 CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1, near SUNNYSD4 138 kV for 7 cycles with stuck breaker at SUNNYSD4 138 kV. Clear Fault after 10 cycles and trip: SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD7_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | TALOGA_2_521064 | Apply single-phase fault on: TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 LOAD 1 521082 VICI 2 69.0 KV 521082 TO WOODWRD2 69.0 KV 521096 CKT 1, near TALOGA 2 69 kV for 7 cycles with stuck breaker at TALOGA 2 69 kV. Clear Fault after 10 cycles and trip: TALOGA 2 69.0 KV 521064 TO CANTON-2 69.0 KV 520843 CKT 1 LOAD 1 520843 LOAD 2 520843 CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TALOGA_4_521065 | Apply single-phase fault on: TALOGA 4 138.0 KV 521065 TO DEWEY 4 138.0 KV 514787 CKT 1, near TALOGA 4 138 kV for 7 cycles with stuck breaker at TALOGA 4 138 kV. Clear Fault after 10 cycles and trip: G20-010-TAP 138.0 KV 765215 TO TALOGA 4 138.0 KV 521065 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TERRYRD7_511568 | Apply single-phase fault on: TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345 kV for 6 cycles with stuck breaker at TERRYRD7 345 kV. Clear Fault after 10 cycles and trip: TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TURK___7_507455 | Apply single-phase fault on: TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1, near TURK 7 345 kV for 6 cycles with stuck breaker at TURK 7 345 kV. Clear Fault after 10 cycles and trip: TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VALIANT7_510911 | Apply single-phase fault on: TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1, near VALIANT7 345 kV for 6 cycles with stuck breaker at VALIANT7 345 kV. Clear Fault after 10 cycles and trip: LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WAUKOTP4_514711 | Apply single-phase fault on: WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1, near WAUKOTP4 138 kV for 7 cycles with stuck breaker at WAUKOTP4 138 kV. Clear Fault after 10 cycles and trip: WAUKOTP4 138.0 KV 514711 TO WAUKOMI4 138.0 KV 514710 CKT 1 LOAD 1 514710 WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WELSH__7_508359 | Apply single-phase fault on: WELSH 7 345.0 KV 508359 TO LYDIA 7 345.0 KV 508298 CKT 1, near WELSH 7 345 kV for 6 cycles with stuck breaker at WELSH 7 345 kV. Clear Fault after 10 cycles and trip: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WILKES_7_508841 | Apply single-phase fault on: WILKES 7 345.0 KV 508841 TO LONGWD 7 345.0 KV 508809 CKT 1 LOAD 1 508311, near WILKES 7 345 kV for 6 cycles with stuck breaker at WILKES 7 345 kV. Clear Fault after 10 cycles and trip: WILKES 7 345.0 KV 508841 TO NWTXARK7 345.0 KV 508072 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 - Southeast | 25S | Transfer | WOODRNG4_514714 | Apply single-phase fault on: WOODRNG4 138.0 KV 514714 TO FRMNTAP4 138.0 KV 514709 CKT 1, near WOODRNG4 138 kV for 7 cycles with stuck breaker at WOODRNG4 138 kV. Clear Fault after 10 cycles and trip: WOODRNG4 138.0 KV 514714 TO OTTER 4 138.0 KV 514708 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG7_514715 | Apply single-phase fault on: WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1, near WOODRNG7 345 kV for 6 cycles with stuck breaker at WOODRNG7 345 kV. Clear Fault after 10 cycles and trip: WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODWRD2_521096 | Apply single-phase fault on: WOODWRD2 69.0 KV 521096 TO CRTSJCT2 69.0 KV 521197 CKT 1, near WOODWRD2 69 kV for 7 cycles with stuck breaker at WOODWRD2 69 kV. Clear Fault after 10 cycles and trip: WOODWRD2 69.0 KV 521096 TO WODWRD 2 69.0 KV 514782 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV4_515376 | Apply single-phase fault on: WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1, near WWRDEHV4 138 kV for 7 cycles with stuck breaker at WWRDEHV4 138 kV. Clear Fault after 10 cycles and trip: WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 112GORE4_511488 | Apply single-phase fault on: 112GORE4 138.0 KV 511488 TO COMANC-4 138.0 KV 511437 CKT 1, near 112GORE4 138 kV for 7 cycles with stuck breaker at 112GORE4 138 kV. Clear Fault after 10 cycles and trip: 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ALTUSJT4_511440 | Apply single-phase fault on: ALTUSJT4 138.0 KV 511440 TO RUSSELL4 138.0 KV 521043 CKT 1, near ALTUSJT4 138 kV for 7 cycles with stuck breaker at ALTUSJT4 138 kV. Clear Fault after 10 cycles and trip: ALTUSJT4 138.0 KV 511440 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN___4_508054 | Apply single-phase fault on: BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1, near BANN 4 138 kV for 7 cycles with stuck breaker at BANN 4 138 kV. Clear Fault after 10 cycles and trip: BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CACHEJ4_521190 | Apply single-phase fault on: CACHEJ4 138.0 KV 521190 TO G20-016-TAP 138.0 KV 764505 CKT 1, near CACHEJ4 138 kV for 7 cycles with stuck breaker at CACHEJ4 138 kV. Clear Fault after 10 cycles and trip: CACHEJ4 138.0 KV 521190 TO MDCPRK4 138.0 KV 520404 CKT 1 LOAD 1 520404 MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 LOAD 1 521024 PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEOCOR4_514778 | Apply single-phase fault on: CLEOCOR4 138.0 KV 514778 TO CLEOPLT4 138.0 KV 515562 CKT 1, near CLEOCOR4 138 kV for 7 cycles with stuck breaker at CLEOCOR4 138 kV. Clear Fault after 10 cycles and trip: CLEOCOR4 138.0 KV 514778 TO SUNDANC4 138.0 KV 516025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEOPLT4_515562 | Apply single-phase fault on: CLEOPLT4 138.0 KV 515562 TO CLEO PL4 138.0 KV 515553 CKT 1, near CLEOPLT4 138 kV for 7 cycles with stuck breaker at CLEOPLT4 138 kV. Clear Fault after 10 cycles and trip: CLEOPLT4 138.0 KV 515562 TO MENOTAP4 138.0 KV 514789 CKT 1 LOAD 1 514789 MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COMMTAP4_511494 | Apply single-phase fault on: COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1, near COMMTAP4 138 kV for 7 cycles with stuck breaker at COMMTAP4 138 kV. Clear Fault after 10 cycles and trip: COMMTAP4 138.0 KV 511494 TO L.E.S.-4 138.0 KV 511467 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CROCKET7_509241 | Apply single-phase fault on: CROCKET7 345.0 KV 509241 TO 7GRIMES% 345.0 KV 334028 CKT 1, near CROCKET7 345 kV for 6 cycles with stuck breaker at CROCKET7 345 kV. Clear Fault after 10 cycles and trip: CROCKET7 345.0 KV 509241 TO TENRUSK7 345.0 KV 508585 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DEWEY__4_514787 | Apply single-phase fault on: DEWEY 4 138.0 KV 514787 TO TALOGA 4 138.0 KV 521065 CKT 1, near DEWEY 4 138 kV for 7 cycles with stuck breaker at DEWEY 4 138 kV. Clear Fault after 10 cycles and trip: REDCLFT4 138.0 KV 515533 TO DEWEY 4 138.0 KV 514787 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EXCLART4_510401 | Apply single-phase fault on: EXCLART4 138.0 KV 510401 TO 510373 CKT 1 510373 TO 510437 CKT 1 509752 TO 510437 CKT 1, near EXCLART4 138 kV for 7 cycles with stuck breaker at EXCLART4 138 kV. Clear Fault after 10 cycles and trip: EXCLART4 138.0 KV 510401 TO PRY_CRK4 138.0 KV 510431 CKT 1 LOAD 1 510431 PRY_CRK4 138.0 KV 510431 TO MCARBDE4 138.0 KV 510366 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FRMNTAP4_514709_0 | Apply single-phase fault on: WOODRNG4 138.0 KV 514714 TO FRMNTAP4 138.0 KV 514709 CKT 1, near FRMNTAP4 138 kV for 7 cycles with stuck breaker at FRMNTAP4 138 kV. Clear Fault after 10 cycles and trip: FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 LOAD 1 514712 FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 LOAD 1 515641 PLNSMEN4 138.0 KV 515641 TO BRECKNR4 138.0 KV 514815 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSUPLY2_520919 | Apply single-phase fault on: FTSUPLY2 69.0 KV 520919 TO STOCKHOLM2 69.0 KV 520421 CKT 1 LOAD 1 520421 STOCKHOLM2 69.0 KV 520421 TO BUFBEAR2 69.0 KV 521120 CKT 1, near FTSUPLY2 69 kV for 7 cycles with stuck breaker at FTSUPLY2 69 kV. Clear Fault after 10 cycles and trip: FTSUPLY2 69.0 KV 520919 TO FTSPLY 2 69.0 KV 520456 CKT 1 LOAD 1 520456 LOAD 2 520456 FTSPLY 2 69.0 KV 520456 TO FARGOJCT2 69.0 KV 521196 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSUPLY4_520920 | Apply single-phase fault on: FTSUPLY4 138.0 KV 520920 TO SLEEPBR4 138.0 KV 520922 CKT 1, near FTSUPLY4 138 kV for 7 cycles with stuck breaker at FTSUPLY4 138 kV. Clear Fault after 10 cycles and trip: FTSUPLY4 138.0 KV 520920 TO IODINE 4 138.0 KV 520957 CKT 1 LOAD 1 520957 IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G176_TAP_588779 | Apply single-phase fault on: G17-036_TAP 138.0 KV 588779 TO GEN-2017-036 138.0 KV 588780 CKT 1, near G17-036_TAP 138 kV for 7 cycles with stuck breaker at G17-036_TAP 138 kV. Clear Fault after 10 cycles and trip: SNYDER-4 138.0 KV 511435 TO G17-036_TAP 138.0 KV 588779 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G185_TAP_762467 | Apply single-phase fault on: G18-015-TAP 345.0 KV 762467 TO G17-151TAP 345.0 KV 762216 CKT 1, near G18-015-TAP 345 kV for 6 cycles with stuck breaker at G18-015-TAP 345 kV. Clear Fault after 10 cycles and trip: G18-015-TAP 345.0 KV 762467 TO L.E.S.-7 345.0 KV 511468 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G18_092_PROX_763215 | Apply single-phase fault on: G18-092-PROX 345.0 KV 763215 TO CRAWFISH_DR 345.0 KV 560022 CKT 2, near G18-092-PROX 345 kV for 6 cycles with stuck breaker at G18-092-PROX 345 kV. Clear Fault after 10 cycles and trip: G18-092-PROX 345.0 KV 763215 TO O.K.U.-7 345.0 KV 511456 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GOTEBO_2_520925 | Apply single-phase fault on: GOTEBO 2 69.0 KV 520925 TO LTELKSW2 69.0 KV 521137 CKT 1, near GOTEBO 2 69 kV for 7 cycles with stuck breaker at GOTEBO 2 69 kV. Clear Fault after 10 cycles and trip: STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 STALOGA2 69.0 KV 520454 TO PUTNAM 2 69.0 KV 521033 CKT 1 LOAD 1 521033 HM-BTTP2 69.0 KV 520942 TO PUTNAM 2 69.0 KV 521033 CKT 1 LOAD 1 521033 ARAPAHO2 69.0 KV 520815 TO HM-BTTP2 69.0 KV 520942 CKT 1 ARAPAHO2 69.0 KV 520815 TO INDPARK2 69.0 KV 520955 CKT 1 LOAD 1 520955 WCORDELLJ2 69.0 KV 520424 TO INDPARK2 69.0 KV 520955 CKT 1 LOAD 1 520955 WCORDELLJ2 69.0 KV 520424 TO CORDELL2 69.0 KV 520866 CKT 1 LOAD 1 520866 CORDELL2 69.0 KV 520866 TO GOTEBO 2 69.0 KV 520925 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRACMNT7_515800 | Apply single-phase fault on: GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1, near GRACMNT7 345 kV for 6 cycles with stuck breaker at GRACMNT7 345 kV. Clear Fault after 10 cycles and trip: GRACMNT7 345.0 KV 515800 TO MINCO 7 345.0 KV 514801 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GROVE__4_510402 | Apply single-phase fault on: PRY-JCT4 138.0 KV 510419 TO BIRDHOL4 138.0 KV 510398 CKT 1 LOAD 1 510398 BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 LOAD 1 510421 JAY 4 138.0 KV 510421 TO GROVE 4 138.0 KV 510402 CKT 1, near GROVE 4 138 kV for 7 cycles with stuck breaker at GROVE 4 138 kV. Clear Fault after 10 cycles and trip: GROVE 4 138.0 KV 510402 TO COWSKIN 4 138.0 KV 512719 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HOB_JCT4_511463 | Apply single-phase fault on: HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1, near HOB-JCT4 138 kV for 7 cycles with stuck breaker at HOB-JCT4 138 kV. Clear Fault after 10 cycles and trip: HOB-JCT4 138.0 KV 511463 TO CL-AFTP4 138.0 KV 511446 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HUNTERS7_515476 | Apply single-phase fault on: HUNTERS7 345.0 KV 515476 TO WOODRNG7 345.0 KV 514715 CKT 1, near HUNTERS7 345 kV for 6 cycles with stuck breaker at HUNTERS7 345 kV. Clear Fault after 10 cycles and trip: HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | IMO____4_514790 | Apply single-phase fault on: CLEOPLT4 138.0 KV 515562 TO MENOTAP4 138.0 KV 514789 CKT 1 LOAD 1 514789 MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1, near IMO 4 138 kV for 7 cycles with stuck breaker at IMO 4 138 kV. Clear Fault after 10 cycles and trip: IMO 4 138.0 KV 514790 TO GLENWD 4 138.0 KV 514734 CKT 1 LOAD 1 514734 GLENWD 4 138.0 KV 514734 TO NE ENID4 138.0 KV 514769 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JOHNCO_7_514809 | Apply single-phase fault on: JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1, near JOHNCO 7 345 kV for 6 cycles with stuck breaker at JOHNCO 7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO PITTSB-7 345.0 KV 510907 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LEBROCK7_508572 | Apply single-phase fault on: LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1, near LEBROCK7 345 kV for 6 cycles with stuck breaker at LEBROCK7 345 kV. Clear Fault after 10 cycles and trip: LEBROCK7 345.0 KV 508572 TO PIRKEY 7 345.0 KV 508563 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LES4_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LES7_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO G18-015-TAP 345.0 KV 762467 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LWS_NTP4_511471 | Apply single-phase fault on: LWS-NTP4 138.0 KV 511471 TO LWS N4 138.0 KV 511430 CKT 1, near LWS-NTP4 138 kV for 7 cycles with stuck breaker at LWS-NTP4 138 kV. Clear Fault after 10 cycles and trip: LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LYDIA__7_508298 | Apply single-phase fault on: LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1, near LYDIA 7 345 kV for 6 cycles with stuck breaker at LYDIA 7 345 kV. Clear Fault after 10 cycles and trip: LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MOORLND4_520999 | Apply single-phase fault on: MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1, near MOORLND4 138 kV for 7 cycles with stuck breaker at MOORLND4 138 kV. Clear Fault after 10 cycles and trip: MOORLND4 138.0 KV 520999 TO GLASMTN4 138.0 KV 514788 CKT 1 LOAD 1 514788 LOAD 2 514788 GLASMTN4 138.0 KV 514788 TO CLEOCOR4 138.0 KV 514778 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MORWODS4_521001 | Apply single-phase fault on: MORWODS4 138.0 KV 521001 TO ELLIS 4 138.0 KV 511561 CKT 1 LOAD 1 511561 ELLIS 4 138.0 KV 511561 TO CUSTER 4 138.0 KV 520459 CKT 1 LOAD 1 520459 CUSTER 4 138.0 KV 520459 TO 521116 CKT 1, near MORWODS4 138 kV for 7 cycles with stuck breaker at MORWODS4 138 kV. Clear Fault after 10 cycles and trip: MORWODS4 138.0 KV 521001 TO MORWOOD4 138.0 KV 521002 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NINMLTP4_521128 | Apply single-phase fault on: NINMLTP4 138.0 KV 521128 TO MORWODS4 138.0 KV 521001 CKT 1, near NINMLTP4 138 kV for 7 cycles with stuck breaker at NINMLTP4 138 kV. Clear Fault after 10 cycles and trip: NINMLTP4 138.0 KV 521128 TO BEARCAT4 138.0 KV 520500 CKT 1 LOAD 1 520500 BEARCAT4 138.0 KV 520500 TO ASPEN 4 138.0 KV 520462 CKT 1 LOAD 1 520462 ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NWTXARK4_508071 | Apply single-phase fault on: NWTXARK4 138.0 KV 508071 TO NASH 4 138.0 KV 508049 CKT 1, near NWTXARK4 138 kV for 7 cycles with stuck breaker at NWTXARK4 138 kV. Clear Fault after 10 cycles and trip: NWTXARK4 138.0 KV 508071 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NWTXARK7_508072 | Apply single-phase fault on: NWTXARK7 345.0 KV 508072 TO TURK 7 345.0 KV 507455 CKT 1, near NWTXARK7 345 kV for 6 cycles with stuck breaker at NWTXARK7 345 kV. Clear Fault after 10 cycles and trip: NWTXARK7 345.0 KV 508072 TO WILKES 7 345.0 KV 508841 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NWT_BNT4_508070 | Apply single-phase fault on: NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1, near NWT-BNT4 138 kV for 7 cycles with stuck breaker at NWT-BNT4 138 kV. Clear Fault after 10 cycles and trip: BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OKEENE_4_521016 | Apply single-phase fault on: OKEENE 4 138.0 KV 521016 TO CDRDLTP4 138.0 KV 520848 CKT 1, near OKEENE 4 138 kV for 7 cycles with stuck breaker at OKEENE 4 138 kV. Clear Fault after 10 cycles and trip: OKEENE 4 138.0 KV 521016 TO WATNGSW4 138.0 KV 520536 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PINTAIL7_516010 | Apply single-phase fault on: PINTAIL7 345.0 KV 516010 TO WOODRNG7 345.0 KV 514715 CKT 1, near PINTAIL7 345 kV for 6 cycles with stuck breaker at PINTAIL7 345 kV. Clear Fault after 10 cycles and trip: PINTAIL7 345.0 KV 516010 TO SOONER 7 345.0 KV 514803 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIRKEY_7_508563 | Apply single-phase fault on: PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1, near PIRKEY 7 345 kV for 6 cycles with stuck breaker at PIRKEY 7 345 kV. Clear Fault after 10 cycles and trip: LEBROCK7 345.0 KV 508572 TO PIRKEY 7 345.0 KV 508563 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PRY_JCT2_510400 | Apply single-phase fault on: PRY-JCT2 69.0 KV 510400 TO ADAIR--2 69.0 KV 510387 CKT 1 LOAD 1 510387 ADAIR--2 69.0 KV 510387 TO VINITA-2 69.0 KV 510404 CKT 1, near PRY-JCT2 69 kV for 7 cycles with stuck breaker at PRY-JCT2 69 kV. Clear Fault after 10 cycles and trip: PRY-JCT2 69.0 KV 510400 TO PRYORC12 69.0 KV 512810 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PRY_JCT4_510419 | Apply single-phase fault on: PRY-JCT4 138.0 KV 510419 TO BIRDHOL4 138.0 KV 510398 CKT 1 LOAD 1 510398 BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 LOAD 1 510421 JAY 4 138.0 KV 510421 TO GROVE 4 138.0 KV 510402 CKT 1, near PRY-JCT4 138 kV for 7 cycles with stuck breaker at PRY-JCT4 138 kV. Clear Fault after 10 cycles and trip: PRY-JCT4 138.0 KV 510419 TO G20-092-TAP 138.0 KV 764160 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ROMNOSE4_514823_0 | Apply single-phase fault on: ROMNOSE4 138.0 KV 514823 TO SOUTHRD4 138.0 KV 514822 CKT 1 LOAD 1 514822 LOAD 2 514822 SOUTHRD4 138.0 KV 514822 TO CANTNLK4 138.0 KV 515964 CKT 1 LOAD 1 515964 CANTNLK4 138.0 KV 515964 TO DEWEY 4 138.0 KV 514787 CKT 1, near ROMNOSE4 138 kV for 7 cycles with stuck breaker at ROMNOSE4 138 kV. Clear Fault after 10 cycles and trip: ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RUSSELL4_521043 | Apply single-phase fault on: RUSSELL4 138.0 KV 521043 TO 512110 CKT 1, near RUSSELL4 138 kV for 7 cycles with stuck breaker at RUSSELL4 138 kV. Clear Fault after 10 cycles and trip: RUSSELL4 138.0 KV 521043 TO ALTUSJT4 138.0 KV 511440 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_2_511475 | Apply single-phase fault on: SNYDER-2 69.0 KV 511475 TO TOMSTEED2 69.0 KV 511495 CKT 1, near SNYDER-2 69 kV for 7 cycles with stuck breaker at SNYDER-2 69 kV. Clear Fault after 10 cycles and trip: SNYDER-2 69.0 KV 511475 TO TIPTE T2 69.0 KV 511472 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_2_521051 | Apply single-phase fault on: SNYDER 2 69.0 KV 521051 TO SNYDRSB2 69.0 KV 520541 CKT Z1 LOAD 1 520541 SNYDRSB2 69.0 KV 520541 TO NAVJOTP2 69.0 KV 521009 CKT 1, near SNYDER 2 69 kV for 7 cycles with stuck breaker at SNYDER 2 69 kV. Clear Fault after 10 cycles and trip: SNYDER 2 69.0 KV 521051 TO TIPTONJ2 69.0 KV 521070 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_4_511435 | Apply single-phase fault on: SNYDER-4 138.0 KV 511435 TO SNYDER 4 138.0 KV 521052 CKT 1, near SNYDER-4 138 kV for 7 cycles with stuck breaker at SNYDER-4 138 kV. Clear Fault after 10 cycles and trip: SNYDER-4 138.0 KV 511435 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SNYDER_4_521052 | Apply single-phase fault on: SNYDER 4 138.0 KV 521052 TO G20-016-TAP 138.0 KV 764505 CKT 1, near SNYDER 4 138 kV for 7 cycles with stuck breaker at SNYDER 4 138 kV. Clear Fault after 10 cycles and trip: SNYDER 4 138.0 KV 521052 TO SNYDER-4 138.0 KV 511435 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUNNYSD4_515135 | Apply single-phase fault on: SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 LOAD 1 515137 UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 LOAD 1 515372 CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1, near SUNNYSD4 138 kV for 7 cycles with stuck breaker at SUNNYSD4 138 kV. Clear Fault after 10 cycles and trip: SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUNNYSD7_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | TALOGA_2_521064 | Apply single-phase fault on: TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 LOAD 1 521082 VICI 2 69.0 KV 521082 TO WOODWRD2 69.0 KV 521096 CKT 1, near TALOGA 2 69 kV for 7 cycles with stuck breaker at TALOGA 2 69 kV. Clear Fault after 10 cycles and trip: TALOGA 2 69.0 KV 521064 TO CANTON-2 69.0 KV 520843 CKT 1 LOAD 1 520843 LOAD 2 520843 CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TALOGA_4_521065 | Apply single-phase fault on: TALOGA 4 138.0 KV 521065 TO DEWEY 4 138.0 KV 514787 CKT 1, near TALOGA 4 138 kV for 7 cycles with stuck breaker at TALOGA 4 138 kV. Clear Fault after 10 cycles and trip: G20-010-TAP 138.0 KV 765215 TO TALOGA 4 138.0 KV 521065 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TERRYRD7_511568 | Apply single-phase fault on: TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345 kV for 6 cycles with stuck breaker at TERRYRD7 345 kV. Clear Fault after 10 cycles and trip: TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TURK___7_507455 | Apply single-phase fault on: TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1, near TURK 7 345 kV for 6 cycles with stuck breaker at TURK 7 345 kV. Clear Fault after 10 cycles and trip: TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VALIANT7_510911 | Apply single-phase fault on: TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1, near VALIANT7 345 kV for 6 cycles with stuck breaker at VALIANT7 345 kV. Clear Fault after 10 cycles and trip: LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WAUKOTP4_514711 | Apply single-phase fault on: WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1, near WAUKOTP4 138 kV for 7 cycles with stuck breaker at WAUKOTP4 138 kV. Clear Fault after 10 cycles and trip: WAUKOTP4 138.0 KV 514711 TO WAUKOMI4 138.0 KV 514710 CKT 1 LOAD 1 514710 WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WELSH__7_508359 | Apply single-phase fault on: WELSH 7 345.0 KV 508359 TO LYDIA 7 345.0 KV 508298 CKT 1, near WELSH 7 345 kV for 6 cycles with stuck breaker at WELSH 7 345 kV. Clear Fault after 10 cycles and trip: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WILKES_7_508841 | Apply single-phase fault on: WILKES 7 345.0 KV 508841 TO LONGWD 7 345.0 KV 508809 CKT 1 LOAD 1 508311, near WILKES 7 345 kV for 6 cycles with stuck breaker at WILKES 7 345 kV. Clear Fault after 10 cycles and trip: WILKES 7 345.0 KV 508841 TO NWTXARK7 345.0 KV 508072 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 - Southeast | 25W | Transfer | WOODRNG4_514714 | Apply single-phase fault on: WOODRNG4 138.0 KV 514714 TO FRMNTAP4 138.0 KV 514709 CKT 1, near WOODRNG4 138 kV for 7 cycles with stuck breaker at WOODRNG4 138 kV. Clear Fault after 10 cycles and trip: WOODRNG4 138.0 KV 514714 TO OTTER 4 138.0 KV 514708 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG7_514715 | Apply single-phase fault on: WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1, near WOODRNG7 345 kV for 6 cycles with stuck breaker at WOODRNG7 345 kV. Clear Fault after 10 cycles and trip: WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODWRD2_521096 | Apply single-phase fault on: WOODWRD2 69.0 KV 521096 TO CRTSJCT2 69.0 KV 521197 CKT 1, near WOODWRD2 69 kV for 7 cycles with stuck breaker at WOODWRD2 69 kV. Clear Fault after 10 cycles and trip: WOODWRD2 69.0 KV 521096 TO WODWRD 2 69.0 KV 514782 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV4_515376 | Apply single-phase fault on: WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1, near WWRDEHV4 138 kV for 7 cycles with stuck breaker at WWRDEHV4 138 kV. Clear Fault after 10 cycles and trip: WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_63_P4_2_TWNLKSW4 | Apply single-phase fault on LINE 520882 TO 520535 CKT 1, near TWNLKSW4 for 6 cycles with stuck breaker at TWNLKSW4 (521073) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520533 TO 520865 CKT 1 and LINE 521073 TO 520540 CKT Z1 and drop LOAD 1 520879 and drop LOAD 1 520540 and DISCONNECT 520879 and DISCONNECT 520540 and drop LOAD 1 521037 and drop LOAD 1 515930 and drop LOAD 1 520546 and drop LOAD 1 520479 and DISCONNECT 521037 and DISCONNECT 520474 and DISCONNECT 515930 and DISCONNECT 520545 and DISCONNECT 520546 and DISCONNECT 520847 and DISCONNECT 520479 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_76_P4_TONECE5 | Apply single-phase fault on and DISCONNECT 527964, near TONECE5 for 15 cycles with stuck breaker at TONECE5 (512751) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_63_P4_2_TWNLKSW4 | Apply single-phase fault on LINE 520882 TO 520535 CKT 1, near TWNLKSW4 for 6 cycles with stuck breaker at TWNLKSW4 (521073) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520533 TO 520865 CKT 1 and LINE 521073 TO 520540 CKT Z1 and drop LOAD 1 520879 and drop LOAD 1 520540 and DISCONNECT 520879 and DISCONNECT 520540 and drop LOAD 1 521037 and drop LOAD 1 515930 and drop LOAD 1 520546 and drop LOAD 1 520479 and DISCONNECT 521037 and DISCONNECT 520474 and DISCONNECT 515930 and DISCONNECT 520545 and DISCONNECT 520546 and DISCONNECT 520847 and DISCONNECT 520479 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_76_P4_TONECE5 | Apply single-phase fault on and DISCONNECT 527964, near TONECE5 for 15 cycles with stuck breaker at TONECE5 (512751) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | 112GORE4__LAIRGST4 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | 7_RIVERS___6__PECOS______6 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 230.0 KV 528095 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ACCO_______2__CLUTTER____2 | 3 Phase fault on ACCO 2 (526249) 69 kV Bus a. Apply fault at the ACCO 2 (526249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACCO 2 69.0 KV 526249 TO CLUTTER 2 69.0 KV 526310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ALLEN______3__LP_WHEELOCK3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO LP-WHEELOCK3 115.0 KV 526236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ALLEN______3__LUBBCK_STH_3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO LUBBCK_STH 3 115.0 KV 526268 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ALLEN______3__SP_QUAKER__3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO SP-QUAKER 3 115.0 KV 526243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ALRDCRTZ_TP3__CORTEZ_____3 | 3 Phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLRED_SUB 3 115.0 KV 527024 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 b.2. APACHE_ROB 3 115.0 KV 527022 TO ALLRED_SUB 3 115.0 KV 527024 CKT 1 b.3. LOAD 1 527024 b.4. CORTEZ 3 115.0 KV 527021 TO APACHE_ROB 3 115.0 KV 527022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ALRDCRTZ_TP3__SHELLC3_TP_3 | 3 Phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALRDCRTZ_TP3 115.0 KV 527030 TO XTO_CORNEL+3 115.0 KV 527033 CKT 1 b.2. LOAD 1 527033 b.3. XTO_CORNEL+3 115.0 KV 527033 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | AMERADA____3__SEMINOLE___3 | 3 Phase fault on AMERADA 3 (527242) 115 kV Bus a. Apply fault at the AMERADA 3 (527242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMERADA 3 115.0 KV 527242 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | AMOCO_TP___3__AMOCO_CRYO_3 | 3 Phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_TP 3 115.0 KV 526445 TO AMOCO_CRYO 3 115.0 KV 526452 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ANADARK4__CHERRYRD_4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ANADARK4__GEORGIA4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ANADARK4__POCASET4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ANDREWS____3__NA_ENRICH__3 | 3 Phase fault on ANDREWS 3 (528602) 115 kV Bus a. Apply fault at the ANDREWS 3 (528602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ARCO_TP____3__ARCO_TP____3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNETT 3 115.0 KV 527018 TO ARCO_TP 3 115.0 KV 527041 CKT 1 b.2. BENNETT 3 115.0 KV 527018 TO ODC_TP 3 115.0 KV 527051 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ARCO_TP____3__OXY_WILRD1_3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO_TP 3 115.0 KV 527041 TO OXY_WILRD1 3 115.0 KV 527047 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ARTESIA____3__EAGLE_CREEK3 | 3 Phase fault on ARTESIA 3 (527707) 115 kV Bus a. Apply fault at the ARTESIA 3 (527707) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTESIA 3 115.0 KV 527707 TO EAGLE_CREEK3 115.0 KV 527711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ARTSA_CC_TP3__ATOKA______3 | 3 Phase fault on ARTSA_CC_TP3 (527777) 115 kV Bus a. Apply fault at the ARTSA_CC_TP3 (527777) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTSA_CC_TP3 115.0 KV 527777 TO ATOKA 3 115.0 KV 527786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ARTVLTP4__LWS_NTP4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 b.2. LWS-NTP4 138.0 KV 511471 TO 53CACHE4 138.0 KV 511509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ATOKA______3__CV_IRISHHL_3 | 3 Phase fault on ATOKA 3 (527786) 115 kV Bus a. Apply fault at the ATOKA 3 (527786) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA 3 115.0 KV 527786 TO CV-IRISHHL+3 115.0 KV 528116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BLANCO_____3__CROSBY_____3 | 3 Phase fault on BLANCO 3 (525803) 115 kV Bus a. Apply fault at the BLANCO 3 (525803) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCO 3 115.0 KV 525803 TO CROSBY 3 115.0 KV 525926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BLUECLDCOL_6__BLUECLDPOI_6 | 3 Phase fault on BLUECLDCOL 6 (525584) 230 kV Bus a. Apply fault at the BLUECLDCOL 6 (525584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDCOL 6 230.0 KV 525584 TO BLUECLDPOI 6 230.0 KV 525585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BLUECLDPOI_6__NEEDMORE___6 | 3 Phase fault on BLUECLDPOI 6 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 230.0 KV 525585 TO NEEDMORE 6 230.0 KV 525586 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BORDER_____7__CRAWFISH_DR | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO CRAWFISH_DR 345.0 KV 560022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BRU_SUB____6__OXYBRU_____6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO OXYBRU 6 230.0 KV 527010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BRU_SUB____6__XTO_MAHONEY6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BUCKEYE_TP_3__BUCKEYE____3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO BUCKEYE 3 115.0 KV 528385 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BUCKEYE_TP_3__LE_TXACO_TP3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BYRD_TP____3__BYRD_______3 | 3 Phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRD_TP 3 115.0 KV 528581 TO BYRD 3 115.0 KV 528582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CALLAHAN___3__FLOYD_CNTY_3 | 3 Phase fault on CALLAHAN 3 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 115.0 KV 525763 TO FLOYD_CNTY 3 115.0 KV 525780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CANNON_TP__3__CANNONAFB__3 | 3 Phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANNON_TP 3 115.0 KV 524790 TO CANNONAFB 3 115.0 KV 524794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CANNON_TP__3__FE_CLVS_INT3 | 3 Phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_CLOVIS 3 115.0 KV 524784 TO CANNON_TP 3 115.0 KV 524790 CKT 1 b.2. W_CLOVIS 3 115.0 KV 524784 TO FE-CLVS_INT3 115.0 KV 524808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CAPITAN____3__ROSWLL_INT_3 | 3 Phase fault on CAPITAN 3 (527541) 115 kV Bus a. Apply fault at the CAPITAN 3 (527541) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAPITAN 3 115.0 KV 527541 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CAPROCK____3__NORTON_____3 | 3 Phase fault on CAPROCK 3 (524486) 115 kV Bus a. Apply fault at the CAPROCK 3 (524486) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAPROCK 3 115.0 KV 524486 TO NORTON 3 115.0 KV 524502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARDINAL___3__LIVSTNRIDGE3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 b.2. MEDANOS 3 115.0 KV 527954 TO SAGE_BRUSH 3 115.0 KV 527955 CKT 1 b.3. LOAD 1 527955 b.4. LOAD 1* 527955 b.5. LIVSTNRIDGE3 115.0 KV 527953 TO MEDANOS 3 115.0 KV 527954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARDINAL___3__S_JAL______3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO CARDINAL 3 115.0 KV 528596 CKT 1 b.2. TEAGUE 3 115.0 KV 528526 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARLISLE___3__LP_DOUD_TP_3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO LP-DOUD_TP 3 115.0 KV 526162 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARLISLE___3__MURPHY_____3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO MURPHY 3 115.0 KV 526192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARLSBAD___3__PECOS______3 | 3 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 115.0 KV 528160 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARNEG_4__S_W_S__4 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARTER_4__CHIKSAW4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARTER_4__HONEYCK4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARTRCO4__GEN_2017_027 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARTRCO4__ORIGINW4 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CASTRO_CNTY3__BETHEL_COL13 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO BETHEL_COL13 115.0 KV 524757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CASTRO_CNTY3__NEWHART____3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CASTRO_CNTY3__TIERABLANCA3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#21 3 115.0 KV 524734 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 b.2. TIERABLANCA3 115.0 KV 524630 TO DS-#21 3 115.0 KV 524734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHAN_TASCOS6__POTTER_CO__6 | 3 Phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 230.0 KV 523869 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHAVES_CNTY3__PRICE_TAP__3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO PRICE_TAP 3 115.0 KV 527509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHAVES_CNTY3__SAMSON_____3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO SAMSON 3 115.0 KV 527546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHAVES_CNTY3__URTON______3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO URTON 3 115.0 KV 527501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHEEKTP4__CHEEK_4 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | CHISHOLM7__POTTER_CO__7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO POTTER_CO 7 345.0 KV 523961 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | CHVS_SLRCOL3__CHAVES_CNTY3 | 3 Phase fault on CHVS_SLRCOL3 (527470) 115 kV Bus a. Apply fault at the CHVS_SLRCOL3 (527470) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHVS_SLRCOL3 115.0 KV 527470 TO CHAVES_CNTY3 115.0 KV 527482 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | IDV crashes when ran with reclose. | Removing reclose prevents IDV from crashing.
05 - Southwest | 25S | Transfer | CLVLDSW4__ANADARK4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COMANC_2__L_DISTP2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L-DISTP2 69.0 KV 511524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COOPER_RNCH3__BYRD_TP____3 | 3 Phase fault on COOPER_RNCH3 (528554) 115 kV Bus a. Apply fault at the COOPER_RNCH3 (528554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_RNCH3 115.0 KV 528554 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COX________3__CALLAHAN___3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO CALLAHAN 3 115.0 KV 525763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COX________3__HALE_CNTY__3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CRAWFISH_DR__G17_151TAP | 3 Phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR 345.0 KV 560022 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | CRAWFISH_DR__G18_015_TAP | 3 Phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR 345.0 KV 560022 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | CRAWFISH_DR__G18_092_PROX | 3 Phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR 345.0 KV 560022 TO G18-092-PROX 345.0 KV 763215 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | CROSBY_____2__LH_CROSBY__2 | 3 Phase fault on CROSBY 2 (525925) 69 kV Bus a. Apply fault at the CROSBY 2 (525925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 2 69.0 KV 525925 TO LH-CROSBY +2 69.0 KV 525936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CROSBY_____3__LUBBCK_EST_3 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CROSSROADS_7__HOBBS_INT__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT LX c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CROSSROADS_7__SAGA_SDCOL_7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 b.2. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SCOL 7 345.0 KV 527610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNIGHM_N_6__POTASH_JCT_6 | 3 Phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAM__3__BUCKEYE_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAM__3__HOBBS_INT__3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO HOBBS_INT 3 115.0 KV 527891 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAM__3__MADDOX_____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAM__3__MONUMNT_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MONUMNT_TP 3 115.0 KV 528568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAM__3__QUAHADA____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CURRY______3__BAILEYCO___3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CURRY______3__PLSNT_HILL_3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E_CLOVIS 3 115.0 KV 524773 TO CURRY 3 115.0 KV 524822 CKT 1 b.2. LOAD 1 524822 b.3. PLSNT_HILL 3 115.0 KV 524768 TO E_CLOVIS 3 115.0 KV 524773 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CURRY______3__ROOSEVELT__3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO ROOSEVELT 3 115.0 KV 524908 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUSTERMTN__3__PONDEROSA__3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO PONDEROSA 3 115.0 KV 528240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUSTERMTN__3__WHITTEN____3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO WHITTEN 3 115.0 KV 528540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CV_8_MILE__3__CV_TURKYTRK3 | 3 Phase fault on CV-8_MILE 3 (527809) 115 kV Bus a. Apply fault at the CV-8_MILE 3 (527809) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CV-8_MILE 3 115.0 KV 527809 TO CV-TURKYTRK3 115.0 KV 527822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CV_AZMESA__3__PECOS______3 | 3 Phase fault on CV-AZMESA 3 (528070) 115 kV Bus a. Apply fault at the CV-AZMESA 3 (528070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CV-AZMESA 3 115.0 KV 528070 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DCP_ZIA_TP_3__DCP_ZIA____3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCP_ZIA TP 3 115.0 KV 528422 TO DCP_ZIA 3 115.0 KV 528423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DEAFSMITH__6__G17_146_TAP | 3 Phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 230.0 KV 524623 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DENVER_N___3__MUSTANG____3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DENVER_S___3__MUSTANG____3 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3 (527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 115.0 KV 527136 TO MUSTANG 3 115.0 KV 527146 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DFSMTH_EST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_EST 3 (524619) 115 kV Bus a. Apply fault at the DFSMTH_EST 3 (524619) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_EST 3 115.0 KV 524619 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DFSMTH_WST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_WST 3 (524622) 115 kV Bus a. Apply fault at the DFSMTH_WST 3 (524622) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_WST 3 115.0 KV 524622 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DIAMONDBACK3__FLATLAND___3 | 3 Phase fault on DIAMONDBACK3 (527212) 115 kV Bus a. Apply fault at the DIAMONDBACK3 (527212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK3 115.0 KV 527212 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DS_CASTRO__2__CASTRO_CNTY2 | 3 Phase fault on DS-CASTRO 2 (524728) 69 kV Bus a. Apply fault at the DS-CASTRO 2 (524728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-CASTRO 2 69.0 KV 524728 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DS__15&_19_2__CASTRO_CNTY2 | 3 Phase fault on DS-#15&#19+2 (524721) 69 kV Bus a. Apply fault at the DS-#15&#19+2 (524721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#15&#19+2 69.0 KV 524721 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DS__20_____3__CURRY______3 | 3 Phase fault on DS-#20 3 (524669) 115 kV Bus a. Apply fault at the DS-#20 3 (524669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#20 3 115.0 KV 524669 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DS__22_____3__CASTRO_CNTY3 | 3 Phase fault on DS-#22 3 (524694) 115 kV Bus a. Apply fault at the DS-#22 3 (524694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#22 3 115.0 KV 524694 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DS__25_____3__TIERABLANCA3 | 3 Phase fault on DS-#25+ 3 (524575) 115 kV Bus a. Apply fault at the DS-#25+ 3 (524575) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#25+ 3 115.0 KV 524575 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DS__3______2__CASTRO_CNTY2 | 3 Phase fault on DS-#3 2 (524688) 69 kV Bus a. Apply fault at the DS-#3 2 (524688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#3 2 69.0 KV 524688 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DUNCAN_4__OMDUNCN4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EAGLE_CREEK3__7_RIVERS___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO 7-RIVERS 3 115.0 KV 528094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EAGLE_CREEK3__ARTSA_CC_TP3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO ARTSA_CC_TP3 115.0 KV 527777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EAGLE_CREEK3__EDDY_NTH___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EAGLE_CREEK3__NAVAJO_2TP_3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO NAVAJO_2TP 3 115.0 KV 527715 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EAGLE_CREEK3__NAVAJO_5TP_3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO NAVAJO_5TP 3 115.0 KV 527736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_NTH___3__CV_8_MILE__3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NTH 3 115.0 KV 527798 TO CV-8_MILE 3 115.0 KV 527809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_NTH___3__ROSWLL_INT_3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWEEDY 3 115.0 KV 527597 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 b.2. ROSWLL_INT 3 115.0 KV 527564 TO TWEEDY 3 115.0 KV 527597 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_STH___3__ATOKA______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 b.2. LOAD 1 527821 b.3. ATOKA 3 115.0 KV 527786 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_STH___3__PECOS______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ELGINJT2__CORNVIL2 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CYRIL--2 69.0 KV 511451 TO ELGINJT2 69.0 KV 511487 CKT 1 b.2. LOAD 1 511487 b.3. CORNVIL2 69.0 KV 511450 TO CYRIL--2 69.0 KV 511451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ELGINJT2__FT_SILL2 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PO.HILL2 69.0 KV 511473 TO ELGINJT2 69.0 KV 511487 CKT 1 b.2. LOAD 1 511487 b.3. FT.SILL2 69.0 KV 511461 TO PO.HILL2 69.0 KV 511473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ELGINJT4__S_W_S__4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EL_PASO____3__DENVER_N___3 | 3 Phase fault on EL_PASO 3 (527080) 115 kV Bus a. Apply fault at the EL_PASO 3 (527080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL_PASO 3 115.0 KV 527080 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ENRON_TP___3__ENRON______3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO ENRON 3 115.0 KV 528318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ENRON_TP___3__LEA_NATIONL3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EUNICE_____3__CARDINAL___3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EUNICE_____3__DRINKARD_TP3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | FE_CLVS_INT3__A12_02&13_05 | 3 Phase fault on FE-CLVS_INT3 (524808) 115 kV Bus a. Apply fault at the FE-CLVS_INT3 (524808) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FE-CLVS_INT3 115.0 KV 524808 TO A12-02&13-05 115.0 KV 583280 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | FLATLAND___3__GEN_2017_187 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO GEN-2017-187 115.0 KV 761796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | FLATLAND___3__SULPHUR____3 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO SULPHUR 3 115.0 KV 527262 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-187 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2017-187 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25S | Transfer | FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | FLOYD_CNTY_3__BLANCO_____3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G16_063_TAP__GEN_2016_063 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2016-063 345.0 KV 587430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G16_063_TAP__GEN_2017_075 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G18_015_TAP__G18_092_PROX | 3 Phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-015-TAP 345.0 KV 762467 TO G18-092-PROX 345.0 KV 763215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G20_067_TAP__GEN_2020_068 | 3 Phase fault on G20-067-TAP (764945) 345 kV Bus a. Apply fault at the G20-067-TAP (764945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-067-TAP 345.0 KV 764945 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G20_068_SS1__GEN_2020_068 | 3 Phase fault on G20-068-SS1 (764948) 345 kV Bus a. Apply fault at the G20-068-SS1 (764948) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-068-SS1 345.0 KV 764948 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G20_068_SS2__GEN_2020_068 | 3 Phase fault on G20-068-SS2 (764949) 345 kV Bus a. Apply fault at the G20-068-SS2 (764949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-068-SS2 345.0 KV 764949 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G20_075_TAP__GEN_2020_087 | 3 Phase fault on G20-075-TAP (764550) 345 kV Bus a. Apply fault at the G20-075-TAP (764550) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-075-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GAINES_PLNT7__SIDEWINDER_7 | 3 Phase fault on GAINES_PLNT7 (527000) 345 kV Bus a. Apply fault at the GAINES_PLNT7 (527000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GAINES_PLNT7 345.0 KV 527000 TO SIDEWINDER 7 345.0 KV 527020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GEN_2017_167__GEN_2017_167 | 3 Phase fault on GEN-2017-167 (761859) 345 kV Bus a. Apply fault at the GEN-2017-167 (761859) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-167 345.0 KV 761859 TO GEN-2017-167 345.0 KV 761880 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GEN_2018_004__G18_004_TAP | 3 Phase fault on GEN-2018-004 (762438) 115 kV Bus a. Apply fault at the GEN-2018-004 (762438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-004 115.0 KV 762438 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GEN_2020_009__G20_009_TAP | 3 Phase fault on GEN-2020-009 (766290) 345 kV Bus a. Apply fault at the GEN-2020-009 (766290) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-009 345.0 KV 766290 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GEN_2020_059__G20_059_TAP | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059 (764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 345.0 KV 764840 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | GEN_2020_067__G20_067_TAP | 3 Phase fault on GEN-2020-067 (764935) 345 kV Bus a. Apply fault at the GEN-2020-067 (764935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-067 345.0 KV 764935 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GEN_2020_074__G20_074_TAP | 3 Phase fault on GEN-2020-074 (764105) 345 kV Bus a. Apply fault at the GEN-2020-074 (764105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-074 345.0 KV 764105 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRACMNT7__GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRASSLAND__3__GRAHAM_____3 | 3 Phase fault on GRASSLAND 3 (526676) 115 kV Bus a. Apply fault at the GRASSLAND 3 (526676) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 3 115.0 KV 526676 TO GRAHAM 3 115.0 KV 526694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRASSLAND__6__CIRRUS_WND_6 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 230.0 KV 526677 TO CIRRUS_WND 6 230.0 KV 526679 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HALECENTER_2__TUCO_INT___2 | 3 Phase fault on HALECENTER 2 (525738) 69 kV Bus a. Apply fault at the HALECENTER 2 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 69.0 KV 525738 TO TUCO_INT 2 69.0 KV 525826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HALE_CNTY__3__PLANT_X____3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HART_INDUST3__LAMTON_____3 | 3 Phase fault on HART_INDUST3 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO LAMTON 3 115.0 KV 525414 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HART_INDUST3__NEWHART____3 | 3 Phase fault on HART_INDUST3 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HEREFORD___3__TIERABLANCA3 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3 (524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 115.0 KV 524606 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HIGG_______3__DENVER_N___3 | 3 Phase fault on HIGG 3 (527363) 115 kV Bus a. Apply fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 b.2. DENVER_N 3 115.0 KV 527130 TO HIGGEAST 3 115.0 KV 527286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HITCHLAND__7__CARPENTER__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO CARPENTER 7 345.0 KV 523823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when these generators trip offline or when the protection settings are disabled to prevent them from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | HITCHLAND__7__G10014G11022 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO G10014G11022 345.0 KV 576397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | HITCHLAND__7__NOBLE_WND__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOBLE_WND 7 345.0 KV 523101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | HITCHLAND__7__NOVUS1_____7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOVUS1 7 345.0 KV 523112 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | HOBBS_INT__3__HIGG_______3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO BENSING 3 115.0 KV 528433 CKT 1 b.2. LOAD 1 528433 b.3. LOAD 1* 528433 b.4. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT__3__LE_WEST_SUB3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO LE-WEST_SUB3 115.0 KV 528333 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT__3__MADDOX_____3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT__3__MILLEN_TPW_3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT__7__G20_059_TAP | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT__7__RDRUNNER___7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT XA c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HUGO___7__G16_063_TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | INK_BASIN__3__A16_008SUB | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO A16-008SUB 115.0 KV 588460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | INK_BASIN__3__ALRDCRTZ_TP3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | INK_BASIN__3__LE_WAITS___3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO LE-WAITS 3 115.0 KV 528325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | IVORY_TP___2__LUBBCK_STH_2 | 3 Phase fault on IVORY_TP 2 (526256) 69 kV Bus a. Apply fault at the IVORY_TP 2 (526256) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IVORY_TP 2 69.0 KV 526256 TO LUBBCK_STH 2 69.0 KV 526267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | IVORY______2__LUBBCK_STH_2 | 3 Phase fault on IVORY 2 (526205) 69 kV Bus a. Apply fault at the IVORY 2 (526205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IVORY 2 69.0 KV 526205 TO LUBBCK_STH 2 69.0 KV 526267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JOHNCO_7__DMNDSPG7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JOHNCO_7__GEN_2017_149 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JOHNCO_7__GEN_2020_015 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2020-015 345.0 KV 764270 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JOHNSON_DRW3__TAYLOR_____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO TAYLOR 3 115.0 KV 528413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | KISER______3__COX________3 | 3 Phase fault on KISER 3 (525272) 115 kV Bus a. Apply fault at the KISER 3 (525272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISER 3 115.0 KV 525272 TO COX 3 115.0 KV 525326 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | KRESS_INT__3__HALE_CNTY__3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | KRESS_INT__3__KRS_RURL_TP3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO KRS_RURL_TP3 115.0 KV 525226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | KRESS_INT__3__NEWHART____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | KRESS_INT__3__SWISHER____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO SWISHER 3 115.0 KV 525212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LAMB_CNTY__2__SUDANRURAL_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 b.2. AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 b.3. LOAD 1 525613 b.4. LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 b.5. LOAD 1 525606 b.6. SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LAMB_CNTY__2__W_ANTON_TP_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 2 69.0 KV 525635 TO LC-LTTLFLD+2 69.0 KV 525650 CKT 1 b.2. LOAD 1 525650 b.3. LC-LTTLFLD+2 69.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LAMB_CNTY__3__HOCKLEY____3 | 3 Phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LAMB_CNTY__6__GEN_2020_017 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 230.0 KV 525637 TO GEN-2020-017 230.0 KV 764825 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LAMTON_____3__HALE_CNTY__3 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 115.0 KV 525414 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LC_BECK____2__SUDANRURAL_2 | 3 Phase fault on LC-BECK +2 (525045) 69 kV Bus a. Apply fault at the LC-BECK +2 (525045) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-BECK +2 69.0 KV 525045 TO SUDANRURAL 2 69.0 KV 525592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LEA_NATIONL3__SUMMIT_3 | 3 Phase fault on LEA_NATIONL3 (528399) 115 kV Bus a. Apply fault at the LEA_NATIONL3 (528399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_NATIONL3 115.0 KV 528399 TO SUMMIT_3 115.0 KV 528404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LEA_ROAD___3__OIL_CENTER_3 | 3 Phase fault on LEA_ROAD 3 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 115.0 KV 528505 TO OIL_CENTER 3 115.0 KV 528552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LEHMAN_TP__3__LEHMAN_____3 | 3 Phase fault on LEHMAN_TP 3 (526350) 115 kV Bus a. Apply fault at the LEHMAN_TP 3 (526350) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEHMAN_TP 3 115.0 KV 526350 TO LEHMAN 3 115.0 KV 526352 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_PLNSINT_2__LE_PLNSGOAB2 | 3 Phase fault on LE-PLNSINT 2 (528626) 69 kV Bus a. Apply fault at the LE-PLNSINT 2 (528626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-PLNSINT 2 69.0 KV 528626 TO LE-PLNSGOAB2 69.0 KV 528709 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_SANANDRS3__LE_TXACO_TP3 | 3 Phase fault on LE-SANANDRS3 (528341) 115 kV Bus a. Apply fault at the LE-SANANDRS3 (528341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS3 115.0 KV 528341 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_TXACO_TP3__LE_TEXACO__3 | 3 Phase fault on LE-TXACO_TP3 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-TXACO_TP3 115.0 KV 528627 TO LE-TEXACO 3 115.0 KV 528792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_WAITS___2__LE_FORT_SW_2 | 3 Phase fault on LE-WAITS 2 (528617) 69 kV Bus a. Apply fault at the LE-WAITS 2 (528617) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 2 69.0 KV 528617 TO LE-FORT_SW 2 69.0 KV 528714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_WAITS___2__LE_TP51____2 | 3 Phase fault on LE-WAITS 2 (528617) 69 kV Bus a. Apply fault at the LE-WAITS 2 (528617) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 2 69.0 KV 528617 TO LE-TP51 2 69.0 KV 528759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_WAITS___3__LE_NRTH_INT3 | 3 Phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 3 115.0 KV 528325 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_WEST_SUB3__LE_NRTH_INT3 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 115.0 KV 528333 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LG_DOCWEBR_2__TERRY_CNTY_2 | 3 Phase fault on LG-DOCWEBR 2 (526506) 69 kV Bus a. Apply fault at the LG-DOCWEBR 2 (526506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-DOCWEBR 2 69.0 KV 526506 TO TERRY_CNTY 2 69.0 KV 526735 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LG_WELLMAN_2__SEAGRAVES__2 | 3 Phase fault on LG-WELLMAN 2 (526993) 69 kV Bus a. Apply fault at the LG-WELLMAN 2 (526993) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-WELLMAN 2 69.0 KV 526993 TO SEAGRAVES 2 69.0 KV 527201 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LG_YEAR4__112GORE4 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LIVSTNRIDGE3__WIPP_______3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO WIPP 3 115.0 KV 528009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LIVSTNRIDGE3__XTO_DI9_TP_3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LOST_DRAW__3__COCHRAN____3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO COCHRAN 3 115.0 KV 526361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LOST_DRAW__3__LEHMAN_TP__3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO LEHMAN_TP 3 115.0 KV 526350 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LP_DOUD_TP_3__SP_WOLF_TP_3 | 3 Phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LP-DOUD_TP 3 115.0 KV 526162 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LRNZ_MPT___3__BLANCO_____3 | 3 Phase fault on LRNZ_MPT 3 (525801) 115 kV Bus a. Apply fault at the LRNZ_MPT 3 (525801) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LRNZ_MPT 3 115.0 KV 525801 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LTFLD_S&CTY2__LAMB_CNTY__2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LTFLD_S&CTY2__W_ANTON_TP_2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_EST_2__CLUTTER____2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 2 69.0 KV 526297 TO CLUTTER 2 69.0 KV 526310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_EST_2__SLATON_____2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 2 69.0 KV 526297 TO SLATON 2 69.0 KV 526562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_EST_2__SW_6786_S__2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANTERS 2 69.0 KV 526284 TO LUBBCK_EST 2 69.0 KV 526297 CKT 1 b.2. SW_6786_S 2 69.0 KV 526087 TO PLANTERS 2 69.0 KV 526284 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_EST_6__GEN_2020_060 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO GEN-2020-060 230.0 KV 764875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_STH_3__LUBBCK_EST_3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_STH_3__LYNN_CNTY__3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO WOODROW 3 115.0 KV 526602 CKT 1 b.2. LOAD 1 526602 b.3. WOODROW 3 115.0 KV 526602 TO LYNN_CNTY 3 115.0 KV 526656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LWSTAP_4__112GORE4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 b.2. LOAD 1 511512 b.3. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LWS_NTP4__112GORE4 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LWS___N4__LWS_NTP4 | 3 Phase fault on LWS N4 (511430) 138 kV Bus a. Apply fault at the LWS N4 (511430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS N4 138.0 KV 511430 TO LWS-NTP4 138.0 KV 511471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LYNN_CNTY__3__GRASSLAND__3 | 3 Phase fault on LYNN_CNTY 3 (526656) 115 kV Bus a. Apply fault at the LYNN_CNTY 3 (526656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNN_CNTY 3 115.0 KV 526656 TO GRASSLAND 3 115.0 KV 526676 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__2__FT_SILL2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 b.2. LOAD 1 511469 b.3. FT.SILL2 69.0 KV 511461 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__2__LAW__WC2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 b.2. LOAD 1 511470 b.3. LGORE-S2 69.0 KV 511470 TO LAW WC2 69.0 KV 511503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__7__G18_015_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__7__G18_092_PROX | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G18-092-PROX 345.0 KV 763215 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__7__G20_009_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__7__G20_075_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__7__GEN_2018_115 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MADDOX_____3__ENRON_TP___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO PEARLE 3 115.0 KV 528392 CKT 1 b.2. LOAD 1 528392 b.3. LOAD 1* 528392 b.4. ENRON_TP 3 115.0 KV 528317 TO PEARLE 3 115.0 KV 528392 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25S | Transfer | MADDOX_____3__G18_004_TAP | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25S | Transfer | MADDOX_____3__MONUMENT___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO MONUMENT 3 115.0 KV 528491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25S | Transfer | MAPCO______3__JOHNSON_DRW3 | 3 Phase fault on MAPCO 3 (527360) 115 kV Bus a. Apply fault at the MAPCO 3 (527360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPCO 3 115.0 KV 527360 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MCDWL_CREEK6__POTTER_CO__6 | 3 Phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 230.0 KV 523323 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | MILLEN_TPE_3__MILLEN_TPW_3 | 3 Phase fault on MILLEN_TPE 3 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3 115.0 KV 528435 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 b.2. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN 3 115.0 KV 528435 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MILLEN_TPE_3__TAYLOR_____3 | 3 Phase fault on MILLEN_TPE 3 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPE 3 115.0 KV 528436 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 b.2. LOAD 1 528442 b.3. TAYLOR 3 115.0 KV 528413 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MILLEN_TPW_3__MILLEN_TPE_3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__NORMHLL7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__NSUB345 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MONUMENT___3__MONUMNT_TP_3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO MONUMNT_TP 3 115.0 KV 528568 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MONUMENT___3__W_HOBBS____3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MONUMNT_TP_3__BYRD_TP____3 | 3 Phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3 115.0 KV 528568 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MRIETA_2__ROCKYPT4 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MULESHVALLY3__MULSHVLY_TP3 | 3 Phase fault on MULESHVALLY3 (525018) 115 kV Bus a. Apply fault at the MULESHVALLY3 (525018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULESHVALLY3 115.0 KV 525018 TO MULSHVLY_TP3 115.0 KV 525019 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MULSHVLY_TP3__BAILEYCO___3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MULSHVLY_TP3__PLANT_X____3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MUSTANG____3__SEAGRAVES__3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MUSTANG____3__SEMINOLE___3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MUSTANG____6__SEMINOLE___6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MUSTANG____6__XTO_MAHONEY6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 b.2. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NA_ENRICH__3__CARDINAL___3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 b.2. LOAD 1 528605 b.3. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NA_ENRICH__3__DRINKARD_TP3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD 3 115.0 KV 528589 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 b.2. LOAD 1 528603 b.3. LOAD 5* 528603 b.4. DRINKARD_TP3 115.0 KV 528533 TO DRINKARD 3 115.0 KV 528589 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NEWHART____6__GEN_2018_089 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO GEN-2018-089 230.0 KV 763186 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25S | Transfer | NE_HEREFORD3__TIERABLANCA3 | 3 Phase fault on NE_HEREFORD3 (524567) 115 kV Bus a. Apply fault at the NE_HEREFORD3 (524567) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE_HEREFORD3 115.0 KV 524567 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NICHOLS____6__AMA_SOUTH__6 | 3 Phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 230.0 KV 524044 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | NORRIS_TP__3__CURRY______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NORRIS_TP__3__NORRIS_____3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO NORRIS 3 115.0 KV 524801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NORRIS_TP__3__OASIS______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 b.2. LOAD 1 524863 b.3. FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NORTON_____3__FE_TUCMCARI3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO FE-TUCMCARI3 115.0 KV 524509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NORTON_____3__PLSNT_HILL_3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO PLSNT_HILL 3 115.0 KV 524768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | N_CANAL____3__PECOS______3 | 3 Phase fault on N_CANAL 3 (528137) 115 kV Bus a. Apply fault at the N_CANAL 3 (528137) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CANAL 3 115.0 KV 528137 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | N_CLOVIS_TP3__FE_CLVS_INT3 | 3 Phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CLOVIS_TP3 115.0 KV 524776 TO FE-CLVS_INT3 115.0 KV 524808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | N_CLOVIS_TP3__N_CLOVIS___3 | 3 Phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CLOVIS_TP3 115.0 KV 524776 TO N_CLOVIS 3 115.0 KV 524777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OASIS______3__CANNON_TP__3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERIMETER 3 115.0 KV 524797 TO OASIS 3 115.0 KV 524874 CKT 1 b.2. CANNON_TP 3 115.0 KV 524790 TO PERIMETER 3 115.0 KV 524797 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OASIS______3__PORTALES___3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OASIS______6__GEN_2020_062 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO GEN-2020-062 230.0 KV 764890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OASIS______6__ROOSEVELT__6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OASIS______6__SN_JUAN_TAP6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO SN_JUAN_TAP6 230.0 KV 524885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OCOTILLO___3__PECOS______3 | 3 Phase fault on OCOTILLO 3 (528132) 115 kV Bus a. Apply fault at the OCOTILLO 3 (528132) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCOTILLO 3 115.0 KV 528132 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ODC_TP_____3__ODC________3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO ODC 3 115.0 KV 527056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ODC_TP_____3__SHELL_CO2__3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO SHELL_CO2 3 115.0 KV 527062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ONEY___4__WASHITA4 | 3 Phase fault on ONEY 4 (521017) 138 kV Bus a. Apply fault at the ONEY 4 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138.0 KV 521017 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OXY_WSEM_TP3__JOHNSON_DRW3 | 3 Phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSEM_TP3 115.0 KV 527325 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | O_K_U__7__G18_092_PROX | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-092-PROX 345.0 KV 763215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | O_K_U__7__G20_009_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PCA________3__CARLSBAD___3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PCA________3__CV_LUSK_TP_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CV-LUSK_TP 3 115.0 KV 527948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PCA________3__POTASH_JCT_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO POTASH_JCT 3 115.0 KV 527962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PECOS______3__HOPI_SUB___3 | 3 Phase fault on PECOS 3 (528178) 115 kV Bus a. Apply fault at the PECOS 3 (528178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 3 115.0 KV 528178 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PHANTOM____3__CHINA_DRAW_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 b.2. LOAD 1 528228 b.3. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PHANTOM____3__MALAGABEND_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PITTSB_7__JOHNCO_7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLAINS_INT_3__LEHMAN_TP__3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 b.2. LOAD 1 526944 b.3. LEHMAN_TP 3 115.0 KV 526350 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLAINS_INT_3__YOAKUM_____3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLAINVW_TP_2__HALE_CNTY__2 | 3 Phase fault on PLAINVW_TP 2 (525291) 69 kV Bus a. Apply fault at the PLAINVW_TP 2 (525291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINVW_TP 2 69.0 KV 525291 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLANT_X____3__CASTRO_CNTY3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 b.2. LOAD 1 525480 b.3. BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 b.4. LOAD 1 525056 b.5. CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLANT_X____3__LAMB_CNTY__3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLANT_X____6__G17_146_TAP | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | PLSNT_HILL_3__CURRY______3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO FE-HOLLAND 3 115.0 KV 524831 CKT 1 b.2. LOAD 1 524831 b.3. FE-HOLLAND 3 115.0 KV 524831 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 b.4. LOAD 1 524838 b.5. CURRY 3 115.0 KV 524822 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLSNT_HILL_3__N_CLOVIS_TP3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO N_CLOVIS_TP3 115.0 KV 524776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLSNT_HILL_6__OASIS______6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLSNT_HILL_6__ROOSEVELT__6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POOLVIL4__CARTRCO4 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PORTALES___2__PORTALES_1_2 | 3 Phase fault on PORTALES 2 (524923) 69 kV Bus a. Apply fault at the PORTALES 2 (524923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 2 69.0 KV 524923 TO PORTALES#1 2 69.0 KV 524941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PORTALES___2__ZODIAC_____2 | 3 Phase fault on PORTALES 2 (524923) 69 kV Bus a. Apply fault at the PORTALES 2 (524923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 2 69.0 KV 524923 TO ZODIAC 2 69.0 KV 524934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PORTALES___3__KILGORE____3 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 115.0 KV 524924 TO GREYHOUND 3 115.0 KV 524977 CKT 1 b.2. LOAD 1 524977 b.3. S_PORTALES 3 115.0 KV 524963 TO GREYHOUND 3 115.0 KV 524977 CKT 1 b.4. LOAD 1 524977 b.5. KILGORE 3 115.0 KV 524935 TO S_PORTALES 3 115.0 KV 524963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTASH_JCT_3__CARLSBAD___3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTASH_JCT_3__INTREPDW_TP3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO INTREPDW_TP3 115.0 KV 527999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTASH_JCT_6__PECOS______6 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 230.0 KV 527963 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTTER_CO__6__BUSHLAND___6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO BUSHLAND 6 230.0 KV 524267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | POTTER_CO__6__HARRNG_EST_6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO HARRNG_EST 6 230.0 KV 523979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | POTTER_CO__6__ROLLHILLS__6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO ROLLHILLS 6 230.0 KV 524010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | POTTER_CO__7__TOLK_______7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | QUAHADA____3__DCP_ZIA_TP_3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | QUAHADA____3__LEA_NATIONL3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | QUAHADA____3__PCA________3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 b.2. LOAD 1 528396 b.3. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RANDALL____6__AMA_SOUTH__6 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 230.0 KV 524365 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | RATLIFF4__CARTRCO4 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER___3__OCHOA______3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 b.2. LOAD 1 528230 b.3. AGAVE_RHILL3 115.0 KV 528230 TO OCHOA 3 115.0 KV 528232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RED_BLUFF__3__WIPP_______3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAND_DUNES 3 115.0 KV 528016 TO RED_BLUFF 3 115.0 KV 528018 CKT 1 b.2. WIPP 3 115.0 KV 528009 TO SAND_DUNES 3 115.0 KV 528016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RED_BLUFF__3__WOLFCAMP_TP3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RKYFORD_TP_3__LAMTON_____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-S_OLTON+3 115.0 KV 525440 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 b.2. LAMTON 3 115.0 KV 525414 TO LC-S_OLTON+3 115.0 KV 525440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RKYFORD_TP_3__PLANT_X____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ROCKYFORD__3__RKYFORD_TP_3 | 3 Phase fault on ROCKYFORD 3 (525393) 115 kV Bus a. Apply fault at the ROCKYFORD 3 (525393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYFORD 3 115.0 KV 525393 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ROCKYPT4__SPRNDAL4 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ROOSEVELT__3__PORTALES___3 | 3 Phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 3 115.0 KV 524908 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ROOSEVELT__6__GEN_2019_003 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO GEN-2019-003 230.0 KV 763483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generators trip when this IDV is ran with reclose. | Removing reclose prevents generators from tripping.
05 - Southwest | 25S | Transfer | ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ROZ________3__SEMINOLE___3 | 3 Phase fault on ROZ 3 (527238) 115 kV Bus a. Apply fault at the ROZ 3 (527238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROZ 3 115.0 KV 527238 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RR_SVC_HV__3__RDRUNNER___3 | 3 Phase fault on RR_SVC_HV 3 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 115.0 KV 528024 TO RDRUNNER 3 115.0 KV 528025 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RSVLT_CC_W_7__RSVLT_CC_E_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_CC_E 7 345.0 KV 527655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RSVLT_CC_W_7__RSVLT_COL1_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_COL1 7 345.0 KV 527666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RSVLT_CC_W_7__RSVLT_COL2_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_COL2 7 345.0 KV 527667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RSWL_SLRCOL3__CHAVES_CNTY3 | 3 Phase fault on RSWL_SLRCOL3 (527455) 115 kV Bus a. Apply fault at the RSWL_SLRCOL3 (527455) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSWL_SLRCOL3 115.0 KV 527455 TO CHAVES_CNTY3 115.0 KV 527482 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | IDV crashes when ran with reclose. | Removing reclose prevents IDV from crashing.
05 - Southwest | 25S | Transfer | RUSHSPR7__GEN_2015_092 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2015-092 345.0 KV 563259 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SAGA_SDCOL_7__SAGA_SMEAS_7 | 3 Phase fault on SAGA_SDCOL 7 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7 (527599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SMEAS 7 345.0 KV 527600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SAMSON_____3__ROSWLL_INT_3 | 3 Phase fault on SAMSON 3 (527546) 115 kV Bus a. Apply fault at the SAMSON 3 (527546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAMSON 3 115.0 KV 527546 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SANGER_SW__3__G18_004_TAP | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SANGER_SW__3__OXYPERMIAN_3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SANGER_SW__3__SW_4J44____3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SAN_ANDS_TP3__DENVER_S___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SAN_ANDS_TP3__SEMINOLE___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SEAGRAVES__2__LG_MC&SMNL_2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO LG-MC&SMNL+2 69.0 KV 527223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SEAGRAVES__2__MOSS_______2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO MOSS 2 69.0 KV 527217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SEAGRAVES__3__FLATLAND___3 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3 (527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 115.0 KV 527202 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SEMINOLE___3__DOSS_______3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO DOSS 3 115.0 KV 527340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SEMINOLE___3__GAINES_____3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO GAINES 3 115.0 KV 527322 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SEQUOYAHJ4__ANADARK4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SHELLC3_TP_3__SHELLC3____3 | 3 Phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELLC3_TP 3 115.0 KV 527068 TO SHELLC3 3 115.0 KV 527074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SHELL_C2___3__DENVER_S___3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SHELL_C2___3__SHELLC3_TP_3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SHELL_CO2__3__EL_PASO____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO EL_PASO 3 115.0 KV 527080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SHELL_CO2__3__MUSTANG____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SIDEWINDER_7__ANDREWS____6 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO ANDREWS 6 345.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SIDEWINDER_7__HOBBS_INT__7 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | No | No | No | No | No | No | No | Voltage Instability/Voltage Collapse. | Build New Andrews to Road Runner 345 kV Line
05 - Southwest | 25S | Transfer | SLATON_____2__SP_SLATON__2 | 3 Phase fault on SLATON 2 (526562) 69 kV Bus a. Apply fault at the SLATON 2 (526562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLATON 2 69.0 KV 526562 TO SP-SLATON 2 69.0 KV 526569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SN_JUAN_TAP6__SN_JUAN_WND6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO SN_JUAN_WND6 230.0 KV 524889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SOUTH_LOVNG3__MALAGABEND_3 | 3 Phase fault on SOUTH_LOVNG3 (528192) 115 kV Bus a. Apply fault at the SOUTH_LOVNG3 (528192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTH_LOVNG3 115.0 KV 528192 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SPNSPUR_WND7__SPNSPUR_COL7 | 3 Phase fault on SPNSPUR_WND7 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 345.0 KV 524296 TO SPNSPUR_COL7 345.0 KV 524299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SP_ABERNTHY2__TUCO_INT2__2 | 3 Phase fault on SP-ABERNTHY2 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY2 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 69.0 KV 525731 TO TUCO_INT2 2 69.0 KV 525816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SP_ACUFF___2__CROSBY_____2 | 3 Phase fault on SP-ACUFF +2 (525906) 69 kV Bus a. Apply fault at the SP-ACUFF +2 (525906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ACUFF +2 69.0 KV 525906 TO CROSBY 2 69.0 KV 525925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SP_CROSBY__2__CROSBY_____2 | 3 Phase fault on SP-CROSBY 2 (525915) 69 kV Bus a. Apply fault at the SP-CROSBY 2 (525915) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-CROSBY 2 69.0 KV 525915 TO CROSBY 2 69.0 KV 525925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SP_HALFWAY_2__HALE_CNTY__2 | 3 Phase fault on SP-HALFWAY+2 (525432) 69 kV Bus a. Apply fault at the SP-HALFWAY+2 (525432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-HALFWAY+2 69.0 KV 525432 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SP_UPLAND__SP_WOLF_TP_3 | 3 Phase fault on SP-UPLAND (526198) 115 kV Bus a. Apply fault at the SP-UPLAND (526198) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-UPLAND 115.0 KV 526198 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SP_WOLF_TP_3__SP_WOLFORTH3 | 3 Phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-WOLF_TP 3 115.0 KV 526481 TO SP-WOLFORTH3 115.0 KV 526483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | STANTON_E__2__SW_6786_S__2 | 3 Phase fault on STANTON_E 2 (526075) 69 kV Bus a. Apply fault at the STANTON_E 2 (526075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTON_E 2 69.0 KV 526075 TO SW_6786_S 2 69.0 KV 526087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNDOWN____3__AMOCO_TP___3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 3 115.0 KV 526434 TO AMOCO_TP 3 115.0 KV 526445 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNDOWN____3__COCHRAN____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PACIFIC 3 115.0 KV 526424 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. COCHRAN 3 115.0 KV 526361 TO PACIFIC 3 115.0 KV 526424 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNDOWN____3__HOCKLEY____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD4__CARTER_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD4__CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD4__CHEEKTP4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD4__ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD7__G20_074_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD7__GEN_2017_167 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-167 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SW4J795_E__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_E 3 (527533) 115 kV Bus a. Apply fault at the SW4J795_E 3 (527533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_E 3 115.0 KV 527533 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SW4J795_W__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_W 3 (527534) 115 kV Bus a. Apply fault at the SW4J795_W 3 (527534) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_W 3 115.0 KV 527534 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SW_6786_N__2__SW_6786_S__2 | 3 Phase fault on SW_6786_N 2 (526086) 69 kV Bus a. Apply fault at the SW_6786_N 2 (526086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_6786_N 2 69.0 KV 526086 TO SW_6786_S 2 69.0 KV 526087 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | S_JAL______3__DOLLARHIDE_3 | 3 Phase fault on S_JAL 3 (528547) 115 kV Bus a. Apply fault at the S_JAL 3 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 115.0 KV 528547 TO DOLLARHIDE 3 115.0 KV 528561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | S_PLAINVEW_2__HALE_CNTY__2 | 3 Phase fault on S_PLAINVEW 2 (525298) 69 kV Bus a. Apply fault at the S_PLAINVEW 2 (525298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_PLAINVEW 2 69.0 KV 525298 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | S_W_S__4__ANADARK4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | S_W_S__4__G16_097_TAP | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | S_W_S__4__NORGE__4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | S_W_S__4__WASHITA4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TAYLOR_____3__E_SANGER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRYRD7__G20_074_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRY_CNTY_2__LG_BROWNFLD2 | 3 Phase fault on TERRY_CNTY 2 (526735) 69 kV Bus a. Apply fault at the TERRY_CNTY 2 (526735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 2 69.0 KV 526735 TO LG-BROWNFLD2 69.0 KV 526747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRY_CNTY_3__AMOCO_TP___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-CLAUENE 3 115.0 KV 526491 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 b.2. LG-LEVELAND3 115.0 KV 526484 TO LG-CLAUENE 3 115.0 KV 526491 CKT 1 b.3. LOAD 1 526491 b.4. AMOCO_TP 3 115.0 KV 526445 TO LG-LEVELAND3 115.0 KV 526484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRY_CNTY_3__DENVER_N___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRY_CNTY_3__FLATLAND___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-017 trips on frequency protection settings. LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. Disabling frequency protection settings for GEN-2020-017 prevents trip. There are no stability constraints when these generators trip offline or when the protection settings are disabled to prevent them from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-017 trips on frequency protection settings. LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. Disabling frequency protection settings for GEN-2020-017 prevents trip. There are no stability constraints when these generators trip offline or when the protection settings are disabled to prevent them from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-017 trips on frequency protection settings. LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. Disabling frequency protection settings for GEN-2020-017 prevents trip. There are no stability constraints when these generators trip offline or when the protection settings are disabled to prevent them from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | TREASILD7__G20_075_TAP | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TREASILD7__GEN_2016_091 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TREASILD7__GEN_2016_095 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TREASILD7__GRACMNT7 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___2__LH_WIL&ELN_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO LH-WIL&ELN+2 69.0 KV 525853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___2__SP_NEWDEAL_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO SP-NEWDEAL 2 69.0 KV 525885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___3__STANTON_W__3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Antelope units trip on power unbalance. | Reducing fault clearing time to 5 cycles prevents trip. There are no stability constraints when these generators trip offline or when the fault clearing times are reduced to 5 cycles to prevent them from tripping.
05 - Southwest | 25S | Transfer | TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Antelope units trip on power unbalance. | Reducing fault clearing time to 5 cycles prevents trip. There are no stability constraints when these generators trip offline or when the fault clearing times are reduced to 5 cycles to prevent them from tripping.
05 - Southwest | 25S | Transfer | TUCO_INT___7__CRAWFISH_DR | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO CRAWFISH_DR 345.0 KV 560022 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | TUCO_INT___7__G20_067_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | TULIA_TP___3__KRESS_INT__3 | 3 Phase fault on TULIA_TP 3 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULIA_TP 3 115.0 KV 525179 TO KRESS_INT 3 115.0 KV 525192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | VALIANT7__HUGO___7 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | VERDEN_4__S_W_S__4 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WASHITA4__SLKHILLS_4 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138.0 KV 521089 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WHITTEN____3__LEA_ROAD___3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 3 115.0 KV 528519 TO WHITTEN 3 115.0 KV 528540 CKT 1 b.2. LOAD 1 528540 b.3. LEA_ROAD 3 115.0 KV 528505 TO WARD 3 115.0 KV 528519 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WHITTEN____3__S_JAL______3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITTEN 3 115.0 KV 528540 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WOLFCAMP_TP3__PHANTOM____3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOPCO_PKRLK3 115.0 KV 528020 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 b.2. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WOLFCAMP_TP3__WOLFCAMP___3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCAMP_TP3 115.0 KV 528235 TO WOLFCAMP 3 115.0 KV 528236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WOLFCRK4__CHEEKTP4 | 3 Phase fault on WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WOLFFORTH__3__SP_WOLF_TP_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUMA_INT 3 115.0 KV 526475 TO WOLFFORTH 3 115.0 KV 526524 CKT 1 b.2. YUMA_INT 3 115.0 KV 526475 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WOLFFORTH__3__TERRY_CNTY_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 3 115.0 KV 526524 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__BOBCAT_7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BOBCAT 7 345.0 KV 516106 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__BVRCNTY7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BVRCNTY7 345.0 KV 515554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__G07621119_20 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__GEN_2019_012 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | W_HOBBS____3__DRINKARD_TP3 | 3 Phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_HOBBS 3 115.0 KV 528498 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | XTO_MAHONEY6__GEN_2017_239 | 3 Phase fault on XTO_MAHONEY6 (527011) 230 kV Bus a. Apply fault at the XTO_MAHONEY6 (527011) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_MAHONEY6 230.0 KV 527011 TO GEN-2017-239 230.0 KV 761355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_345__G20_059_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | YOAKUM_345__G20_067_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | YOAKUM_345__GEN_2019_011 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2019-011 345.0 KV 763516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | YOAKUM_____3__ARCO_TP____3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_____3__SEAGRAVES__3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 b.2. LOAD 1 527194 b.3. LG-PLSHILL 3 115.0 KV 527194 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_____3__TERRY_CNTY_3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 b.2. TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ZIA________3__DCP_ZIA_TP_3 | 3 Phase fault on ZIA 3 (528420) 115 kV Bus a. Apply fault at the ZIA 3 (528420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZIA 3 115.0 KV 528420 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | 112GORE4__LAIRGST4 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | 7_RIVERS___6__PECOS______6 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 230.0 KV 528095 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ACCO_______2__CLUTTER____2 | 3 Phase fault on ACCO 2 (526249) 69 kV Bus a. Apply fault at the ACCO 2 (526249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACCO 2 69.0 KV 526249 TO CLUTTER 2 69.0 KV 526310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ALLEN______3__LP_WHEELOCK3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO LP-WHEELOCK3 115.0 KV 526236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ALLEN______3__LUBBCK_STH_3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO LUBBCK_STH 3 115.0 KV 526268 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ALLEN______3__SP_QUAKER__3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO SP-QUAKER 3 115.0 KV 526243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ALRDCRTZ_TP3__CORTEZ_____3 | 3 Phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLRED_SUB 3 115.0 KV 527024 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 b.2. APACHE_ROB 3 115.0 KV 527022 TO ALLRED_SUB 3 115.0 KV 527024 CKT 1 b.3. LOAD 1 527024 b.4. CORTEZ 3 115.0 KV 527021 TO APACHE_ROB 3 115.0 KV 527022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ALRDCRTZ_TP3__SHELLC3_TP_3 | 3 Phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALRDCRTZ_TP3 115.0 KV 527030 TO XTO_CORNEL+3 115.0 KV 527033 CKT 1 b.2. LOAD 1 527033 b.3. XTO_CORNEL+3 115.0 KV 527033 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | AMERADA____3__SEMINOLE___3 | 3 Phase fault on AMERADA 3 (527242) 115 kV Bus a. Apply fault at the AMERADA 3 (527242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMERADA 3 115.0 KV 527242 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | AMOCO_TP___3__AMOCO_CRYO_3 | 3 Phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_TP 3 115.0 KV 526445 TO AMOCO_CRYO 3 115.0 KV 526452 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ANADARK4__CHERRYRD_4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ANADARK4__GEORGIA4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ANADARK4__POCASET4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ANDREWS____3__NA_ENRICH__3 | 3 Phase fault on ANDREWS 3 (528602) 115 kV Bus a. Apply fault at the ANDREWS 3 (528602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ARCO_TP____3__ARCO_TP____3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNETT 3 115.0 KV 527018 TO ARCO_TP 3 115.0 KV 527041 CKT 1 b.2. BENNETT 3 115.0 KV 527018 TO ODC_TP 3 115.0 KV 527051 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ARCO_TP____3__OXY_WILRD1_3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO_TP 3 115.0 KV 527041 TO OXY_WILRD1 3 115.0 KV 527047 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ARTESIA____3__EAGLE_CREEK3 | 3 Phase fault on ARTESIA 3 (527707) 115 kV Bus a. Apply fault at the ARTESIA 3 (527707) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTESIA 3 115.0 KV 527707 TO EAGLE_CREEK3 115.0 KV 527711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ARTSA_CC_TP3__ATOKA______3 | 3 Phase fault on ARTSA_CC_TP3 (527777) 115 kV Bus a. Apply fault at the ARTSA_CC_TP3 (527777) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTSA_CC_TP3 115.0 KV 527777 TO ATOKA 3 115.0 KV 527786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ARTVLTP4__LWS_NTP4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 b.2. LWS-NTP4 138.0 KV 511471 TO 53CACHE4 138.0 KV 511509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ATOKA______3__CV_IRISHHL_3 | 3 Phase fault on ATOKA 3 (527786) 115 kV Bus a. Apply fault at the ATOKA 3 (527786) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA 3 115.0 KV 527786 TO CV-IRISHHL+3 115.0 KV 528116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BLANCO_____3__CROSBY_____3 | 3 Phase fault on BLANCO 3 (525803) 115 kV Bus a. Apply fault at the BLANCO 3 (525803) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCO 3 115.0 KV 525803 TO CROSBY 3 115.0 KV 525926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BLUECLDCOL_6__BLUECLDPOI_6 | 3 Phase fault on BLUECLDCOL 6 (525584) 230 kV Bus a. Apply fault at the BLUECLDCOL 6 (525584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDCOL 6 230.0 KV 525584 TO BLUECLDPOI 6 230.0 KV 525585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BLUECLDPOI_6__NEEDMORE___6 | 3 Phase fault on BLUECLDPOI 6 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 230.0 KV 525585 TO NEEDMORE 6 230.0 KV 525586 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | BORDER_____7__CRAWFISH_DR | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO CRAWFISH_DR 345.0 KV 560022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | BRU_SUB____6__OXYBRU_____6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO OXYBRU 6 230.0 KV 527010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | BRU_SUB____6__XTO_MAHONEY6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BUCKEYE_TP_3__BUCKEYE____3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO BUCKEYE 3 115.0 KV 528385 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BUCKEYE_TP_3__LE_TXACO_TP3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BYRD_TP____3__BYRD_______3 | 3 Phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRD_TP 3 115.0 KV 528581 TO BYRD 3 115.0 KV 528582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CALLAHAN___3__FLOYD_CNTY_3 | 3 Phase fault on CALLAHAN 3 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 115.0 KV 525763 TO FLOYD_CNTY 3 115.0 KV 525780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CANNON_TP__3__CANNONAFB__3 | 3 Phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANNON_TP 3 115.0 KV 524790 TO CANNONAFB 3 115.0 KV 524794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CANNON_TP__3__FE_CLVS_INT3 | 3 Phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_CLOVIS 3 115.0 KV 524784 TO CANNON_TP 3 115.0 KV 524790 CKT 1 b.2. W_CLOVIS 3 115.0 KV 524784 TO FE-CLVS_INT3 115.0 KV 524808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CAPITAN____3__ROSWLL_INT_3 | 3 Phase fault on CAPITAN 3 (527541) 115 kV Bus a. Apply fault at the CAPITAN 3 (527541) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAPITAN 3 115.0 KV 527541 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CAPROCK____3__NORTON_____3 | 3 Phase fault on CAPROCK 3 (524486) 115 kV Bus a. Apply fault at the CAPROCK 3 (524486) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAPROCK 3 115.0 KV 524486 TO NORTON 3 115.0 KV 524502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARDINAL___3__LIVSTNRIDGE3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 b.2. MEDANOS 3 115.0 KV 527954 TO SAGE_BRUSH 3 115.0 KV 527955 CKT 1 b.3. LOAD 1 527955 b.4. LOAD 1* 527955 b.5. LIVSTNRIDGE3 115.0 KV 527953 TO MEDANOS 3 115.0 KV 527954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARDINAL___3__S_JAL______3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO CARDINAL 3 115.0 KV 528596 CKT 1 b.2. TEAGUE 3 115.0 KV 528526 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARLISLE___3__LP_DOUD_TP_3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO LP-DOUD_TP 3 115.0 KV 526162 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARLISLE___3__MURPHY_____3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO MURPHY 3 115.0 KV 526192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARLSBAD___3__PECOS______3 | 3 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 115.0 KV 528160 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARNEG_4__S_W_S__4 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARTER_4__CHIKSAW4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARTER_4__HONEYCK4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARTRCO4__GEN_2017_027 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | IDV crashes when ran with reclose. | Removing reclose prevents IDV from crashing.
05 - Southwest | 25W | Transfer | CARTRCO4__ORIGINW4 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CASTRO_CNTY3__BETHEL_COL13 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO BETHEL_COL13 115.0 KV 524757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CASTRO_CNTY3__NEWHART____3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CASTRO_CNTY3__TIERABLANCA3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#21 3 115.0 KV 524734 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 b.2. TIERABLANCA3 115.0 KV 524630 TO DS-#21 3 115.0 KV 524734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHAN_TASCOS6__POTTER_CO__6 | 3 Phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 230.0 KV 523869 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHAVES_CNTY3__PRICE_TAP__3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO PRICE_TAP 3 115.0 KV 527509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHAVES_CNTY3__SAMSON_____3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO SAMSON 3 115.0 KV 527546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHAVES_CNTY3__URTON______3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO URTON 3 115.0 KV 527501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHEEKTP4__CHEEK_4 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | CHISHOLM7__POTTER_CO__7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO POTTER_CO 7 345.0 KV 523961 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | CHVS_SLRCOL3__CHAVES_CNTY3 | 3 Phase fault on CHVS_SLRCOL3 (527470) 115 kV Bus a. Apply fault at the CHVS_SLRCOL3 (527470) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHVS_SLRCOL3 115.0 KV 527470 TO CHAVES_CNTY3 115.0 KV 527482 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | IDV crashes when ran with reclose. | Removing reclose prevents IDV from crashing.
05 - Southwest | 25W | Transfer | CLVLDSW4__ANADARK4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COMANC_2__L_DISTP2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L-DISTP2 69.0 KV 511524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COOPER_RNCH3__BYRD_TP____3 | 3 Phase fault on COOPER_RNCH3 (528554) 115 kV Bus a. Apply fault at the COOPER_RNCH3 (528554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_RNCH3 115.0 KV 528554 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COX________3__CALLAHAN___3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO CALLAHAN 3 115.0 KV 525763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COX________3__HALE_CNTY__3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CRAWFISH_DR__G17_151TAP | 3 Phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR 345.0 KV 560022 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | CRAWFISH_DR__G18_015_TAP | 3 Phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR 345.0 KV 560022 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | CRAWFISH_DR__G18_092_PROX | 3 Phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR 345.0 KV 560022 TO G18-092-PROX 345.0 KV 763215 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | CROSBY_____2__LH_CROSBY__2 | 3 Phase fault on CROSBY 2 (525925) 69 kV Bus a. Apply fault at the CROSBY 2 (525925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 2 69.0 KV 525925 TO LH-CROSBY +2 69.0 KV 525936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CROSBY_____3__LUBBCK_EST_3 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | CROSSROADS_7__HOBBS_INT__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT LX c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | CROSSROADS_7__SAGA_SDCOL_7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 b.2. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SCOL 7 345.0 KV 527610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNIGHM_N_6__POTASH_JCT_6 | 3 Phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | CUNNINHAM__3__BUCKEYE_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNINHAM__3__HOBBS_INT__3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO HOBBS_INT 3 115.0 KV 527891 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | CUNNINHAM__3__MADDOX_____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNINHAM__3__MONUMNT_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MONUMNT_TP 3 115.0 KV 528568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNINHAM__3__QUAHADA____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CURRY______3__BAILEYCO___3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CURRY______3__PLSNT_HILL_3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E_CLOVIS 3 115.0 KV 524773 TO CURRY 3 115.0 KV 524822 CKT 1 b.2. LOAD 1 524822 b.3. PLSNT_HILL 3 115.0 KV 524768 TO E_CLOVIS 3 115.0 KV 524773 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CURRY______3__ROOSEVELT__3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO ROOSEVELT 3 115.0 KV 524908 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUSTERMTN__3__PONDEROSA__3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO PONDEROSA 3 115.0 KV 528240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUSTERMTN__3__WHITTEN____3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO WHITTEN 3 115.0 KV 528540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CV_8_MILE__3__CV_TURKYTRK3 | 3 Phase fault on CV-8_MILE 3 (527809) 115 kV Bus a. Apply fault at the CV-8_MILE 3 (527809) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CV-8_MILE 3 115.0 KV 527809 TO CV-TURKYTRK3 115.0 KV 527822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CV_AZMESA__3__PECOS______3 | 3 Phase fault on CV-AZMESA 3 (528070) 115 kV Bus a. Apply fault at the CV-AZMESA 3 (528070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CV-AZMESA 3 115.0 KV 528070 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DCP_ZIA_TP_3__DCP_ZIA____3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCP_ZIA TP 3 115.0 KV 528422 TO DCP_ZIA 3 115.0 KV 528423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DEAFSMITH__6__G17_146_TAP | 3 Phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 230.0 KV 524623 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DENVER_N___3__MUSTANG____3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DENVER_S___3__MUSTANG____3 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3 (527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 115.0 KV 527136 TO MUSTANG 3 115.0 KV 527146 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DFSMTH_EST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_EST 3 (524619) 115 kV Bus a. Apply fault at the DFSMTH_EST 3 (524619) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_EST 3 115.0 KV 524619 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DFSMTH_WST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_WST 3 (524622) 115 kV Bus a. Apply fault at the DFSMTH_WST 3 (524622) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_WST 3 115.0 KV 524622 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DIAMONDBACK3__FLATLAND___3 | 3 Phase fault on DIAMONDBACK3 (527212) 115 kV Bus a. Apply fault at the DIAMONDBACK3 (527212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK3 115.0 KV 527212 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DS_CASTRO__2__CASTRO_CNTY2 | 3 Phase fault on DS-CASTRO 2 (524728) 69 kV Bus a. Apply fault at the DS-CASTRO 2 (524728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-CASTRO 2 69.0 KV 524728 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DS__15&_19_2__CASTRO_CNTY2 | 3 Phase fault on DS-#15&#19+2 (524721) 69 kV Bus a. Apply fault at the DS-#15&#19+2 (524721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#15&#19+2 69.0 KV 524721 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DS__20_____3__CURRY______3 | 3 Phase fault on DS-#20 3 (524669) 115 kV Bus a. Apply fault at the DS-#20 3 (524669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#20 3 115.0 KV 524669 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DS__22_____3__CASTRO_CNTY3 | 3 Phase fault on DS-#22 3 (524694) 115 kV Bus a. Apply fault at the DS-#22 3 (524694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#22 3 115.0 KV 524694 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DS__25_____3__TIERABLANCA3 | 3 Phase fault on DS-#25+ 3 (524575) 115 kV Bus a. Apply fault at the DS-#25+ 3 (524575) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#25+ 3 115.0 KV 524575 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DS__3______2__CASTRO_CNTY2 | 3 Phase fault on DS-#3 2 (524688) 69 kV Bus a. Apply fault at the DS-#3 2 (524688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#3 2 69.0 KV 524688 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DUNCAN_4__OMDUNCN4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EAGLE_CREEK3__7_RIVERS___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO 7-RIVERS 3 115.0 KV 528094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EAGLE_CREEK3__ARTSA_CC_TP3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO ARTSA_CC_TP3 115.0 KV 527777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EAGLE_CREEK3__EDDY_NTH___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EAGLE_CREEK3__NAVAJO_2TP_3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO NAVAJO_2TP 3 115.0 KV 527715 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EAGLE_CREEK3__NAVAJO_5TP_3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO NAVAJO_5TP 3 115.0 KV 527736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | EDDY_NTH___3__CV_8_MILE__3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NTH 3 115.0 KV 527798 TO CV-8_MILE 3 115.0 KV 527809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_NTH___3__ROSWLL_INT_3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWEEDY 3 115.0 KV 527597 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 b.2. ROSWLL_INT 3 115.0 KV 527564 TO TWEEDY 3 115.0 KV 527597 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_STH___3__ATOKA______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 b.2. LOAD 1 527821 b.3. ATOKA 3 115.0 KV 527786 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_STH___3__PECOS______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ELGINJT2__CORNVIL2 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CYRIL--2 69.0 KV 511451 TO ELGINJT2 69.0 KV 511487 CKT 1 b.2. LOAD 1 511487 b.3. CORNVIL2 69.0 KV 511450 TO CYRIL--2 69.0 KV 511451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ELGINJT2__FT_SILL2 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PO.HILL2 69.0 KV 511473 TO ELGINJT2 69.0 KV 511487 CKT 1 b.2. LOAD 1 511487 b.3. FT.SILL2 69.0 KV 511461 TO PO.HILL2 69.0 KV 511473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ELGINJT4__S_W_S__4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EL_PASO____3__DENVER_N___3 | 3 Phase fault on EL_PASO 3 (527080) 115 kV Bus a. Apply fault at the EL_PASO 3 (527080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL_PASO 3 115.0 KV 527080 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ENRON_TP___3__ENRON______3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO ENRON 3 115.0 KV 528318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ENRON_TP___3__LEA_NATIONL3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EUNICE_____3__CARDINAL___3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EUNICE_____3__DRINKARD_TP3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | FE_CLVS_INT3__A12_02&13_05 | 3 Phase fault on FE-CLVS_INT3 (524808) 115 kV Bus a. Apply fault at the FE-CLVS_INT3 (524808) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FE-CLVS_INT3 115.0 KV 524808 TO A12-02&13-05 115.0 KV 583280 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | FLATLAND___3__GEN_2017_187 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO GEN-2017-187 115.0 KV 761796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | FLATLAND___3__SULPHUR____3 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO SULPHUR 3 115.0 KV 527262 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-187 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2017-187 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25W | Transfer | FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | FLOYD_CNTY_3__BLANCO_____3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G16_063_TAP__GEN_2016_063 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2016-063 345.0 KV 587430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G16_063_TAP__GEN_2017_075 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G18_015_TAP__G18_092_PROX | 3 Phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-015-TAP 345.0 KV 762467 TO G18-092-PROX 345.0 KV 763215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G20_067_TAP__GEN_2020_068 | 3 Phase fault on G20-067-TAP (764945) 345 kV Bus a. Apply fault at the G20-067-TAP (764945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-067-TAP 345.0 KV 764945 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G20_068_SS1__GEN_2020_068 | 3 Phase fault on G20-068-SS1 (764948) 345 kV Bus a. Apply fault at the G20-068-SS1 (764948) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-068-SS1 345.0 KV 764948 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G20_068_SS2__GEN_2020_068 | 3 Phase fault on G20-068-SS2 (764949) 345 kV Bus a. Apply fault at the G20-068-SS2 (764949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-068-SS2 345.0 KV 764949 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G20_075_TAP__GEN_2020_087 | 3 Phase fault on G20-075-TAP (764550) 345 kV Bus a. Apply fault at the G20-075-TAP (764550) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-075-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GAINES_PLNT7__SIDEWINDER_7 | 3 Phase fault on GAINES_PLNT7 (527000) 345 kV Bus a. Apply fault at the GAINES_PLNT7 (527000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GAINES_PLNT7 345.0 KV 527000 TO SIDEWINDER 7 345.0 KV 527020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GEN_2017_167__GEN_2017_167 | 3 Phase fault on GEN-2017-167 (761859) 345 kV Bus a. Apply fault at the GEN-2017-167 (761859) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-167 345.0 KV 761859 TO GEN-2017-167 345.0 KV 761880 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GEN_2018_004__G18_004_TAP | 3 Phase fault on GEN-2018-004 (762438) 115 kV Bus a. Apply fault at the GEN-2018-004 (762438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-004 115.0 KV 762438 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GEN_2020_009__G20_009_TAP | 3 Phase fault on GEN-2020-009 (766290) 345 kV Bus a. Apply fault at the GEN-2020-009 (766290) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-009 345.0 KV 766290 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GEN_2020_059__G20_059_TAP | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059 (764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 345.0 KV 764840 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GEN_2020_067__G20_067_TAP | 3 Phase fault on GEN-2020-067 (764935) 345 kV Bus a. Apply fault at the GEN-2020-067 (764935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-067 345.0 KV 764935 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GEN_2020_074__G20_074_TAP | 3 Phase fault on GEN-2020-074 (764105) 345 kV Bus a. Apply fault at the GEN-2020-074 (764105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-074 345.0 KV 764105 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | GRACMNT7__GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GRASSLAND__3__GRAHAM_____3 | 3 Phase fault on GRASSLAND 3 (526676) 115 kV Bus a. Apply fault at the GRASSLAND 3 (526676) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 3 115.0 KV 526676 TO GRAHAM 3 115.0 KV 526694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GRASSLAND__6__CIRRUS_WND_6 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 230.0 KV 526677 TO CIRRUS_WND 6 230.0 KV 526679 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HALECENTER_2__TUCO_INT___2 | 3 Phase fault on HALECENTER 2 (525738) 69 kV Bus a. Apply fault at the HALECENTER 2 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 69.0 KV 525738 TO TUCO_INT 2 69.0 KV 525826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HALE_CNTY__3__PLANT_X____3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HART_INDUST3__LAMTON_____3 | 3 Phase fault on HART_INDUST3 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO LAMTON 3 115.0 KV 525414 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HART_INDUST3__NEWHART____3 | 3 Phase fault on HART_INDUST3 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HEREFORD___3__TIERABLANCA3 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3 (524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 115.0 KV 524606 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HIGG_______3__DENVER_N___3 | 3 Phase fault on HIGG 3 (527363) 115 kV Bus a. Apply fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 b.2. DENVER_N 3 115.0 KV 527130 TO HIGGEAST 3 115.0 KV 527286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HITCHLAND__7__CARPENTER__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO CARPENTER 7 345.0 KV 523823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. GEN-2020-068 trips on voltage protection settings. Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Disabling voltage protection settings for GEN-2020-068 prevents trip. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when these generators trip offline or when the protection settings are disabled to prevent them from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | HITCHLAND__7__G10014G11022 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO G10014G11022 345.0 KV 576397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | HITCHLAND__7__NOBLE_WND__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOBLE_WND 7 345.0 KV 523101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | HITCHLAND__7__NOVUS1_____7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOVUS1 7 345.0 KV 523112 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | HOBBS_INT__3__HIGG_______3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO BENSING 3 115.0 KV 528433 CKT 1 b.2. LOAD 1 528433 b.3. LOAD 1* 528433 b.4. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | HOBBS_INT__3__LE_WEST_SUB3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO LE-WEST_SUB3 115.0 KV 528333 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | HOBBS_INT__3__MADDOX_____3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | HOBBS_INT__3__MILLEN_TPW_3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | HOBBS_INT__7__G20_059_TAP | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings. Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Disabling voltage protection settings for GEN-2020-009 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings. Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Disabling voltage protection settings for GEN-2020-009 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | HOBBS_INT__7__RDRUNNER___7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT XA c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings. Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Disabling voltage protection settings for GEN-2020-009 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | HUGO___7__G16_063_TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | INK_BASIN__3__A16_008SUB | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO A16-008SUB 115.0 KV 588460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | INK_BASIN__3__ALRDCRTZ_TP3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | INK_BASIN__3__LE_WAITS___3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO LE-WAITS 3 115.0 KV 528325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | IVORY_TP___2__LUBBCK_STH_2 | 3 Phase fault on IVORY_TP 2 (526256) 69 kV Bus a. Apply fault at the IVORY_TP 2 (526256) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IVORY_TP 2 69.0 KV 526256 TO LUBBCK_STH 2 69.0 KV 526267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | IVORY______2__LUBBCK_STH_2 | 3 Phase fault on IVORY 2 (526205) 69 kV Bus a. Apply fault at the IVORY 2 (526205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IVORY 2 69.0 KV 526205 TO LUBBCK_STH 2 69.0 KV 526267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | JOHNCO_7__DMNDSPG7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-015 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2020-015 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25W | Transfer | JOHNCO_7__GEN_2017_149 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-015 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2020-015 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25W | Transfer | JOHNCO_7__GEN_2020_015 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2020-015 345.0 KV 764270 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-015 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2020-015 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25W | Transfer | JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | JOHNSON_DRW3__TAYLOR_____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO TAYLOR 3 115.0 KV 528413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | KISER______3__COX________3 | 3 Phase fault on KISER 3 (525272) 115 kV Bus a. Apply fault at the KISER 3 (525272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISER 3 115.0 KV 525272 TO COX 3 115.0 KV 525326 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | KRESS_INT__3__HALE_CNTY__3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | KRESS_INT__3__KRS_RURL_TP3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO KRS_RURL_TP3 115.0 KV 525226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | KRESS_INT__3__NEWHART____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | KRESS_INT__3__SWISHER____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO SWISHER 3 115.0 KV 525212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LAMB_CNTY__2__SUDANRURAL_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 b.2. AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 b.3. LOAD 1 525613 b.4. LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 b.5. LOAD 1 525606 b.6. SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LAMB_CNTY__2__W_ANTON_TP_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 2 69.0 KV 525635 TO LC-LTTLFLD+2 69.0 KV 525650 CKT 1 b.2. LOAD 1 525650 b.3. LC-LTTLFLD+2 69.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LAMB_CNTY__3__HOCKLEY____3 | 3 Phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LAMB_CNTY__6__GEN_2020_017 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 230.0 KV 525637 TO GEN-2020-017 230.0 KV 764825 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LAMTON_____3__HALE_CNTY__3 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 115.0 KV 525414 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LC_BECK____2__SUDANRURAL_2 | 3 Phase fault on LC-BECK +2 (525045) 69 kV Bus a. Apply fault at the LC-BECK +2 (525045) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-BECK +2 69.0 KV 525045 TO SUDANRURAL 2 69.0 KV 525592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LEA_NATIONL3__SUMMIT_3 | 3 Phase fault on LEA_NATIONL3 (528399) 115 kV Bus a. Apply fault at the LEA_NATIONL3 (528399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_NATIONL3 115.0 KV 528399 TO SUMMIT_3 115.0 KV 528404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LEA_ROAD___3__OIL_CENTER_3 | 3 Phase fault on LEA_ROAD 3 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 115.0 KV 528505 TO OIL_CENTER 3 115.0 KV 528552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LEHMAN_TP__3__LEHMAN_____3 | 3 Phase fault on LEHMAN_TP 3 (526350) 115 kV Bus a. Apply fault at the LEHMAN_TP 3 (526350) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEHMAN_TP 3 115.0 KV 526350 TO LEHMAN 3 115.0 KV 526352 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_PLNSINT_2__LE_PLNSGOAB2 | 3 Phase fault on LE-PLNSINT 2 (528626) 69 kV Bus a. Apply fault at the LE-PLNSINT 2 (528626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-PLNSINT 2 69.0 KV 528626 TO LE-PLNSGOAB2 69.0 KV 528709 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_SANANDRS3__LE_TXACO_TP3 | 3 Phase fault on LE-SANANDRS3 (528341) 115 kV Bus a. Apply fault at the LE-SANANDRS3 (528341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS3 115.0 KV 528341 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_TXACO_TP3__LE_TEXACO__3 | 3 Phase fault on LE-TXACO_TP3 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-TXACO_TP3 115.0 KV 528627 TO LE-TEXACO 3 115.0 KV 528792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_WAITS___2__LE_FORT_SW_2 | 3 Phase fault on LE-WAITS 2 (528617) 69 kV Bus a. Apply fault at the LE-WAITS 2 (528617) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 2 69.0 KV 528617 TO LE-FORT_SW 2 69.0 KV 528714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_WAITS___2__LE_TP51____2 | 3 Phase fault on LE-WAITS 2 (528617) 69 kV Bus a. Apply fault at the LE-WAITS 2 (528617) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 2 69.0 KV 528617 TO LE-TP51 2 69.0 KV 528759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_WAITS___3__LE_NRTH_INT3 | 3 Phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 3 115.0 KV 528325 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_WEST_SUB3__LE_NRTH_INT3 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 115.0 KV 528333 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LG_DOCWEBR_2__TERRY_CNTY_2 | 3 Phase fault on LG-DOCWEBR 2 (526506) 69 kV Bus a. Apply fault at the LG-DOCWEBR 2 (526506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-DOCWEBR 2 69.0 KV 526506 TO TERRY_CNTY 2 69.0 KV 526735 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LG_WELLMAN_2__SEAGRAVES__2 | 3 Phase fault on LG-WELLMAN 2 (526993) 69 kV Bus a. Apply fault at the LG-WELLMAN 2 (526993) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-WELLMAN 2 69.0 KV 526993 TO SEAGRAVES 2 69.0 KV 527201 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LG_YEAR4__112GORE4 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LIVSTNRIDGE3__WIPP_______3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO WIPP 3 115.0 KV 528009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LIVSTNRIDGE3__XTO_DI9_TP_3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LOST_DRAW__3__COCHRAN____3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO COCHRAN 3 115.0 KV 526361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LOST_DRAW__3__LEHMAN_TP__3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO LEHMAN_TP 3 115.0 KV 526350 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LP_DOUD_TP_3__SP_WOLF_TP_3 | 3 Phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LP-DOUD_TP 3 115.0 KV 526162 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LRNZ_MPT___3__BLANCO_____3 | 3 Phase fault on LRNZ_MPT 3 (525801) 115 kV Bus a. Apply fault at the LRNZ_MPT 3 (525801) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LRNZ_MPT 3 115.0 KV 525801 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LTFLD_S&CTY2__LAMB_CNTY__2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LTFLD_S&CTY2__W_ANTON_TP_2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_EST_2__CLUTTER____2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 2 69.0 KV 526297 TO CLUTTER 2 69.0 KV 526310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_EST_2__SLATON_____2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 2 69.0 KV 526297 TO SLATON 2 69.0 KV 526562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_EST_2__SW_6786_S__2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANTERS 2 69.0 KV 526284 TO LUBBCK_EST 2 69.0 KV 526297 CKT 1 b.2. SW_6786_S 2 69.0 KV 526087 TO PLANTERS 2 69.0 KV 526284 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_EST_6__GEN_2020_060 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO GEN-2020-060 230.0 KV 764875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_STH_3__LUBBCK_EST_3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_STH_3__LYNN_CNTY__3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO WOODROW 3 115.0 KV 526602 CKT 1 b.2. LOAD 1 526602 b.3. WOODROW 3 115.0 KV 526602 TO LYNN_CNTY 3 115.0 KV 526656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LWSTAP_4__112GORE4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 b.2. LOAD 1 511512 b.3. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LWS_NTP4__112GORE4 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LWS___N4__LWS_NTP4 | 3 Phase fault on LWS N4 (511430) 138 kV Bus a. Apply fault at the LWS N4 (511430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS N4 138.0 KV 511430 TO LWS-NTP4 138.0 KV 511471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LYNN_CNTY__3__GRASSLAND__3 | 3 Phase fault on LYNN_CNTY 3 (526656) 115 kV Bus a. Apply fault at the LYNN_CNTY 3 (526656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNN_CNTY 3 115.0 KV 526656 TO GRASSLAND 3 115.0 KV 526676 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__2__FT_SILL2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 b.2. LOAD 1 511469 b.3. FT.SILL2 69.0 KV 511461 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__2__LAW__WC2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 b.2. LOAD 1 511470 b.3. LGORE-S2 69.0 KV 511470 TO LAW WC2 69.0 KV 511503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | L_E_S__7__G18_015_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | L_E_S__7__G18_092_PROX | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G18-092-PROX 345.0 KV 763215 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__7__G20_009_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-009 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | L_E_S__7__G20_075_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-009 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | L_E_S__7__GEN_2018_115 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MADDOX_____3__ENRON_TP___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO PEARLE 3 115.0 KV 528392 CKT 1 b.2. LOAD 1 528392 b.3. LOAD 1* 528392 b.4. ENRON_TP 3 115.0 KV 528317 TO PEARLE 3 115.0 KV 528392 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25W | Transfer | MADDOX_____3__G18_004_TAP | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25W | Transfer | MADDOX_____3__MONUMENT___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO MONUMENT 3 115.0 KV 528491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25W | Transfer | MAPCO______3__JOHNSON_DRW3 | 3 Phase fault on MAPCO 3 (527360) 115 kV Bus a. Apply fault at the MAPCO 3 (527360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPCO 3 115.0 KV 527360 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MCDWL_CREEK6__POTTER_CO__6 | 3 Phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 230.0 KV 523323 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | MILLEN_TPE_3__MILLEN_TPW_3 | 3 Phase fault on MILLEN_TPE 3 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3 115.0 KV 528435 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 b.2. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN 3 115.0 KV 528435 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MILLEN_TPE_3__TAYLOR_____3 | 3 Phase fault on MILLEN_TPE 3 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPE 3 115.0 KV 528436 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 b.2. LOAD 1 528442 b.3. TAYLOR 3 115.0 KV 528413 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MILLEN_TPW_3__MILLEN_TPE_3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MINCO__7__NORMHLL7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MINCO__7__NSUB345 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MONUMENT___3__MONUMNT_TP_3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO MONUMNT_TP 3 115.0 KV 528568 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MONUMENT___3__W_HOBBS____3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MONUMNT_TP_3__BYRD_TP____3 | 3 Phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3 115.0 KV 528568 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MRIETA_2__ROCKYPT4 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MULESHVALLY3__MULSHVLY_TP3 | 3 Phase fault on MULESHVALLY3 (525018) 115 kV Bus a. Apply fault at the MULESHVALLY3 (525018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULESHVALLY3 115.0 KV 525018 TO MULSHVLY_TP3 115.0 KV 525019 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MULSHVLY_TP3__BAILEYCO___3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MULSHVLY_TP3__PLANT_X____3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MUSTANG____3__SEAGRAVES__3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MUSTANG____3__SEMINOLE___3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MUSTANG____6__SEMINOLE___6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | MUSTANG____6__XTO_MAHONEY6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 b.2. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | NA_ENRICH__3__CARDINAL___3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 b.2. LOAD 1 528605 b.3. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NA_ENRICH__3__DRINKARD_TP3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD 3 115.0 KV 528589 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 b.2. LOAD 1 528603 b.3. LOAD 5* 528603 b.4. DRINKARD_TP3 115.0 KV 528533 TO DRINKARD 3 115.0 KV 528589 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NEWHART____6__GEN_2018_089 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO GEN-2018-089 230.0 KV 763186 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | IDV crashes when ran with reclose. | Removing reclose prevents IDV from crashing.
05 - Southwest | 25W | Transfer | NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25W | Transfer | NE_HEREFORD3__TIERABLANCA3 | 3 Phase fault on NE_HEREFORD3 (524567) 115 kV Bus a. Apply fault at the NE_HEREFORD3 (524567) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE_HEREFORD3 115.0 KV 524567 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NICHOLS____6__AMA_SOUTH__6 | 3 Phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 230.0 KV 524044 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | NORRIS_TP__3__CURRY______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NORRIS_TP__3__NORRIS_____3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO NORRIS 3 115.0 KV 524801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NORRIS_TP__3__OASIS______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 b.2. LOAD 1 524863 b.3. FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NORTON_____3__FE_TUCMCARI3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO FE-TUCMCARI3 115.0 KV 524509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NORTON_____3__PLSNT_HILL_3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO PLSNT_HILL 3 115.0 KV 524768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | N_CANAL____3__PECOS______3 | 3 Phase fault on N_CANAL 3 (528137) 115 kV Bus a. Apply fault at the N_CANAL 3 (528137) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CANAL 3 115.0 KV 528137 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | N_CLOVIS_TP3__FE_CLVS_INT3 | 3 Phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CLOVIS_TP3 115.0 KV 524776 TO FE-CLVS_INT3 115.0 KV 524808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | N_CLOVIS_TP3__N_CLOVIS___3 | 3 Phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CLOVIS_TP3 115.0 KV 524776 TO N_CLOVIS 3 115.0 KV 524777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | OASIS______3__CANNON_TP__3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERIMETER 3 115.0 KV 524797 TO OASIS 3 115.0 KV 524874 CKT 1 b.2. CANNON_TP 3 115.0 KV 524790 TO PERIMETER 3 115.0 KV 524797 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OASIS______3__PORTALES___3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OASIS______6__GEN_2020_062 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO GEN-2020-062 230.0 KV 764890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OASIS______6__ROOSEVELT__6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OASIS______6__SN_JUAN_TAP6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO SN_JUAN_TAP6 230.0 KV 524885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OCOTILLO___3__PECOS______3 | 3 Phase fault on OCOTILLO 3 (528132) 115 kV Bus a. Apply fault at the OCOTILLO 3 (528132) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCOTILLO 3 115.0 KV 528132 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ODC_TP_____3__ODC________3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO ODC 3 115.0 KV 527056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ODC_TP_____3__SHELL_CO2__3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO SHELL_CO2 3 115.0 KV 527062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ONEY___4__WASHITA4 | 3 Phase fault on ONEY 4 (521017) 138 kV Bus a. Apply fault at the ONEY 4 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138.0 KV 521017 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OXY_WSEM_TP3__JOHNSON_DRW3 | 3 Phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSEM_TP3 115.0 KV 527325 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | O_K_U__7__G18_092_PROX | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-092-PROX 345.0 KV 763215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | O_K_U__7__G20_009_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PCA________3__CARLSBAD___3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PCA________3__CV_LUSK_TP_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CV-LUSK_TP 3 115.0 KV 527948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PCA________3__POTASH_JCT_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO POTASH_JCT 3 115.0 KV 527962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PECOS______3__HOPI_SUB___3 | 3 Phase fault on PECOS 3 (528178) 115 kV Bus a. Apply fault at the PECOS 3 (528178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 3 115.0 KV 528178 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PHANTOM____3__CHINA_DRAW_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 b.2. LOAD 1 528228 b.3. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | PHANTOM____3__MALAGABEND_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | PITTSB_7__JOHNCO_7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLAINS_INT_3__LEHMAN_TP__3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 b.2. LOAD 1 526944 b.3. LEHMAN_TP 3 115.0 KV 526350 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLAINS_INT_3__YOAKUM_____3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLAINVW_TP_2__HALE_CNTY__2 | 3 Phase fault on PLAINVW_TP 2 (525291) 69 kV Bus a. Apply fault at the PLAINVW_TP 2 (525291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINVW_TP 2 69.0 KV 525291 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLANT_X____3__CASTRO_CNTY3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 b.2. LOAD 1 525480 b.3. BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 b.4. LOAD 1 525056 b.5. CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLANT_X____3__LAMB_CNTY__3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLANT_X____6__G17_146_TAP | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | PLSNT_HILL_3__CURRY______3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO FE-HOLLAND 3 115.0 KV 524831 CKT 1 b.2. LOAD 1 524831 b.3. FE-HOLLAND 3 115.0 KV 524831 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 b.4. LOAD 1 524838 b.5. CURRY 3 115.0 KV 524822 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLSNT_HILL_3__N_CLOVIS_TP3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO N_CLOVIS_TP3 115.0 KV 524776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLSNT_HILL_6__OASIS______6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLSNT_HILL_6__ROOSEVELT__6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | POOLVIL4__CARTRCO4 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PORTALES___2__PORTALES_1_2 | 3 Phase fault on PORTALES 2 (524923) 69 kV Bus a. Apply fault at the PORTALES 2 (524923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 2 69.0 KV 524923 TO PORTALES#1 2 69.0 KV 524941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PORTALES___2__ZODIAC_____2 | 3 Phase fault on PORTALES 2 (524923) 69 kV Bus a. Apply fault at the PORTALES 2 (524923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 2 69.0 KV 524923 TO ZODIAC 2 69.0 KV 524934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PORTALES___3__KILGORE____3 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 115.0 KV 524924 TO GREYHOUND 3 115.0 KV 524977 CKT 1 b.2. LOAD 1 524977 b.3. S_PORTALES 3 115.0 KV 524963 TO GREYHOUND 3 115.0 KV 524977 CKT 1 b.4. LOAD 1 524977 b.5. KILGORE 3 115.0 KV 524935 TO S_PORTALES 3 115.0 KV 524963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | POTASH_JCT_3__CARLSBAD___3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | POTASH_JCT_3__INTREPDW_TP3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO INTREPDW_TP3 115.0 KV 527999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | POTASH_JCT_6__PECOS______6 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 230.0 KV 527963 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | POTTER_CO__6__BUSHLAND___6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO BUSHLAND 6 230.0 KV 524267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | POTTER_CO__6__HARRNG_EST_6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO HARRNG_EST 6 230.0 KV 523979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | POTTER_CO__6__ROLLHILLS__6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO ROLLHILLS 6 230.0 KV 524010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | POTTER_CO__7__TOLK_______7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | QUAHADA____3__DCP_ZIA_TP_3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | QUAHADA____3__LEA_NATIONL3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | QUAHADA____3__PCA________3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 b.2. LOAD 1 528396 b.3. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RANDALL____6__AMA_SOUTH__6 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 230.0 KV 524365 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | RATLIFF4__CARTRCO4 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | RDRUNNER___3__OCHOA______3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 b.2. LOAD 1 528230 b.3. AGAVE_RHILL3 115.0 KV 528230 TO OCHOA 3 115.0 KV 528232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | RED_BLUFF__3__WIPP_______3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAND_DUNES 3 115.0 KV 528016 TO RED_BLUFF 3 115.0 KV 528018 CKT 1 b.2. WIPP 3 115.0 KV 528009 TO SAND_DUNES 3 115.0 KV 528016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | RED_BLUFF__3__WOLFCAMP_TP3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | RKYFORD_TP_3__LAMTON_____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-S_OLTON+3 115.0 KV 525440 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 b.2. LAMTON 3 115.0 KV 525414 TO LC-S_OLTON+3 115.0 KV 525440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RKYFORD_TP_3__PLANT_X____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ROCKYFORD__3__RKYFORD_TP_3 | 3 Phase fault on ROCKYFORD 3 (525393) 115 kV Bus a. Apply fault at the ROCKYFORD 3 (525393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYFORD 3 115.0 KV 525393 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ROCKYPT4__SPRNDAL4 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ROOSEVELT__3__PORTALES___3 | 3 Phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 3 115.0 KV 524908 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ROOSEVELT__6__GEN_2019_003 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO GEN-2019-003 230.0 KV 763483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ROZ________3__SEMINOLE___3 | 3 Phase fault on ROZ 3 (527238) 115 kV Bus a. Apply fault at the ROZ 3 (527238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROZ 3 115.0 KV 527238 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RR_SVC_HV__3__RDRUNNER___3 | 3 Phase fault on RR_SVC_HV 3 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 115.0 KV 528024 TO RDRUNNER 3 115.0 KV 528025 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RSVLT_CC_W_7__RSVLT_CC_E_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_CC_E 7 345.0 KV 527655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RSVLT_CC_W_7__RSVLT_COL1_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_COL1 7 345.0 KV 527666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RSVLT_CC_W_7__RSVLT_COL2_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_COL2 7 345.0 KV 527667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RSWL_SLRCOL3__CHAVES_CNTY3 | 3 Phase fault on RSWL_SLRCOL3 (527455) 115 kV Bus a. Apply fault at the RSWL_SLRCOL3 (527455) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSWL_SLRCOL3 115.0 KV 527455 TO CHAVES_CNTY3 115.0 KV 527482 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RUSHSPR7__GEN_2015_092 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2015-092 345.0 KV 563259 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SAGA_SDCOL_7__SAGA_SMEAS_7 | 3 Phase fault on SAGA_SDCOL 7 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7 (527599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SMEAS 7 345.0 KV 527600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SAMSON_____3__ROSWLL_INT_3 | 3 Phase fault on SAMSON 3 (527546) 115 kV Bus a. Apply fault at the SAMSON 3 (527546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAMSON 3 115.0 KV 527546 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SANGER_SW__3__G18_004_TAP | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SANGER_SW__3__OXYPERMIAN_3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SANGER_SW__3__SW_4J44____3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SAN_ANDS_TP3__DENVER_S___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SAN_ANDS_TP3__SEMINOLE___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SEAGRAVES__2__LG_MC&SMNL_2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO LG-MC&SMNL+2 69.0 KV 527223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SEAGRAVES__2__MOSS_______2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO MOSS 2 69.0 KV 527217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SEAGRAVES__3__FLATLAND___3 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3 (527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 115.0 KV 527202 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SEMINOLE___3__DOSS_______3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO DOSS 3 115.0 KV 527340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SEMINOLE___3__GAINES_____3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO GAINES 3 115.0 KV 527322 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SEQUOYAHJ4__ANADARK4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SHELLC3_TP_3__SHELLC3____3 | 3 Phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELLC3_TP 3 115.0 KV 527068 TO SHELLC3 3 115.0 KV 527074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SHELL_C2___3__DENVER_S___3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SHELL_C2___3__SHELLC3_TP_3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SHELL_CO2__3__EL_PASO____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO EL_PASO 3 115.0 KV 527080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SHELL_CO2__3__MUSTANG____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SIDEWINDER_7__ANDREWS____6 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO ANDREWS 6 345.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | SIDEWINDER_7__HOBBS_INT__7 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | No | No | No | No | No | No | No | Voltage Instability/Voltage Collapse. | Build New Andrews to Road Runner 345 kV Line
05 - Southwest | 25W | Transfer | SLATON_____2__SP_SLATON__2 | 3 Phase fault on SLATON 2 (526562) 69 kV Bus a. Apply fault at the SLATON 2 (526562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLATON 2 69.0 KV 526562 TO SP-SLATON 2 69.0 KV 526569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SN_JUAN_TAP6__SN_JUAN_WND6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO SN_JUAN_WND6 230.0 KV 524889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SOUTH_LOVNG3__MALAGABEND_3 | 3 Phase fault on SOUTH_LOVNG3 (528192) 115 kV Bus a. Apply fault at the SOUTH_LOVNG3 (528192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTH_LOVNG3 115.0 KV 528192 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | SPNSPUR_WND7__SPNSPUR_COL7 | 3 Phase fault on SPNSPUR_WND7 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 345.0 KV 524296 TO SPNSPUR_COL7 345.0 KV 524299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SP_ABERNTHY2__TUCO_INT2__2 | 3 Phase fault on SP-ABERNTHY2 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY2 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 69.0 KV 525731 TO TUCO_INT2 2 69.0 KV 525816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SP_ACUFF___2__CROSBY_____2 | 3 Phase fault on SP-ACUFF +2 (525906) 69 kV Bus a. Apply fault at the SP-ACUFF +2 (525906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ACUFF +2 69.0 KV 525906 TO CROSBY 2 69.0 KV 525925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SP_CROSBY__2__CROSBY_____2 | 3 Phase fault on SP-CROSBY 2 (525915) 69 kV Bus a. Apply fault at the SP-CROSBY 2 (525915) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-CROSBY 2 69.0 KV 525915 TO CROSBY 2 69.0 KV 525925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SP_HALFWAY_2__HALE_CNTY__2 | 3 Phase fault on SP-HALFWAY+2 (525432) 69 kV Bus a. Apply fault at the SP-HALFWAY+2 (525432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-HALFWAY+2 69.0 KV 525432 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SP_UPLAND__SP_WOLF_TP_3 | 3 Phase fault on SP-UPLAND (526198) 115 kV Bus a. Apply fault at the SP-UPLAND (526198) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-UPLAND 115.0 KV 526198 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SP_WOLF_TP_3__SP_WOLFORTH3 | 3 Phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-WOLF_TP 3 115.0 KV 526481 TO SP-WOLFORTH3 115.0 KV 526483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | STANTON_E__2__SW_6786_S__2 | 3 Phase fault on STANTON_E 2 (526075) 69 kV Bus a. Apply fault at the STANTON_E 2 (526075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTON_E 2 69.0 KV 526075 TO SW_6786_S 2 69.0 KV 526087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNDOWN____3__AMOCO_TP___3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 3 115.0 KV 526434 TO AMOCO_TP 3 115.0 KV 526445 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNDOWN____3__COCHRAN____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PACIFIC 3 115.0 KV 526424 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. COCHRAN 3 115.0 KV 526361 TO PACIFIC 3 115.0 KV 526424 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNDOWN____3__HOCKLEY____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNNYSD4__CARTER_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNNYSD4__CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNNYSD4__CHEEKTP4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNNYSD4__ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNNYSD7__G20_074_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | SUNNYSD7__GEN_2017_167 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-167 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SW4J795_E__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_E 3 (527533) 115 kV Bus a. Apply fault at the SW4J795_E 3 (527533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_E 3 115.0 KV 527533 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SW4J795_W__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_W 3 (527534) 115 kV Bus a. Apply fault at the SW4J795_W 3 (527534) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_W 3 115.0 KV 527534 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SW_6786_N__2__SW_6786_S__2 | 3 Phase fault on SW_6786_N 2 (526086) 69 kV Bus a. Apply fault at the SW_6786_N 2 (526086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_6786_N 2 69.0 KV 526086 TO SW_6786_S 2 69.0 KV 526087 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | S_JAL______3__DOLLARHIDE_3 | 3 Phase fault on S_JAL 3 (528547) 115 kV Bus a. Apply fault at the S_JAL 3 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 115.0 KV 528547 TO DOLLARHIDE 3 115.0 KV 528561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | S_PLAINVEW_2__HALE_CNTY__2 | 3 Phase fault on S_PLAINVEW 2 (525298) 69 kV Bus a. Apply fault at the S_PLAINVEW 2 (525298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_PLAINVEW 2 69.0 KV 525298 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | S_W_S__4__ANADARK4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | S_W_S__4__G16_097_TAP | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | S_W_S__4__NORGE__4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | S_W_S__4__WASHITA4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TAYLOR_____3__E_SANGER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | TERRYRD7__G20_074_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TERRY_CNTY_2__LG_BROWNFLD2 | 3 Phase fault on TERRY_CNTY 2 (526735) 69 kV Bus a. Apply fault at the TERRY_CNTY 2 (526735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 2 69.0 KV 526735 TO LG-BROWNFLD2 69.0 KV 526747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TERRY_CNTY_3__AMOCO_TP___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-CLAUENE 3 115.0 KV 526491 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 b.2. LG-LEVELAND3 115.0 KV 526484 TO LG-CLAUENE 3 115.0 KV 526491 CKT 1 b.3. LOAD 1 526491 b.4. AMOCO_TP 3 115.0 KV 526445 TO LG-LEVELAND3 115.0 KV 526484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TERRY_CNTY_3__DENVER_N___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TERRY_CNTY_3__FLATLAND___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. LANOGSU1 trips on voltage protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when these generators trip offline or when the protection settings are disabled to prevent them from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TREASILD7__G20_075_TAP | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | TREASILD7__GEN_2016_091 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TREASILD7__GEN_2016_095 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TREASILD7__GRACMNT7 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | TUCO_INT___2__LH_WIL&ELN_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO LH-WIL&ELN+2 69.0 KV 525853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___2__SP_NEWDEAL_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO SP-NEWDEAL 2 69.0 KV 525885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___3__STANTON_W__3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | IDV crashes when ran with reclose. | Removing reclose prevents IDV from crashing.
05 - Southwest | 25W | Transfer | TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | IDV crashes when ran with reclose. | Removing reclose prevents IDV from crashing.
05 - Southwest | 25W | Transfer | TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | IDV crashes when ran with reclose. | Removing reclose prevents IDV from crashing.
05 - Southwest | 25W | Transfer | TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | IDV crashes when ran with reclose. | Removing reclose prevents IDV from crashing.
05 - Southwest | 25W | Transfer | TUCO_INT___7__CRAWFISH_DR | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO CRAWFISH_DR 345.0 KV 560022 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | TUCO_INT___7__G20_067_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | TULIA_TP___3__KRESS_INT__3 | 3 Phase fault on TULIA_TP 3 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULIA_TP 3 115.0 KV 525179 TO KRESS_INT 3 115.0 KV 525192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | VALIANT7__HUGO___7 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | VERDEN_4__S_W_S__4 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WASHITA4__SLKHILLS_4 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138.0 KV 521089 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WHITTEN____3__LEA_ROAD___3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 3 115.0 KV 528519 TO WHITTEN 3 115.0 KV 528540 CKT 1 b.2. LOAD 1 528540 b.3. LEA_ROAD 3 115.0 KV 528505 TO WARD 3 115.0 KV 528519 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WHITTEN____3__S_JAL______3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITTEN 3 115.0 KV 528540 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WOLFCAMP_TP3__PHANTOM____3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOPCO_PKRLK3 115.0 KV 528020 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 b.2. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | WOLFCAMP_TP3__WOLFCAMP___3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCAMP_TP3 115.0 KV 528235 TO WOLFCAMP 3 115.0 KV 528236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | WOLFCRK4__CHEEKTP4 | 3 Phase fault on WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WOLFFORTH__3__SP_WOLF_TP_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUMA_INT 3 115.0 KV 526475 TO WOLFFORTH 3 115.0 KV 526524 CKT 1 b.2. YUMA_INT 3 115.0 KV 526475 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WOLFFORTH__3__TERRY_CNTY_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 3 115.0 KV 526524 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | WWRDEHV7__BOBCAT_7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BOBCAT 7 345.0 KV 516106 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | WWRDEHV7__BVRCNTY7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BVRCNTY7 345.0 KV 515554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | WWRDEHV7__G07621119_20 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | WWRDEHV7__GEN_2019_012 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | W_HOBBS____3__DRINKARD_TP3 | 3 Phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_HOBBS 3 115.0 KV 528498 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | XTO_MAHONEY6__GEN_2017_239 | 3 Phase fault on XTO_MAHONEY6 (527011) 230 kV Bus a. Apply fault at the XTO_MAHONEY6 (527011) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_MAHONEY6 230.0 KV 527011 TO GEN-2017-239 230.0 KV 761355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_345__G20_059_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | YOAKUM_345__G20_067_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | YOAKUM_345__GEN_2019_011 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2019-011 345.0 KV 763516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | YOAKUM_____3__ARCO_TP____3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_____3__SEAGRAVES__3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 b.2. LOAD 1 527194 b.3. LG-PLSHILL 3 115.0 KV 527194 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_____3__TERRY_CNTY_3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 b.2. TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | ZIA________3__DCP_ZIA_TP_3 | 3 Phase fault on ZIA 3 (528420) 115 kV Bus a. Apply fault at the ZIA 3 (528420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZIA 3 115.0 KV 528420 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | 7_RIVERS___6__528094_0 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6( 528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 528095 TO 7-RIVERS 3 528094 TO 7-RIVER_TR11 528090 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | AMA_SOUTH__6__524414_0 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6( 524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | ANADARK4__520810_0 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ANDREWS____6__528602_0 | 3 Phase fault on ANDREWS 6 (528604) 345 kV Bus a. Apply fault at the ANDREWS 6( 528604) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANDREWS 6 528604 TO ANDREWS 3 528602 TO ANDREWS_TR11 528601 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ATOKA______3__527785_0 | 3 Phase fault on ATOKA 3 (527786) 115 kV Bus a. Apply fault at the ATOKA 3( 527786) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA 3 527786 TO ATOKA 2 527785 TO ATOKA_TR1 1 527784 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARLISLE___3__526159_0 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3( 526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHAVES_CNTY6__527482_0 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6( 527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 527483 TO CHAVES_CNTY3 527482 TO CHAVES_TR2 1 527479 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHINA_DRAW_7__528222_0 | 3 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | COCHRAN____3__526360_0 | 3 Phase fault on COCHRAN 3 (526361) 115 kV Bus a. Apply fault at the COCHRAN 3( 526361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COCHRAN 3 526361 TO COCHRAN 2 526360 TO COCHRAN_TR21 526359 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CORNVIL2__511449_0 | 3 Phase fault on CORNVIL2 (511450) 69 kV Bus a. Apply fault at the CORNVIL2( 511450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CROSBY_____3__525925_0 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3( 525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 525926 TO CROSBY 2 525925 TO CROSBY_TR2 1 525924 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNIGHM_S_6__527864_0 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6( 527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 527867 TO CUNNINHAM 3 527864 TO CUNNHM_TR1 1 527863 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CURRY______3__524821_0 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3( 524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 524822 TO CURRY 2 524821 TO CURRY_TR2 1 524820 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DENVER_N___3__527125_0 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3( 527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 527130 TO DENVER_CTY 2 527125 TO DNVER_N_TR11 527122 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DENVER_S___3__527125_0 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3( 527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 527136 TO DENVER_CTY 2 527125 TO DNVER_S_TR21 527123 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EAGLE_CREEK3__527710_0 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3( 527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 527711 TO EAGLE_CREEK2 527710 TO EGCREEK_TR11 527709 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_CNTY__7__527799_0 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_NORTH_6__527793_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_NORTH_6__527798_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ELGINJT2__511486_0 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | FLOYD_CNTY_3__525779_0 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3( 525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GEN_2020_059__764845_0 | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059( 764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 764840 TO G20-059-XFM1 764845 TO GSU_1_LV 10003 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | GEN_2020_059__764850_0 | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059( 764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 764840 TO G20-059-XFM2 764850 TO GSU_2_LV 20003 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRASSLAND__6__526676_0 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6( 526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HALE_CNTY__3__525453_0 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3( 525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HALE_WNDCL16__525931_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | IDV crashes when ran with reclose. | Removing reclose prevents IDV from crashing.
05 - Southwest | 25S | Transfer | HALE_WNDCL16__525981_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | IDV crashes when ran with reclose. | Removing reclose prevents IDV from crashing.
05 - Southwest | 25S | Transfer | HALE_WNDCL16__525990_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | IDV crashes when ran with reclose. | Removing reclose prevents IDV from crashing.
05 - Southwest | 25S | Transfer | HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOCKLEY____3__526019_0 | 3 Phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply fault at the HOCKLEY 3( 526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCKLEY 3 526020 TO HOCKLEY 2 526019 TO HOCKLEY_TR21 526018 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HUGO___7__520560_0 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | INK_BASIN__6__527027_0 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6( 527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JOHNCO_4__514809_0 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LAMB_CNTY__6__525636_0 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6( 525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-017 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2020-017 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25S | Transfer | LE_WEST_SUB3__528337_0 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3( 528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 528333 TO WC_SEC 1 528337 TO WC_TER 1 528336 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_EST_3__526297_0 | 3 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3( 526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_EST_6__526298_0 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6( 526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_STH_3__526267_0 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3( 526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 526268 TO LUBBCK_STH 2 526267 TO LBB_STH TR21 526266 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_STH_6__526268_0 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6( 526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LYNN_CNTY__3__526655_0 | 3 Phase fault on LYNN_CNTY 3 (526656) 115 kV Bus a. Apply fault at the LYNN_CNTY 3( 526656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNN_CNTY 3 526656 TO LYNN_CNTY 2 526655 TO LYNN_TR2 1 526654 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MUSTANG____6__527146_0 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6( 527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NEWHART____6__525460_0 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6( 525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25S | Transfer | N_LOVING___7__528182_0 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OASIS______6__524874_0 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6( 524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 524875 TO OASIS 3 524874 TO OASIS_TR1 1 524872 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PCA________3__527929_0 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3( 527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 527930 TO PCA 2 527929 TO PCA_TR1 1 527928 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PECOS______6__528178_0 | 3 Phase fault on PECOS 6 (528179) 230 kV Bus a. Apply fault at the PECOS 6( 528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 528179 TO PECOS 3 528178 TO PECOS_TR1 1 528176 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PHANTOM____7__528013_0 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLANT_X____6__525480_0 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6( 525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLSNT_HILL_6__524768_0 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6( 524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 524770 TO PLSNT_HILL 3 524768 TO PLSNHIL_TR11 524767 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PORTALES___3__524923_0 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3( 524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 524924 TO PORTALES 2 524923 TO PORTLES_TR21 524922 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTASH_JCT_3__527961_0 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3( 527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 527962 TO POTASH_JCT 2 527961 TO POTASH_TR3 1 527960 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTASH_JCT_6__527962_0 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6( 527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 527963 TO POTASH_JCT 3 527962 TO POTASH_TR1 1 527958 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTTER_CO__7__523959_0 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7( 523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ROCKYPT2__515164_0 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ROOSEVELT__6__524908_0 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6( 524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ROSWLL_INT_3__527563_0 | 3 Phase fault on ROSWLL_INT 3 (527564) 115 kV Bus a. Apply fault at the ROSWLL_INT 3( 527564) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSWLL_INT 3 527564 TO ROSWLL_INT 2 527563 TO ROSWELL_TR21 527562 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RUSHSPR7__511965_0 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SAGA_SDCOL_7__527628_0 | 3 Phase fault on SAGA_SDCOL 7 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7( 527599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SDCOL 7 527599 TO SUB #1 527628 TO SAGA_SCLTR11 527623 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SAGA_SDCOL_7__527629_0 | 3 Phase fault on SAGA_SDCOL 7 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7( 527599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SDCOL 7 527599 TO SUB #2 527629 TO SAGA_SCLTR21 527624 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SEAGRAVES__3__527201_0 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3( 527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 527202 TO SEAGRAVES 2 527201 TO SEAGRAV_TR11 527200 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SEMINOLE___6__527275_0 | 3 Phase fault on SEMINOLE 6 (527276) 230 kV Bus a. Apply fault at the SEMINOLE 6( 527276) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 6 527276 TO SEMINOLE 3 527275 TO SEMINLE_TR21 527274 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNDOWN____6__526434_0 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6( 526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | S_W_S__2__511477_0 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | S_W_S__4__511849_0 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRY_CNTY_3__526735_0 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3( 526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 526736 TO TERRY_CNTY 2 526735 TO TERRY_TR2 1 526734 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK_______6__525549_0 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6( 525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 525531 TO TOLK 7 525549 TO TOLK_TF3 525539 CKT 3 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-017 trips on frequency protection settings. LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. Disabling frequency protection settings for GEN-2020-017 prevents trip. There are no stability constraints when these generators trip offline or when the protection settings are disabled to prevent them from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 1 525537 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Antelope units trip on power unbalance. | Reducing fault clearing time to 5 cycles prevents trip. There are no stability constraints when these generators trip offline or when the fault clearing times are reduced to 5 cycles to prevent them from tripping.
05 - Southwest | 25S | Transfer | TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | WASHITA4__521088_0 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4( 521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WOLFFORTH__6__526524_0 | 3 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6( 526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | 7_RIVERS___6__528094_0 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6( 528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 528095 TO 7-RIVERS 3 528094 TO 7-RIVER_TR11 528090 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | AMA_SOUTH__6__524414_0 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6( 524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | ANADARK4__520810_0 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ANDREWS____6__528602_0 | 3 Phase fault on ANDREWS 6 (528604) 345 kV Bus a. Apply fault at the ANDREWS 6( 528604) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANDREWS 6 528604 TO ANDREWS 3 528602 TO ANDREWS_TR11 528601 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ATOKA______3__527785_0 | 3 Phase fault on ATOKA 3 (527786) 115 kV Bus a. Apply fault at the ATOKA 3( 527786) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA 3 527786 TO ATOKA 2 527785 TO ATOKA_TR1 1 527784 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARLISLE___3__526159_0 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3( 526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHAVES_CNTY6__527482_0 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6( 527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 527483 TO CHAVES_CNTY3 527482 TO CHAVES_TR2 1 527479 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHINA_DRAW_7__528222_0 | 3 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | COCHRAN____3__526360_0 | 3 Phase fault on COCHRAN 3 (526361) 115 kV Bus a. Apply fault at the COCHRAN 3( 526361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COCHRAN 3 526361 TO COCHRAN 2 526360 TO COCHRAN_TR21 526359 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CORNVIL2__511449_0 | 3 Phase fault on CORNVIL2 (511450) 69 kV Bus a. Apply fault at the CORNVIL2( 511450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CROSBY_____3__525925_0 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3( 525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 525926 TO CROSBY 2 525925 TO CROSBY_TR2 1 525924 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNIGHM_S_6__527864_0 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6( 527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 527867 TO CUNNINHAM 3 527864 TO CUNNHM_TR1 1 527863 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CURRY______3__524821_0 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3( 524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 524822 TO CURRY 2 524821 TO CURRY_TR2 1 524820 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DENVER_N___3__527125_0 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3( 527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 527130 TO DENVER_CTY 2 527125 TO DNVER_N_TR11 527122 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DENVER_S___3__527125_0 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3( 527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 527136 TO DENVER_CTY 2 527125 TO DNVER_S_TR21 527123 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EAGLE_CREEK3__527710_0 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3( 527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 527711 TO EAGLE_CREEK2 527710 TO EGCREEK_TR11 527709 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_CNTY__7__527799_0 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | EDDY_NORTH_6__527793_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | EDDY_NORTH_6__527798_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | ELGINJT2__511486_0 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | FLOYD_CNTY_3__525779_0 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3( 525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GEN_2020_059__764845_0 | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059( 764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 764840 TO G20-059-XFM1 764845 TO GSU_1_LV 10003 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | GEN_2020_059__764850_0 | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059( 764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 764840 TO G20-059-XFM2 764850 TO GSU_2_LV 20003 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GRASSLAND__6__526676_0 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6( 526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HALE_CNTY__3__525453_0 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3( 525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HALE_WNDCL16__525931_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HALE_WNDCL16__525981_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HALE_WNDCL16__525990_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generators trip when this IDV is ran with default acceleration of 0.6 | Reducing acceleration to 0.3 prevents generators from tripping.
05 - Southwest | 25W | Transfer | HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generators trip when this IDV is ran with default acceleration of 0.6 | Reducing acceleration to 0.3 prevents generators from tripping.
05 - Southwest | 25W | Transfer | HOCKLEY____3__526019_0 | 3 Phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply fault at the HOCKLEY 3( 526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCKLEY 3 526020 TO HOCKLEY 2 526019 TO HOCKLEY_TR21 526018 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HUGO___7__520560_0 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | INK_BASIN__6__527027_0 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6( 527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | JOHNCO_4__514809_0 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generators trip when this IDV is ran with default acceleration of 0.6. Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing acceleration to 0.3 prevents generators from tripping. Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | LAMB_CNTY__6__525636_0 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6( 525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-017 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2020-017 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
05 - Southwest | 25W | Transfer | LE_WEST_SUB3__528337_0 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3( 528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 528333 TO WC_SEC 1 528337 TO WC_TER 1 528336 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_EST_3__526297_0 | 3 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3( 526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_EST_6__526298_0 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6( 526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_STH_3__526267_0 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3( 526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 526268 TO LUBBCK_STH 2 526267 TO LBB_STH TR21 526266 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_STH_6__526268_0 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6( 526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LYNN_CNTY__3__526655_0 | 3 Phase fault on LYNN_CNTY 3 (526656) 115 kV Bus a. Apply fault at the LYNN_CNTY 3( 526656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNN_CNTY 3 526656 TO LYNN_CNTY 2 526655 TO LYNN_TR2 1 526654 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MUSTANG____6__527146_0 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6( 527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NEWHART____6__525460_0 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6( 525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | N_LOVING___7__528182_0 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | OASIS______6__524874_0 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6( 524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 524875 TO OASIS 3 524874 TO OASIS_TR1 1 524872 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PCA________3__527929_0 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3( 527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 527930 TO PCA 2 527929 TO PCA_TR1 1 527928 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PECOS______6__528178_0 | 3 Phase fault on PECOS 6 (528179) 230 kV Bus a. Apply fault at the PECOS 6( 528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 528179 TO PECOS 3 528178 TO PECOS_TR1 1 528176 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PHANTOM____7__528013_0 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | PLANT_X____6__525480_0 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6( 525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLSNT_HILL_6__524768_0 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6( 524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 524770 TO PLSNT_HILL 3 524768 TO PLSNHIL_TR11 524767 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PORTALES___3__524923_0 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3( 524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 524924 TO PORTALES 2 524923 TO PORTLES_TR21 524922 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generators trip when this IDV is ran with default acceleration of 0.6 | Reducing acceleration to 0.3 prevents generators from tripping.
05 - Southwest | 25W | Transfer | POTASH_JCT_3__527961_0 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3( 527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 527962 TO POTASH_JCT 2 527961 TO POTASH_TR3 1 527960 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | POTASH_JCT_6__527962_0 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6( 527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 527963 TO POTASH_JCT 3 527962 TO POTASH_TR1 1 527958 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | POTTER_CO__7__523959_0 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7( 523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillations observed local to Oklaunion and Lawton Eastside 345 kV buses. | Reducing the acceleration factor resolves the numerical oscillations observed.
05 - Southwest | 25W | Transfer | ROCKYPT2__515164_0 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ROOSEVELT__6__524908_0 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6( 524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ROSWLL_INT_3__527563_0 | 3 Phase fault on ROSWLL_INT 3 (527564) 115 kV Bus a. Apply fault at the ROSWLL_INT 3( 527564) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSWLL_INT 3 527564 TO ROSWLL_INT 2 527563 TO ROSWELL_TR21 527562 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RUSHSPR7__511965_0 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SAGA_SDCOL_7__527628_0 | 3 Phase fault on SAGA_SDCOL 7 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7( 527599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SDCOL 7 527599 TO SUB #1 527628 TO SAGA_SCLTR11 527623 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SAGA_SDCOL_7__527629_0 | 3 Phase fault on SAGA_SDCOL 7 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7( 527599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SDCOL 7 527599 TO SUB #2 527629 TO SAGA_SCLTR21 527624 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SEAGRAVES__3__527201_0 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3( 527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 527202 TO SEAGRAVES 2 527201 TO SEAGRAV_TR11 527200 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SEMINOLE___6__527275_0 | 3 Phase fault on SEMINOLE 6 (527276) 230 kV Bus a. Apply fault at the SEMINOLE 6( 527276) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 6 527276 TO SEMINOLE 3 527275 TO SEMINLE_TR21 527274 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNDOWN____6__526434_0 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6( 526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | S_W_S__2__511477_0 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | S_W_S__4__511849_0 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TERRY_CNTY_3__526735_0 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3( 526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 526736 TO TERRY_CNTY 2 526735 TO TERRY_TR2 1 526734 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK_______6__525549_0 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6( 525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 525531 TO TOLK 7 525549 TO TOLK_TF3 525539 CKT 3 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANOGSU1 trips on voltage protection settings. | Disabling voltage protection settings for LANOGSU1 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 1 525537 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | WASHITA4__521088_0 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4( 521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WOLFFORTH__6__526524_0 | 3 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6( 526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BECKHAM7_345kV_516059 | Apply single-phase fault on: BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1, near BECKHAM7 345 kV for 6 cycles with stuck breaker at BECKHAM7 345 kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BRU_SUB6_230kV_527009 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, near BRU_SUB 6 230 kV for 7 cycles with stuck breaker at BRU_SUB 6 230 kV. Clear Fault after 10 cycles and trip: BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHINA_DRAW7_345kV_528223 | Apply single-phase fault on: N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, near CHINA_DRAW 7 345 kV for 6 cycles with stuck breaker at CHINA_DRAW 7 345 kV. Clear Fault after 10 cycles and trip: PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CRAWFISH_DR_345kV_560022 | Apply single-phase fault on: BORDER 7 345.0 KV 515458 TO CRAWFISH_DR 345.0 KV 560022 CKT 1, near CRAWFISH_DR 345 kV for 6 cycles with stuck breaker at CRAWFISH_DR 345 kV. Clear Fault after 10 cycles and trip: TUCO_INT 7 345.0 KV 525832 TO CRAWFISH_DR 345.0 KV 560022 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-009 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25S | Transfer | CROSSROADS7_345kV_527656 | Apply single-phase fault on: CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT LX, near CROSSROADS 7 345 kV for 6 cycles with stuck breaker at CROSSROADS 7 345 kV. Clear Fault after 10 cycles and trip: TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAM3_115kV_527864 | Apply single-phase fault on: CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1, near CUNNINHAM 3 115 kV for 7 cycles with stuck breaker at CUNNINHAM 3 115 kV. Clear Fault after 10 cycles and trip: CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAM6_230kV_527867 | Apply single-phase fault on: CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, near CUNNIGHM_S 6 230 kV for 7 cycles with stuck breaker at CUNNIGHM_S 6 230 kV. Clear Fault after 10 cycles and trip: CUNNIGHM_N 6 230.0 KV 527865 TO CUNNIGHM_S 6 230.0 KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAMN6_230kV_527865 | Apply single-phase fault on: CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1, near CUNNIGHM_N 6 230 kV for 7 cycles with stuck breaker at CUNNIGHM_N 6 230 kV. Clear Fault after 10 cycles and trip: EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_CNTY7_345kV_527802 | Apply single-phase fault on: EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1, near EDDY_CNTY 7 345 kV for 6 cycles with stuck breaker at EDDY_CNTY 7 345 kV. Clear Fault after 10 cycles and trip: CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT3_115kV_527891 | Apply single-phase fault on: HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1, near HOBBS_INT 3 115 kV for 7 cycles with stuck breaker at HOBBS_INT 3 115 kV. Clear Fault after 10 cycles and trip: HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT6_230kV_527894 | Apply single-phase fault on: CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, near HOBBS_INT 6 230 kV for 7 cycles with stuck breaker at HOBBS_INT 6 230 kV. Clear Fault after 10 cycles and trip: INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT7_345kV_527896 | Apply single-phase fault on: HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, near HOBBS_INT 7 345 kV for 6 cycles with stuck breaker at HOBBS_INT 7 345 kV. Clear Fault after 10 cycles and trip: SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOCKLEY3_115kV_526020 | Apply single-phase fault on: LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1, near HOCKLEY 3 115 kV for 7 cycles with stuck breaker at HOCKLEY 3 115 kV. Clear Fault after 10 cycles and trip: LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | INK_BASIN3_115kV_527027 | Apply single-phase fault on: INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1, near INK_BASIN 3 115 kV for 7 cycles with stuck breaker at INK_BASIN 3 115 kV. Clear Fault after 10 cycles and trip: INK_BASIN 3 115.0 KV 527027 TO LEWAITS 3 115.0 KV 528325 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JONES6_115kV_526337 | Apply single-phase fault on: TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, near JONES 6 230 kV for 7 cycles with stuck breaker at JONES 6 230 kV. Clear Fault after 10 cycles and trip: LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | KIOWA7_345kV_527965 | Apply single-phase fault on: HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, near KIOWA 7 345 kV for 6 cycles with stuck breaker at KIOWA 7 345 kV. Clear Fault after 10 cycles and trip: KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LAMB_CNTY3_115kV_525636 | Apply single-phase fault on: PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1, near LAMB_CNTY 3 115 kV for 7 cycles with stuck breaker at LAMB_CNTY 3 115 kV. Clear Fault after 10 cycles and trip: LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LAMB_CNTY_69kV_525635 | Apply single-phase fault on: LAMB_CNTY 2 69.0 KV 525635 TO LC LTTLFLD 69.0 KV 525650 CKT 1 LC LTTLFLD 230.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1, near LAMB_CNTY 2 69 kV for 7 cycles with stuck breaker at LAMB_CNTY 2 69 kV. Clear Fault after 10 cycles and trip: W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 LOAD 1 525613 LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 LOAD 1 525606 SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LES4_138kV_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LES7_345kV_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBUCK_EST_115kV_526298 | Apply single-phase fault on: TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1, near LUBBCK_EST 3 115 kV for 7 cycles with stuck breaker at LUBBCK_EST 3 115 kV. Clear Fault after 10 cycles and trip: CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MUSTANG6_230kV_527149 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1, near MUSTANG 6 230 kV for 7 cycles with stuck breaker at MUSTANG 6 230 kV. Clear Fault after 10 cycles and trip: MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NA_ENRICH3_115kV_528603 | Apply single-phase fault on: ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1, near NA_ENRICH 3 115 kV for 7 cycles with stuck breaker at NA_ENRICH 3 115 kV. Clear Fault after 10 cycles and trip: NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 LOAD 1 528605 CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | N_LOVING7_345kV_528185 | Apply single-phase fault on: N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, near N_LOVING 7 345 kV for 6 cycles with stuck breaker at N_LOVING 7 345 kV. Clear Fault after 10 cycles and trip: KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OASIS3_115kV_524874 | Apply single-phase fault on: OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1, near OASIS 3 115 kV for 7 cycles with stuck breaker at OASIS 3 115 kV. Clear Fault after 10 cycles and trip: NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 LOAD 1 524863 FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OASIS6_230kV_524875 | Apply single-phase fault on: OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, near OASIS 6 230 kV for 7 cycles with stuck breaker at OASIS 6 230 kV. Clear Fault after 10 cycles and trip: PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PHANTOM7_345kV_528015 | Apply single-phase fault on: PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, near PHANTOM 7 345 kV for 6 cycles with stuck breaker at PHANTOM 7 345 kV. Clear Fault after 10 cycles and trip: PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLANT_X3_115kV_525480 | Apply single-phase fault on: BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 LOAD 1 525480 BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 LOAD 1 525056 CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1, near PLANT_X 3 115 kV for 7 cycles with stuck breaker at PLANT_X 3 115 kV. Clear Fault after 10 cycles and trip: RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTTER_CO7_345kV_523961 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 2, near POTTER_CO 7 345 kV for 6 cycles with stuck breaker at POTTER_CO 7 345 kV. Clear Fault after 10 cycles and trip: CHISHOLM7 345.0 KV 511553 TO POTTER_CO 7 345.0 KV 523961 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER3_115kV_528025 | Apply single-phase fault on: RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1, near RDRUNNER 3 115 kV for 7 cycles with stuck breaker at RDRUNNER 3 115 kV. Clear Fault after 10 cycles and trip: RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER7_345kV_528027 | Apply single-phase fault on: PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, near RDRUNNER 7 345 kV for 6 cycles with stuck breaker at RDRUNNER 7 345 kV. Clear Fault after 10 cycles and trip: HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT XA | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ROOSEVELT6_230kV_524909 | Apply single-phase fault on: OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, near ROOSEVELT 6 230 kV for 7 cycles with stuck breaker at ROOSEVELT 6 230 kV. Clear Fault after 10 cycles and trip: PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNDOWN6_230kV_526435 | Apply single-phase fault on: SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1, near SUNDOWN 6 230 kV for 7 cycles with stuck breaker at SUNDOWN 6 230 kV. Clear Fault after 10 cycles and trip: AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD7_345kV_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRYRD7_345kV_511568 | Apply single-phase fault on: TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345 kV for 6 cycles with stuck breaker at TERRYRD7 345 kV. Clear Fault after 10 cycles and trip: TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK6_230kV_525531 | Apply single-phase fault on: TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1, near TOLK 6 230 kV for 7 cycles with stuck breaker at TOLK 6 230 kV. Clear Fault after 10 cycles and trip: PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK7_345kV_525549 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 2, near TOLK 7 345 kV for 6 cycles with stuck breaker at TOLK 7 345 kV. Clear Fault after 10 cycles and trip: TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT6_230kV_525830 | Apply single-phase fault on: TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, near TUCO_INT 6 230 kV for 7 cycles with stuck breaker at TUCO_INT 6 230 kV. Clear Fault after 10 cycles and trip: SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT7_345kV_525832 | Apply single-phase fault on: TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1, near TUCO_INT 7 345 kV for 6 cycles with stuck breaker at TUCO_INT 7 345 kV. Clear Fault after 10 cycles and trip: TUCO_INT 7 345.0 KV 525832 TO CRAWFISH_DR 345.0 KV 560022 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM3_115kV_526934 | Apply single-phase fault on: PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1, near YOAKUM 3 115 kV for 7 cycles with stuck breaker at YOAKUM 3 115 kV. Clear Fault after 10 cycles and trip: PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM6_230kV_526935 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, near YOAKUM 6 230 kV for 7 cycles with stuck breaker at YOAKUM 6 230 kV. Clear Fault after 10 cycles and trip: AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_345kV_526936 | Apply single-phase fault on: YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1, near YOAKUM_345 345 kV for 6 cycles with stuck breaker at YOAKUM_345 345 kV. Clear Fault after 10 cycles and trip: YOAKUM_345 345.0 KV 526936 TO G20-059-TAP 345.0 KV 764866 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BECKHAM7_345kV_516059 | Apply single-phase fault on: BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1, near BECKHAM7 345 kV for 6 cycles with stuck breaker at BECKHAM7 345 kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BRU_SUB6_230kV_527009 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, near BRU_SUB 6 230 kV for 7 cycles with stuck breaker at BRU_SUB 6 230 kV. Clear Fault after 10 cycles and trip: BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHINA_DRAW7_345kV_528223 | Apply single-phase fault on: N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, near CHINA_DRAW 7 345 kV for 6 cycles with stuck breaker at CHINA_DRAW 7 345 kV. Clear Fault after 10 cycles and trip: PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CRAWFISH_DR_345kV_560022 | Apply single-phase fault on: BORDER 7 345.0 KV 515458 TO CRAWFISH_DR 345.0 KV 560022 CKT 1, near CRAWFISH_DR 345 kV for 6 cycles with stuck breaker at CRAWFISH_DR 345 kV. Clear Fault after 10 cycles and trip: TUCO_INT 7 345.0 KV 525832 TO CRAWFISH_DR 345.0 KV 560022 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CROSSROADS7_345kV_527656 | Apply single-phase fault on: CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT LX, near CROSSROADS 7 345 kV for 6 cycles with stuck breaker at CROSSROADS 7 345 kV. Clear Fault after 10 cycles and trip: TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNINHAM3_115kV_527864 | Apply single-phase fault on: CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1, near CUNNINHAM 3 115 kV for 7 cycles with stuck breaker at CUNNINHAM 3 115 kV. Clear Fault after 10 cycles and trip: CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNINHAM6_230kV_527867 | Apply single-phase fault on: CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, near CUNNIGHM_S 6 230 kV for 7 cycles with stuck breaker at CUNNIGHM_S 6 230 kV. Clear Fault after 10 cycles and trip: CUNNIGHM_N 6 230.0 KV 527865 TO CUNNIGHM_S 6 230.0 KV 527867 CKT *1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNINHAMN6_230kV_527865 | Apply single-phase fault on: CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1, near CUNNIGHM_N 6 230 kV for 7 cycles with stuck breaker at CUNNIGHM_N 6 230 kV. Clear Fault after 10 cycles and trip: EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_CNTY7_345kV_527802 | Apply single-phase fault on: EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1, near EDDY_CNTY 7 345 kV for 6 cycles with stuck breaker at EDDY_CNTY 7 345 kV. Clear Fault after 10 cycles and trip: CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HOBBS_INT3_115kV_527891 | Apply single-phase fault on: HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1, near HOBBS_INT 3 115 kV for 7 cycles with stuck breaker at HOBBS_INT 3 115 kV. Clear Fault after 10 cycles and trip: HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HOBBS_INT6_230kV_527894 | Apply single-phase fault on: CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, near HOBBS_INT 6 230 kV for 7 cycles with stuck breaker at HOBBS_INT 6 230 kV. Clear Fault after 10 cycles and trip: INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HOBBS_INT7_345kV_527896 | Apply single-phase fault on: HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, near HOBBS_INT 7 345 kV for 6 cycles with stuck breaker at HOBBS_INT 7 345 kV. Clear Fault after 10 cycles and trip: SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HOCKLEY3_115kV_526020 | Apply single-phase fault on: LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1, near HOCKLEY 3 115 kV for 7 cycles with stuck breaker at HOCKLEY 3 115 kV. Clear Fault after 10 cycles and trip: LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | INK_BASIN3_115kV_527027 | Apply single-phase fault on: INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1, near INK_BASIN 3 115 kV for 7 cycles with stuck breaker at INK_BASIN 3 115 kV. Clear Fault after 10 cycles and trip: INK_BASIN 3 115.0 KV 527027 TO LEWAITS 3 115.0 KV 528325 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | JONES6_115kV_526337 | Apply single-phase fault on: TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, near JONES 6 230 kV for 7 cycles with stuck breaker at JONES 6 230 kV. Clear Fault after 10 cycles and trip: LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | KIOWA7_345kV_527965 | Apply single-phase fault on: HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, near KIOWA 7 345 kV for 6 cycles with stuck breaker at KIOWA 7 345 kV. Clear Fault after 10 cycles and trip: KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LAMB_CNTY3_115kV_525636 | Apply single-phase fault on: PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1, near LAMB_CNTY 3 115 kV for 7 cycles with stuck breaker at LAMB_CNTY 3 115 kV. Clear Fault after 10 cycles and trip: LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LAMB_CNTY_69kV_525635 | Apply single-phase fault on: LAMB_CNTY 2 69.0 KV 525635 TO LC LTTLFLD 69.0 KV 525650 CKT 1 LC LTTLFLD 230.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1, near LAMB_CNTY 2 69 kV for 7 cycles with stuck breaker at LAMB_CNTY 2 69 kV. Clear Fault after 10 cycles and trip: W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 LOAD 1 525613 LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 LOAD 1 525606 SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LES4_138kV_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LES7_345kV_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBUCK_EST_115kV_526298 | Apply single-phase fault on: TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1, near LUBBCK_EST 3 115 kV for 7 cycles with stuck breaker at LUBBCK_EST 3 115 kV. Clear Fault after 10 cycles and trip: CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MUSTANG6_230kV_527149 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1, near MUSTANG 6 230 kV for 7 cycles with stuck breaker at MUSTANG 6 230 kV. Clear Fault after 10 cycles and trip: MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NA_ENRICH3_115kV_528603 | Apply single-phase fault on: ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1, near NA_ENRICH 3 115 kV for 7 cycles with stuck breaker at NA_ENRICH 3 115 kV. Clear Fault after 10 cycles and trip: NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 LOAD 1 528605 CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | N_LOVING7_345kV_528185 | Apply single-phase fault on: N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, near N_LOVING 7 345 kV for 6 cycles with stuck breaker at N_LOVING 7 345 kV. Clear Fault after 10 cycles and trip: KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OASIS3_115kV_524874 | Apply single-phase fault on: OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1, near OASIS 3 115 kV for 7 cycles with stuck breaker at OASIS 3 115 kV. Clear Fault after 10 cycles and trip: NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 LOAD 1 524863 FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OASIS6_230kV_524875 | Apply single-phase fault on: OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, near OASIS 6 230 kV for 7 cycles with stuck breaker at OASIS 6 230 kV. Clear Fault after 10 cycles and trip: PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PHANTOM7_345kV_528015 | Apply single-phase fault on: PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, near PHANTOM 7 345 kV for 6 cycles with stuck breaker at PHANTOM 7 345 kV. Clear Fault after 10 cycles and trip: PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLANT_X3_115kV_525480 | Apply single-phase fault on: BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 LOAD 1 525480 BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 LOAD 1 525056 CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1, near PLANT_X 3 115 kV for 7 cycles with stuck breaker at PLANT_X 3 115 kV. Clear Fault after 10 cycles and trip: RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | POTTER_CO7_345kV_523961 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 2, near POTTER_CO 7 345 kV for 6 cycles with stuck breaker at POTTER_CO 7 345 kV. Clear Fault after 10 cycles and trip: CHISHOLM7 345.0 KV 511553 TO POTTER_CO 7 345.0 KV 523961 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RDRUNNER3_115kV_528025 | Apply single-phase fault on: RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1, near RDRUNNER 3 115 kV for 7 cycles with stuck breaker at RDRUNNER 3 115 kV. Clear Fault after 10 cycles and trip: RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RDRUNNER7_345kV_528027 | Apply single-phase fault on: PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, near RDRUNNER 7 345 kV for 6 cycles with stuck breaker at RDRUNNER 7 345 kV. Clear Fault after 10 cycles and trip: HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT XA | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ROOSEVELT6_230kV_524909 | Apply single-phase fault on: OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, near ROOSEVELT 6 230 kV for 7 cycles with stuck breaker at ROOSEVELT 6 230 kV. Clear Fault after 10 cycles and trip: PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNDOWN6_230kV_526435 | Apply single-phase fault on: SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1, near SUNDOWN 6 230 kV for 7 cycles with stuck breaker at SUNDOWN 6 230 kV. Clear Fault after 10 cycles and trip: AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNNYSD7_345kV_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TERRYRD7_345kV_511568 | Apply single-phase fault on: TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345 kV for 6 cycles with stuck breaker at TERRYRD7 345 kV. Clear Fault after 10 cycles and trip: TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK6_230kV_525531 | Apply single-phase fault on: TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1, near TOLK 6 230 kV for 7 cycles with stuck breaker at TOLK 6 230 kV. Clear Fault after 10 cycles and trip: PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK7_345kV_525549 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 2, near TOLK 7 345 kV for 6 cycles with stuck breaker at TOLK 7 345 kV. Clear Fault after 10 cycles and trip: TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT6_230kV_525830 | Apply single-phase fault on: TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, near TUCO_INT 6 230 kV for 7 cycles with stuck breaker at TUCO_INT 6 230 kV. Clear Fault after 10 cycles and trip: SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT7_345kV_525832 | Apply single-phase fault on: TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1, near TUCO_INT 7 345 kV for 6 cycles with stuck breaker at TUCO_INT 7 345 kV. Clear Fault after 10 cycles and trip: TUCO_INT 7 345.0 KV 525832 TO CRAWFISH_DR 345.0 KV 560022 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM3_115kV_526934 | Apply single-phase fault on: PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1, near YOAKUM 3 115 kV for 7 cycles with stuck breaker at YOAKUM 3 115 kV. Clear Fault after 10 cycles and trip: PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM6_230kV_526935 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, near YOAKUM 6 230 kV for 7 cycles with stuck breaker at YOAKUM 6 230 kV. Clear Fault after 10 cycles and trip: AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_345kV_526936 | Apply single-phase fault on: YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1, near YOAKUM_345 345 kV for 6 cycles with stuck breaker at YOAKUM_345 345 kV. Clear Fault after 10 cycles and trip: YOAKUM_345 345.0 KV 526936 TO G20-059-TAP 345.0 KV 764866 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764866 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 560022 TO 525832 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 560022 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 764866 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764866 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 560022 TO 525832 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 560022 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 764866 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-009 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 - Southwest | 25W | Transfer | LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2020-006 | 01 - North | 588550 | GEN-2017-010 | 230 | 4.7651 | 5.1515 | 0.3864
GEN-2020-006 | 01 - North | 652243 | FAITH 7 | 115 | 2.3948 | 2.4019 | 0.0071
GEN-2020-006 | 01 - North | 652248 | MAURINE8 | 69 | 2.7176 | 2.7253 | 0.0077
GEN-2020-006 | 01 - North | 652403 | DAWSONC4 | 230 | 4.5243 | 4.5542 | 0.0299
GEN-2020-006 | 01 - North | 652411 | MI CTYE4 | 230 | 2.9045 | 2.9381 | 0.0336
GEN-2020-006 | 01 - North | 652412 | MI CTYE7 | 115 | 3.9269 | 3.9505 | 0.0236
GEN-2020-006 | 01 - North | 652424 | BELFELD3 | 345 | 6.9689 | 7.0151 | 0.0462
GEN-2020-006 | 01 - North | 652425 | BELFELD4 | 230 | 9.7619 | 9.8753 | 0.1134
GEN-2020-006 | 01 - North | 652468 | HEBRON 4 | 230 | 5.824 | 5.8377 | 0.0137
GEN-2020-006 | 01 - North | 652480 | MAURINE7 | 115 | 4.0677 | 4.0967 | 0.029
GEN-2020-006 | 01 - North | 652484 | NUNDRWD4 | 230 | 3.7399 | 3.7566 | 0.0167
GEN-2020-006 | 01 - North | 652491 | SULPHUR | 115 | 2.9865 | 2.9951 | 0.0086
GEN-2020-006 | 01 - North | 652497 | MAURINE4 | 230 | 2.9058 | 2.9478 | 0.042
GEN-2020-006 | 01 - North | 652616 | MINGUSVILLE4 | 230 | 4.5694 | 4.5931 | 0.0237
GEN-2020-006 | 01 - North | 652884 | NUNDRWD-LNX3 | 230 | 3.7338 | 3.7505 | 0.0167
GEN-2020-006 | 01 - North | 654493 | WILCRKXFRP 3 | 115 | 2.9845 | 2.9931 | 0.0086
GEN-2020-006 | 01 - North | 655730 | CENTIPED-UM7 | 115 | 3.1314 | 3.1641 | 0.0327
GEN-2020-006 | 01 - North | 659124 | DICKINSN-BE4 | 230 | 7.2801 | 7.3315 | 0.0514
GEN-2020-006 | 01 - North | 659125 | DICKINSN-BE7 | 115 | 9.5414 | 9.5935 | 0.0521
GEN-2020-006 | 01 - North | 659183 | CHARL_CK-BE3 | 345 | 11.2511 | 11.2805 | 0.0294
GEN-2020-006 | 01 - North | 659195 | DICKINS2-BE7 | 115 | 9.5048 | 9.5562 | 0.0514
GEN-2020-006 | 01 - North | 659247 | MEDORA__-UM4 | 230 | 5.5008 | 5.5362 | 0.0354
GEN-2020-006 | 01 - North | 659263 | LITTL_MS-BE7 | 115 | 3.0745 | 3.1311 | 0.0566
GEN-2020-006 | 01 - North | 659265 | LITTL_MS-BE4 | 230 | 3.7062 | 3.8757 | 0.1695
GEN-2020-006 | 01 - North | 659266 | RHAME___-BE4 | 230 | 4.8552 | 5.2591 | 0.4039
GEN-2020-006 | 01 - North | 659267 | RHAME___-BE7 | 115 | 2.0654 | 2.0995 | 0.0341
GEN-2020-006 | 01 - North | 659306 | S.HEART_-RR7 | 115 | 2.3118 | 2.3149 | 0.0031
GEN-2020-006 | 01 - North | 659309 | S.HEART_-RR4 | 230 | 9.7619 | 9.8753 | 0.1134
GEN-2020-006 | 01 - North | 659339 | BOWMAN__-BE4 | 230 | 4.2218 | 4.7929 | 0.5711
GEN-2020-006 | 01 - North | 659340 | BOWMAN__-BE7 | 115 | 3.6645 | 3.865 | 0.2005
GEN-2020-006 | 01 - North | 659341 | NBURR___-GE7 | 115 | 1.8604 | 1.9106 | 0.0502
GEN-2020-006 | 01 - North | 659350 | BISON___-GE7 | 115 | 1.4744 | 1.4849 | 0.0105
GEN-2020-006 | 01 - North | 659351 | BISON___-GE4 | 230 | 2.9128 | 2.9962 | 0.0834
GEN-2020-006 | 01 - North | 659352 | BISON___-GE8 | 69 | 2.1772 | 2.1908 | 0.0136
GEN-2020-006 | 01 - North | 659400 | ND.SUN._-PP4 | 230 | 5.2717 | 5.2826 | 0.0109
GEN-2020-006 | 01 - North | 659442 | 32STREET-RR7 | 115 | 1.9372 | 1.9394 | 0.0022
GEN-2020-006 | 01 - North | 659443 | SKUNKHIL-RR7 | 115 | 1.743 | 1.7448 | 0.0018
GEN-2020-006 | 01 - North | 659448 | DAGLUM__-BE4 | 230 | 6.7276 | 6.8529 | 0.1253
GEN-2020-006 | 01 - North | 659450 | BRADYWND 4 | 230 | 3.6512 | 3.6783 | 0.0271
GEN-2020-006 | 01 - North | 659535 | BEAVRHIL-GW4 | 230 | 4.5694 | 4.5931 | 0.0237
GEN-2020-006 | 01 - North | 659536 | BEAVRHIL-GW7 | 115 | 3.6833 | 3.691 | 0.0077
GEN-2020-006 | 01 - North | 659544 | PRNGHORN-RR7 | 115 | 1.9372 | 1.9394 | 0.0022
GEN-2020-006 | 01 - North | 659550 | LNGBUTTE-RR4 | 230 | 5.6818 | 5.6948 | 0.013
GEN-2020-006 | 01 - North | 659551 | LNGBUTTE-RR7 | 115 | 3.543 | 3.5456 | 0.0026
GEN-2020-006 | 01 - North | 659553 | RAIDER__-RR7 | 115 | 2.3933 | 2.3945 | 0.0012
GEN-2020-006 | 01 - North | 659554 | REDTRAIL-RR7 | 115 | 2.3698 | 2.3709 | 0.0011
GEN-2020-006 | 01 - North | 659555 | RICHRDTN-RR7 | 115 | 2.1928 | 2.1938 | 0.001
GEN-2020-006 | 01 - North | 661004 | BAKER 4 | 230 | 3.4376 | 3.5579 | 0.1203
GEN-2020-006 | 01 - North | 661005 | BAKER 7 | 115 | 3.5975 | 3.6351 | 0.0376
GEN-2020-006 | 01 - North | 661010 | MILESCITYSW7 | 115 | 1.0286 | 1.0296 | 0.001
GEN-2020-006 | 01 - North | 661034 | KEYXLPS14 7 | 115 | 3.2969 | 3.3234 | 0.0265
GEN-2020-006 | 01 - North | 661047 | HETINGR4 | 230 | 3.6374 | 3.8488 | 0.2114
GEN-2020-006 | 01 - North | 661048 | HETINGR7 | 115 | 3.4656 | 3.5243 | 0.0587
GEN-2020-006 | 01 - North | 661050 | GASCOYN7 | 115 | 1.8838 | 1.9011 | 0.0173
GEN-2020-006 | 01 - North | 661070 | N ENGLN7 | 115 | 3.8511 | 3.8744 | 0.0233
GEN-2020-006 | 01 - North | 763043 | GEN-2018-069 | 230 | 4.4961 | 4.5189 | 0.0228
GEN-2020-006 | 01 - North | 764165 | GEN-2020-006 | 230 | 4.2218 | 4.7929 | 0.5711
GEN-2020-014 | 01 - North | 652216 | WATFORD4 | 230 | 6.917 | 6.9658 | 0.0488
GEN-2020-014 | 01 - North | 652400 | WILISTN4 | 230 | 11.8543 | 11.8709 | 0.0166
GEN-2020-014 | 01 - North | 652408 | WATFORD7 | 115 | 8.7333 | 8.8628 | 0.1295
GEN-2020-014 | 01 - North | 655831 | J12_____-MK7 | 115 | 4.0763 | 4.0767 | 0.0004
GEN-2020-014 | 01 - North | 655832 | BLUEBUTE-MK7 | 115 | 8.0395 | 8.0412 | 0.0017
GEN-2020-014 | 01 - North | 655837 | ELMTREE -MK7 | 115 | 3.6731 | 3.6734 | 0.0003
GEN-2020-014 | 01 - North | 655838 | INDIANHL-MK7 | 115 | 4.0889 | 4.0893 | 0.0004
GEN-2020-014 | 01 - North | 655839 | SATHERDM-MK7 | 115 | 2.2611 | 2.2612 | 0.0001
GEN-2020-014 | 01 - North | 655840 | CHRRYCRK-MK7 | 115 | 8.7333 | 8.8628 | 0.1295
GEN-2020-014 | 01 - North | 655841 | ARNEGARD-MK7 | 115 | 6.7418 | 6.9587 | 0.2169
GEN-2020-014 | 01 - North | 655842 | HAYBUTTE-MK7 | 115 | 3.2832 | 3.2834 | 0.0002
GEN-2020-014 | 01 - North | 655843 | TRUEOIL -MK7 | 115 | 1.6358 | 1.6358 | 0
GEN-2020-014 | 01 - North | 655844 | TIMBERCK-MK7 | 115 | 5.281 | 5.2817 | 0.0007
GEN-2020-014 | 01 - North | 655845 | GRDNCRK2-MK7 | 115 | 4.6639 | 4.7004 | 0.0365
GEN-2020-014 | 01 - North | 655846 | F9______-MK7 | 115 | 4.1923 | 4.1927 | 0.0004
GEN-2020-014 | 01 - North | 655847 | SWENSON -MK7 | 115 | 4.3373 | 4.3378 | 0.0005
GEN-2020-014 | 01 - North | 655848 | BERG -MK7 | 115 | 5.7676 | 5.7685 | 0.0009
GEN-2020-014 | 01 - North | 655849 | VEEDER -MK7 | 115 | 9.9109 | 9.9135 | 0.0026
GEN-2020-014 | 01 - North | 655850 | NRTINDHL-MK7 | 115 | 3.4869 | 3.4872 | 0.0003
GEN-2020-014 | 01 - North | 655854 | SANDCREK-MK7 | 115 | 3.539 | 3.5394 | 0.0004
GEN-2020-014 | 01 - North | 655855 | ROOSEVLT-MK7 | 115 | 4.8059 | 4.8446 | 0.0387
GEN-2020-014 | 01 - North | 655856 | STNJOHNY-MK7 | 115 | 6.5589 | 6.56 | 0.0011
GEN-2020-014 | 01 - North | 655857 | MOCCASIN-MK7 | 115 | 2.5965 | 2.5967 | 0.0002
GEN-2020-014 | 01 - North | 655858 | TABLEBUT-MK7 | 115 | 4.3695 | 4.37 | 0.0005
GEN-2020-014 | 01 - North | 655859 | CHARLSON-MK7 | 115 | 3.7513 | 3.7517 | 0.0004
GEN-2020-014 | 01 - North | 655861 | HORSECRK-MK7 | 115 | 2.3269 | 2.3271 | 0.0002
GEN-2020-014 | 01 - North | 655863 | CARTWRIT-MK7 | 115 | 3.1438 | 3.1441 | 0.0003
GEN-2020-014 | 01 - North | 655864 | GRAIL -MK7 | 115 | 5.7815 | 5.7824 | 0.0009
GEN-2020-014 | 01 - North | 655865 | STATION8-MK7 | 115 | 5.9302 | 5.9311 | 0.0009
GEN-2020-014 | 01 - North | 655866 | SNDCRKTP-MK7 | 115 | 4.0843 | 4.0848 | 0.0005
GEN-2020-014 | 01 - North | 655867 | TWNVLYTP-MK7 | 115 | 3.002 | 3.0022 | 0.0002
GEN-2020-014 | 01 - North | 655869 | TWINVLLY-MK7 | 115 | 2.7667 | 2.7669 | 0.0002
GEN-2020-014 | 01 - North | 655870 | TBGARDEN-MK7 | 115 | 2.6656 | 2.6658 | 0.0002
GEN-2020-014 | 01 - North | 655871 | G9______-MK7 | 115 | 3.9406 | 3.941 | 0.0004
GEN-2020-014 | 01 - North | 655873 | BBCOMPTP-MK7 | 115 | 7.0036 | 7.0049 | 0.0013
GEN-2020-014 | 01 - North | 655874 | BBCMPRSS-MK7 | 115 | 6.3925 | 6.3936 | 0.0011
GEN-2020-014 | 01 - North | 655875 | DPLWC___-MK7 | 115 | 7.6396 | 7.7382 | 0.0986
GEN-2020-014 | 01 - North | 655876 | DPLWCTAP-MK7 | 115 | 8.3972 | 8.5167 | 0.1195
GEN-2020-014 | 01 - North | 655877 | LITTLMS4-MK7 | 115 | 5.2688 | 5.3154 | 0.0466
GEN-2020-014 | 01 - North | 655878 | CRESTWD_-MK7 | 115 | 3.9251 | 3.9508 | 0.0257
GEN-2020-014 | 01 - North | 655879 | OASIS___-MK7 | 115 | 4.6998 | 4.7368 | 0.037
GEN-2020-014 | 01 - North | 655880 | SCHAFR_T-MK7 | 115 | 5.8007 | 5.8016 | 0.0009
GEN-2020-014 | 01 - North | 655881 | DAP_____-MK7 | 115 | 13.2387 | 13.2434 | 0.0047
GEN-2020-014 | 01 - North | 655882 | GALAXYTP-MK7 | 115 | 9.9612 | 9.9639 | 0.0027
GEN-2020-014 | 01 - North | 655883 | GALAXY -MK7 | 115 | 7.8351 | 7.8367 | 0.0016
GEN-2020-014 | 01 - North | 655884 | DEMCKSLK-MK7 | 115 | 5.4632 | 5.464 | 0.0008
GEN-2020-014 | 01 - North | 655885 | NRTHFORK-MK7 | 115 | 4.2593 | 4.2598 | 0.0005
GEN-2020-014 | 01 - North | 655886 | KEENE -MK7 | 115 | 5.0773 | 5.078 | 0.0007
GEN-2020-014 | 01 - North | 655888 | BANKS -MK7 | 115 | 3.4646 | 3.4649 | 0.0003
GEN-2020-014 | 01 - North | 655889 | LC_GAS_P-MK7 | 115 | 6.2932 | 6.2942 | 0.001
GEN-2020-014 | 01 - North | 655892 | ALEXANDR-MK7 | 115 | 4.0349 | 4.0353 | 0.0004
GEN-2020-014 | 01 - North | 655895 | GARDN-FB-MK7 | 115 | 4.3012 | 4.3321 | 0.0309
GEN-2020-014 | 01 - North | 655896 | KEENECRN-MK7 | 115 | 3.4658 | 3.4661 | 0.0003
GEN-2020-014 | 01 - North | 655897 | COYOTCHR-MK7 | 115 | 5.3267 | 5.3275 | 0.0008
GEN-2020-014 | 01 - North | 655898 | SCHAFER -MK7 | 115 | 3.1142 | 3.1304 | 0.0162
GEN-2020-014 | 01 - North | 655899 | FNCYBTAP-MK7 | 115 | 6.4342 | 6.4353 | 0.0011
GEN-2020-014 | 01 - North | 659154 | LC_CT4-5-BE7 | 115 | 6.5315 | 6.8563 | 0.3248
GEN-2020-014 | 01 - North | 659183 | CHARL_CK-BE3 | 345 | 11.2664 | 11.2805 | 0.0141
GEN-2020-014 | 01 - North | 659302 | CHARL_CK-BE4 | 230 | 12.01 | 12.0302 | 0.0202
GEN-2020-014 | 01 - North | 659333 | JUDSON__-BE3 | 345 | 8.9813 | 8.9902 | 0.0089
GEN-2020-014 | 01 - North | 659346 | LC_SWY.S-BE7 | 115 | 6.5268 | 6.8568 | 0.33
GEN-2020-014 | 01 - North | 659348 | LC_CT1-3-BE7 | 115 | 12.4194 | 12.4221 | 0.0027
GEN-2020-014 | 01 - North | 659349 | LC_SWY.N-BE7 | 115 | 12.4195 | 12.4222 | 0.0027
GEN-2020-014 | 01 - North | 659387 | KUMMERDG-BE3 | 345 | 7.7069 | 7.7117 | 0.0048
GEN-2020-014 | 01 - North | 659388 | KUMMERDG-MK7 | 115 | 14.7026 | 14.7085 | 0.0059
GEN-2020-014 | 01 - North | 659390 | PATENTGT-BE3 | 345 | 9.4171 | 9.4251 | 0.008
GEN-2020-014 | 01 - North | 659391 | PATENTGT-MK7 | 115 | 18.5825 | 18.5913 | 0.0088
GEN-2020-014 | 01 - North | 659466 | PG.KU17A-BE7 | 115 | 18.4825 | 18.4913 | 0.0088
GEN-2020-014 | 01 - North | 659467 | PG.KU19A-BE7 | 115 | 18.4944 | 18.5032 | 0.0088
GEN-2020-014 | 01 - North | 659584 | BEPCPRXCC3 7 | 115 | 14.4473 | 14.453 | 0.0057
GEN-2020-014 | 01 - North | 661003 | WATFRDSOUTH4 | 230 | 6.8437 | 6.8914 | 0.0477
GEN-2020-014 | 01 - North | 764180 | GEN-2020-014 | 115 | 6.5268 | 6.8568 | 0.33
GEN-2020-014 | 01 - North | 764225 | GEN-2020-091 | 345 | 9.257 | 9.2647 | 0.0077
GEN-2020-021 | 01 - North | 67030 | MPC04000MPT | 230 | 11.1885 | 11.1888 | 0.0003
GEN-2020-021 | 01 - North | 587030 | GEN-2016-004 | 230 | 7.6707 | 7.6753 | 0.0046
GEN-2020-021 | 01 - North | 588210 | GEN-2016-130 | 345 | 13.022 | 13.0566 | 0.0346
GEN-2020-021 | 01 - North | 608597 | SQBP1DC4 | 230 | 23.9804 | 23.9817 | 0.0013
GEN-2020-021 | 01 - North | 608599 | SQBP2DC4 | 230 | 23.9804 | 23.9817 | 0.0013
GEN-2020-021 | 01 - North | 608600 | BISONMP4 | 230 | 8.1687 | 8.1688 | 0.0001
GEN-2020-021 | 01 - North | 608602 | SQBEAST4 | 230 | 23.9804 | 23.9817 | 0.0013
GEN-2020-021 | 01 - North | 608603 | TRICNTY4 | 230 | 5.9024 | 5.9025 | 0.0001
GEN-2020-021 | 01 - North | 615600 | GRE-COAL CR4 | 230 | 19.2946 | 19.2956 | 0.001
GEN-2020-021 | 01 - North | 615601 | GRE-COAL FM8 | 69 | 9.0487 | 9.0487 | 0
GEN-2020-021 | 01 - North | 615604 | GRE-COALFB14 | 230 | 19.2946 | 19.2956 | 0.001
GEN-2020-021 | 01 - North | 615605 | GRE-COALFB24 | 230 | 19.2946 | 19.2956 | 0.001
GEN-2020-021 | 01 - North | 615606 | GRE-COALFB34 | 230 | 19.2946 | 19.2956 | 0.001
GEN-2020-021 | 01 - North | 615900 | GRE-COAL TP4 | 230 | 16.233 | 16.2339 | 0.0009
GEN-2020-021 | 01 - North | 615901 | GRE-STANTON4 | 230 | 18.1904 | 18.1921 | 0.0017
GEN-2020-021 | 01 - North | 652257 | DEVAUL 8 | 69 | 1.1042 | 1.1043 | 0.0001
GEN-2020-021 | 01 - North | 652276 | FTTHOMP8 | 69 | 3.774 | 3.7751 | 0.0011
GEN-2020-021 | 01 - North | 652424 | BELFELD3 | 345 | 7.0139 | 7.0151 | 0.0012
GEN-2020-021 | 01 - North | 652426 | BISMARK4 | 230 | 14.992 | 14.9952 | 0.0032
GEN-2020-021 | 01 - North | 652441 | GARRISN4 | 230 | 12.2325 | 12.2357 | 0.0032
GEN-2020-021 | 01 - North | 652442 | GARRISN7 | 115 | 16.0631 | 16.0648 | 0.0017
GEN-2020-021 | 01 - North | 652444 | JAMESTN4 | 230 | 8.6249 | 8.6253 | 0.0004
GEN-2020-021 | 01 - North | 652456 | WASHBRN4 | 230 | 10.7872 | 10.7944 | 0.0072
GEN-2020-021 | 01 - North | 652466 | HILKEN 4 | 230 | 8.2843 | 8.2853 | 0.001
GEN-2020-021 | 01 - North | 652506 | FTTHOMP3 | 345 | 9.2007 | 9.3254 | 0.1247
GEN-2020-021 | 01 - North | 652507 | FTTHOMP4 | 230 | 19.436 | 19.5571 | 0.1211
GEN-2020-021 | 01 - North | 652540 | BIGBND14 | 230 | 11.8754 | 11.9151 | 0.0397
GEN-2020-021 | 01 - North | 652541 | BIGBND24 | 230 | 11.7967 | 11.8358 | 0.0391
GEN-2020-021 | 01 - North | 652806 | FTTHOM1-LNX3 | 345 | 9.1339 | 9.259 | 0.1251
GEN-2020-021 | 01 - North | 652807 | FTTHOM2-LNX3 | 345 | 9.2007 | 9.3254 | 0.1247
GEN-2020-021 | 01 - North | 655153 | MOS-AMES-ER8 | 69 | 3.7011 | 3.7022 | 0.0011
GEN-2020-021 | 01 - North | 655158 | MOS-HYDE-ER8 | 69 | 2.2116 | 2.2119 | 0.0003
GEN-2020-021 | 01 - North | 655240 | HGHMORE-ER8 | 69 | 1.606 | 1.6061 | 0.0001
GEN-2020-021 | 01 - North | 655328 | BIGBEND-ER8 | 69 | 2.9032 | 2.9039 | 0.0007
GEN-2020-021 | 01 - North | 655329 | GANNVALL-ER8 | 69 | 0.8721 | 0.8721 | 0
GEN-2020-021 | 01 - North | 655352 | AMES-ER8 | 69 | 1.3208 | 1.3209 | 0.0001
GEN-2020-021 | 01 - North | 655384 | NWPS8645-ER8 | 69 | 1.6263 | 1.6264 | 0.0001
GEN-2020-021 | 01 - North | 655731 | LARK -MG8 | 69 | 0.9758 | 0.9759 | 0.0001
GEN-2020-021 | 01 - North | 655732 | FLASHER -MG8 | 69 | 0.9029 | 0.9029 | 0
GEN-2020-021 | 01 - North | 655740 | CANNON -MG8 | 69 | 0.9097 | 0.9097 | 0
GEN-2020-021 | 01 - North | 655741 | CEDAR -MG8 | 69 | 0.6895 | 0.6895 | 0
GEN-2020-021 | 01 - North | 655742 | GRANT -MG8 | 69 | 0.6177 | 0.6177 | 0
GEN-2020-021 | 01 - North | 655744 | DEVALTP -MG8 | 69 | 1.1105 | 1.1105 | 0
GEN-2020-021 | 01 - North | 655746 | DEVAUL -MG8 | 69 | 1.1164 | 1.1164 | 0
GEN-2020-021 | 01 - North | 655747 | DEVAUL -MG7 | 115 | 1.1075 | 1.1076 | 0.0001
GEN-2020-021 | 01 - North | 655748 | NEWSALEM-MG7 | 115 | 1.5142 | 1.5143 | 0.0001
GEN-2020-021 | 01 - North | 655749 | MANSWTCH-MG7 | 115 | 1.0234 | 1.0235 | 0.0001
GEN-2020-021 | 01 - North | 655750 | ROUGHRDR-MG7 | 115 | 0.9908 | 0.9909 | 0.0001
GEN-2020-021 | 01 - North | 655751 | NRWSTMDN-MG7 | 115 | 0.9913 | 0.9913 | 0
GEN-2020-021 | 01 - North | 655752 | NWMDNTAP-MG7 | 115 | 1.5519 | 1.552 | 0.0001
GEN-2020-021 | 01 - North | 655830 | MOUNTAIN-MK7 | 115 | 4.2011 | 4.2013 | 0.0002
GEN-2020-021 | 01 - North | 655831 | J12_____-MK7 | 115 | 4.0766 | 4.0767 | 0.0001
GEN-2020-021 | 01 - North | 655832 | BLUEBUTE-MK7 | 115 | 8.0405 | 8.0412 | 0.0007
GEN-2020-021 | 01 - North | 655833 | GRSYBTTP-MK7 | 115 | 14.2598 | 14.2619 | 0.0021
GEN-2020-021 | 01 - North | 655834 | GRASSYBT-MK7 | 115 | 6.9792 | 6.9797 | 0.0005
GEN-2020-021 | 01 - North | 655835 | LITTLKNF-MK7 | 115 | 3.134 | 3.1342 | 0.0002
GEN-2020-021 | 01 - North | 655836 | OAKDALE -MK7 | 115 | 5.5741 | 5.5745 | 0.0004
GEN-2020-021 | 01 - North | 655837 | ELMTREE -MK7 | 115 | 3.6733 | 3.6734 | 0.0001
GEN-2020-021 | 01 - North | 655838 | INDIANHL-MK7 | 115 | 4.0892 | 4.0893 | 0.0001
GEN-2020-021 | 01 - North | 655842 | HAYBUTTE-MK7 | 115 | 3.2834 | 3.2834 | 0
GEN-2020-021 | 01 - North | 655844 | TIMBERCK-MK7 | 115 | 5.2815 | 5.2817 | 0.0002
GEN-2020-021 | 01 - North | 655846 | F9______-MK7 | 115 | 4.1926 | 4.1927 | 0.0001
GEN-2020-021 | 01 - North | 655847 | SWENSON -MK7 | 115 | 4.3376 | 4.3378 | 0.0002
GEN-2020-021 | 01 - North | 655848 | BERG -MK7 | 115 | 5.7681 | 5.7685 | 0.0004
GEN-2020-021 | 01 - North | 655849 | VEEDER -MK7 | 115 | 9.9124 | 9.9135 | 0.0011
GEN-2020-021 | 01 - North | 655850 | NRTINDHL-MK7 | 115 | 3.4871 | 3.4872 | 0.0001
GEN-2020-021 | 01 - North | 655851 | BIGGULCH-MK7 | 115 | 2.9236 | 2.9237 | 0.0001
GEN-2020-021 | 01 - North | 655852 | L11_____-MK7 | 115 | 3.5798 | 3.5799 | 0.0001
GEN-2020-021 | 01 - North | 655853 | BEARCREK-MK7 | 115 | 8.4387 | 8.4397 | 0.001
GEN-2020-021 | 01 - North | 655854 | SANDCREK-MK7 | 115 | 3.5392 | 3.5394 | 0.0002
GEN-2020-021 | 01 - North | 655856 | STNJOHNY-MK7 | 115 | 6.5597 | 6.56 | 0.0003
GEN-2020-021 | 01 - North | 655857 | MOCCASIN-MK7 | 115 | 2.5966 | 2.5967 | 0.0001
GEN-2020-021 | 01 - North | 655858 | TABLEBUT-MK7 | 115 | 4.3698 | 4.37 | 0.0002
GEN-2020-021 | 01 - North | 655859 | CHARLSON-MK7 | 115 | 3.7516 | 3.7517 | 0.0001
GEN-2020-021 | 01 - North | 655861 | HORSECRK-MK7 | 115 | 2.327 | 2.3271 | 0.0001
GEN-2020-021 | 01 - North | 655863 | CARTWRIT-MK7 | 115 | 3.144 | 3.1441 | 0.0001
GEN-2020-021 | 01 - North | 655864 | GRAIL -MK7 | 115 | 5.782 | 5.7824 | 0.0004
GEN-2020-021 | 01 - North | 655865 | STATION8-MK7 | 115 | 5.9307 | 5.9311 | 0.0004
GEN-2020-021 | 01 - North | 655866 | SNDCRKTP-MK7 | 115 | 4.0846 | 4.0848 | 0.0002
GEN-2020-021 | 01 - North | 655867 | TWNVLYTP-MK7 | 115 | 3.0021 | 3.0022 | 0.0001
GEN-2020-021 | 01 - North | 655869 | TWINVLLY-MK7 | 115 | 2.7668 | 2.7669 | 0.0001
GEN-2020-021 | 01 - North | 655870 | TBGARDEN-MK7 | 115 | 2.6658 | 2.6658 | 0
GEN-2020-021 | 01 - North | 655871 | G9______-MK7 | 115 | 3.9409 | 3.941 | 0.0001
GEN-2020-021 | 01 - North | 655873 | BBCOMPTP-MK7 | 115 | 7.0043 | 7.0049 | 0.0006
GEN-2020-021 | 01 - North | 655874 | BBCMPRSS-MK7 | 115 | 6.3931 | 6.3936 | 0.0005
GEN-2020-021 | 01 - North | 655880 | SCHAFR_T-MK7 | 115 | 5.8012 | 5.8016 | 0.0004
GEN-2020-021 | 01 - North | 655881 | DAP_____-MK7 | 115 | 13.2414 | 13.2434 | 0.002
GEN-2020-021 | 01 - North | 655882 | GALAXYTP-MK7 | 115 | 9.9628 | 9.9639 | 0.0011
GEN-2020-021 | 01 - North | 655883 | GALAXY -MK7 | 115 | 7.836 | 7.8367 | 0.0007
GEN-2020-021 | 01 - North | 655884 | DEMCKSLK-MK7 | 115 | 5.4637 | 5.464 | 0.0003
GEN-2020-021 | 01 - North | 655885 | NRTHFORK-MK7 | 115 | 4.2596 | 4.2598 | 0.0002
GEN-2020-021 | 01 - North | 655886 | KEENE -MK7 | 115 | 5.0777 | 5.078 | 0.0003
GEN-2020-021 | 01 - North | 655888 | BANKS -MK7 | 115 | 3.4648 | 3.4649 | 0.0001
GEN-2020-021 | 01 - North | 655889 | LC_GAS_P-MK7 | 115 | 6.2939 | 6.2942 | 0.0003
GEN-2020-021 | 01 - North | 655892 | ALEXANDR-MK7 | 115 | 4.0352 | 4.0353 | 0.0001
GEN-2020-021 | 01 - North | 655893 | DUNNCNTR-MK7 | 115 | 6.298 | 6.2985 | 0.0005
GEN-2020-021 | 01 - North | 655894 | HALLIDAY-MK7 | 115 | 3.5606 | 3.5608 | 0.0002
GEN-2020-021 | 01 - North | 655896 | KEENECRN-MK7 | 115 | 3.4659 | 3.4661 | 0.0002
GEN-2020-021 | 01 - North | 655897 | COYOTCHR-MK7 | 115 | 5.3272 | 5.3275 | 0.0003
GEN-2020-021 | 01 - North | 655899 | FNCYBTAP-MK7 | 115 | 6.4348 | 6.4353 | 0.0005
GEN-2020-021 | 01 - North | 655905 | RBNSNLAK-MW7 | 115 | 10.5967 | 10.598 | 0.0013
GEN-2020-021 | 01 - North | 655906 | FINSTAD -MW7 | 115 | 20.88 | 20.8863 | 0.0063
GEN-2020-021 | 01 - North | 655919 | OSBORN -MW7 | 115 | 12.2884 | 12.2902 | 0.0018
GEN-2020-021 | 01 - North | 655920 | VANHOOK -MW7 | 115 | 13.7177 | 13.7202 | 0.0025
GEN-2020-021 | 01 - North | 657756 | SQBUTTE4 | 230 | 23.9804 | 23.9817 | 0.0013
GEN-2020-021 | 01 - North | 657848 | YNG2 4 | 230 | 19.4201 | 19.4208 | 0.0007
GEN-2020-021 | 01 - North | 659060 | FINSTAD345 | 345 | 7.4843 | 7.4869 | 0.0026
GEN-2020-021 | 01 - North | 659101 | ANTELOPE-BE3 | 345 | 20.5455 | 20.5789 | 0.0334
GEN-2020-021 | 01 - North | 659105 | LELAND_O-BE3 | 345 | 20.1322 | 20.2168 | 0.0846
GEN-2020-021 | 01 - North | 659106 | LELAND_O-BE4 | 230 | 25.8782 | 25.938 | 0.0598
GEN-2020-021 | 01 - North | 659108 | LOGAN___-BE4 | 230 | 6.5526 | 6.5537 | 0.0011
GEN-2020-021 | 01 - North | 659109 | BASIN___-BE7 | 115 | 5.4303 | 5.4316 | 0.0013
GEN-2020-021 | 01 - North | 659130 | CHAPELLE-BE3 | 345 | 6.4641 | 6.6244 | 0.1603
GEN-2020-021 | 01 - North | 659143 | BLAISDEL-BE4 | 230 | 6.3096 | 6.3103 | 0.0007
GEN-2020-021 | 01 - North | 659155 | LOGAN___-BE7 | 115 | 11.1856 | 11.1866 | 0.001
GEN-2020-021 | 01 - North | 659182 | CHARL_CK-BE7 | 115 | 14.385 | 14.3871 | 0.0021
GEN-2020-021 | 01 - North | 659183 | CHARL_CK-BE3 | 345 | 11.276 | 11.2805 | 0.0045
GEN-2020-021 | 01 - North | 659185 | FOUREYES-RR7 | 115 | 3.7518 | 3.752 | 0.0002
GEN-2020-021 | 01 - North | 659199 | BASIN___-BE4 | 230 | 23.4235 | 23.4722 | 0.0487
GEN-2020-021 | 01 - North | 659212 | DGC_____-BE3 | 345 | 19.4076 | 19.4374 | 0.0298
GEN-2020-021 | 01 - North | 659218 | COTEAU__-RR3 | 345 | 20.5455 | 20.5789 | 0.0334
GEN-2020-021 | 01 - North | 659222 | COTEAU_1-RR8 | 69 | 9.8837 | 9.8853 | 0.0016
GEN-2020-021 | 01 - North | 659233 | DGC_____-BE4 | 230 | 7.7131 | 7.7162 | 0.0031
GEN-2020-021 | 01 - North | 659236 | DGC UREA-BE8 | 69 | 7.4096 | 7.4104 | 0.0008
GEN-2020-021 | 01 - North | 659284 | ECKLUND_-PP4 | 230 | 7.0874 | 7.0881 | 0.0007
GEN-2020-021 | 01 - North | 659302 | CHARL_CK-BE4 | 230 | 12.027 | 12.0302 | 0.0032
GEN-2020-021 | 01 - North | 659336 | TANDE___-BE3 | 345 | 9.201 | 9.203 | 0.002
GEN-2020-021 | 01 - North | 659337 | TANDE___-BE4 | 230 | 13.3848 | 13.3871 | 0.0023
GEN-2020-021 | 01 - North | 659348 | LC_CT1-3-BE7 | 115 | 12.4213 | 12.4221 | 0.0008
GEN-2020-021 | 01 - North | 659349 | LC_SWY.N-BE7 | 115 | 12.4214 | 12.4222 | 0.0008
GEN-2020-021 | 01 - North | 659365 | BALDWIN_-PP4 | 230 | 7.0874 | 7.0881 | 0.0007
GEN-2020-021 | 01 - North | 659384 | ROUNDUP_-BE3 | 345 | 10.1757 | 10.1801 | 0.0044
GEN-2020-021 | 01 - North | 659385 | ROUNDUP_-MK7 | 115 | 12.1507 | 12.1527 | 0.002
GEN-2020-021 | 01 - North | 659387 | KUMMERDG-BE3 | 345 | 7.7097 | 7.7117 | 0.002
GEN-2020-021 | 01 - North | 659388 | KUMMERDG-MK7 | 115 | 14.706 | 14.7085 | 0.0025
GEN-2020-021 | 01 - North | 659390 | PATENTGT-BE3 | 345 | 9.4227 | 9.4251 | 0.0024
GEN-2020-021 | 01 - North | 659391 | PATENTGT-MK7 | 115 | 18.5887 | 18.5913 | 0.0026
GEN-2020-021 | 01 - North | 659404 | BURKE___-PP3 | 345 | 4.9423 | 4.9429 | 0.0006
GEN-2020-021 | 01 - North | 659420 | AV.LS-BD-BE3 | 345 | 20.5455 | 20.5789 | 0.0334
GEN-2020-021 | 01 - North | 659421 | BD.LS-AV-BE3 | 345 | 4.8097 | 4.8126 | 0.0029
GEN-2020-021 | 01 - North | 659422 | LO.LS-GR-BE3 | 345 | 20.1322 | 20.2168 | 0.0846
GEN-2020-021 | 01 - North | 659423 | GR.LS-LO-BE3 | 345 | 6.4727 | 6.4736 | 0.0009
GEN-2020-021 | 01 - North | 659424 | LO.LS-FT-BE3 | 345 | 20.1322 | 20.2168 | 0.0846
GEN-2020-021 | 01 - North | 659427 | TN.LS-JD-BE3 | 345 | 9.201 | 9.203 | 0.002
GEN-2020-021 | 01 - North | 659428 | CC.LS-LO-BE3 | 345 | 6.4332 | 6.5939 | 0.1607
GEN-2020-021 | 01 - North | 659433 | TRIPLEH__UA3 | 345 | 6.4016 | 6.5585 | 0.1569
GEN-2020-021 | 01 - North | 659466 | PG.KU17A-BE7 | 115 | 18.4887 | 18.4913 | 0.0026
GEN-2020-021 | 01 - North | 659467 | PG.KU19A-BE7 | 115 | 18.5007 | 18.5032 | 0.0025
GEN-2020-021 | 01 - North | 659479 | TRADEWND-UA3 | 345 | 6.5158 | 6.5168 | 0.001
GEN-2020-021 | 01 - North | 659576 | BEPCPRXCC1 3 | 345 | 19.6639 | 19.6936 | 0.0297
GEN-2020-021 | 01 - North | 659584 | BEPCPRXCC3 7 | 115 | 14.4506 | 14.453 | 0.0024
GEN-2020-021 | 01 - North | 760998 | GEN-2017-214 | 230 | 3.241 | 3.2412 | 0.0002
GEN-2020-021 | 01 - North | 762537 | GEN-2018-008 | 345 | 4.4381 | 4.4394 | 0.0013
GEN-2020-021 | 01 - North | 762544 | G18-008-TAP | 345 | 4.4425 | 4.4438 | 0.0013
GEN-2020-021 | 01 - North | 763703 | GEN-2019-037 | 345 | 12.1723 | 12.2025 | 0.0302
GEN-2020-021 | 01 - North | 764210 | GEN-2020-021 | 345 | 3.2696 | 3.6537 | 0.3841
GEN-2020-021 | 01 - North | 764220 | G20-021-TAP | 345 | 3.9076 | 4.2849 | 0.3773
GEN-2020-021 | 01 - North | 764225 | GEN-2020-091 | 345 | 9.2624 | 9.2647 | 0.0023
GEN-2020-083 | 01 - North | 588870 | GEN-2017-048 | 230 | 10.2038 | 10.2111 | 0.0073
GEN-2020-083 | 01 - North | 652200 | GLENDIVE7 | 115 | 7.3101 | 7.3251 | 0.015
GEN-2020-083 | 01 - North | 652212 | GLENDIVEP2T7 | 115 | 4.4097 | 4.4151 | 0.0054
GEN-2020-083 | 01 - North | 652213 | FALLON 8 | 69 | 1.0872 | 1.0874 | 0.0002
GEN-2020-083 | 01 - North | 652216 | WATFORD4 | 230 | 6.9591 | 6.9658 | 0.0067
GEN-2020-083 | 01 - North | 652391 | WILLISTON27 | 115 | 19.5413 | 19.6923 | 0.151
GEN-2020-083 | 01 - North | 652400 | WILISTN4 | 230 | 11.8322 | 11.8709 | 0.0387
GEN-2020-083 | 01 - North | 652401 | CIRCLE 7 | 115 | 2.2099 | 2.2108 | 0.0009
GEN-2020-083 | 01 - North | 652403 | DAWSONC4 | 230 | 4.5466 | 4.5542 | 0.0076
GEN-2020-083 | 01 - North | 652404 | DAWSONC7 | 115 | 8.124 | 8.145 | 0.021
GEN-2020-083 | 01 - North | 652405 | FTPECK 4 | 230 | 2.1914 | 2.1924 | 0.001
GEN-2020-083 | 01 - North | 652407 | FALLON 7 | 115 | 3.2438 | 3.2462 | 0.0024
GEN-2020-083 | 01 - North | 652408 | WATFORD7 | 115 | 8.8587 | 8.8628 | 0.0041
GEN-2020-083 | 01 - North | 652409 | WOLFPT 7 | 115 | 2.9996 | 3.0009 | 0.0013
GEN-2020-083 | 01 - North | 652411 | MI CTYE4 | 230 | 2.9361 | 2.9381 | 0.002
GEN-2020-083 | 01 - North | 652421 | WILISTN7 | 115 | 19.53 | 19.682 | 0.152
GEN-2020-083 | 01 - North | 652616 | MINGUSVILLE4 | 230 | 4.5888 | 4.5931 | 0.0043
GEN-2020-083 | 01 - North | 652651 | FAIRVIEW 7 | 115 | 5.0728 | 5.583 | 0.5102
GEN-2020-083 | 01 - North | 655778 | SNAKEBTT-SH7 | 115 | 5.5948 | 5.599 | 0.0042
GEN-2020-083 | 01 - North | 655779 | REDBANK -SH7 | 115 | 3.7836 | 3.7855 | 0.0019
GEN-2020-083 | 01 - North | 655790 | HELMUT -LY7 | 115 | 5.7679 | 6.0428 | 0.2749
GEN-2020-083 | 01 - North | 655791 | SPRINGLK-LY7 | 115 | 1.9908 | 2.0647 | 0.0739
GEN-2020-083 | 01 - North | 655792 | NOHLEY -LY7 | 115 | 3.5887 | 3.8346 | 0.2459
GEN-2020-083 | 01 - North | 655793 | MARLEY -LY7 | 115 | 6.0937 | 6.1082 | 0.0145
GEN-2020-083 | 01 - North | 655838 | INDIANHL-MK7 | 115 | 4.0885 | 4.0893 | 0.0008
GEN-2020-083 | 01 - North | 655839 | SATHERDM-MK7 | 115 | 2.2416 | 2.2612 | 0.0196
GEN-2020-083 | 01 - North | 655840 | CHRRYCRK-MK7 | 115 | 8.8587 | 8.8628 | 0.0041
GEN-2020-083 | 01 - North | 655841 | ARNEGARD-MK7 | 115 | 6.9573 | 6.9587 | 0.0014
GEN-2020-083 | 01 - North | 655842 | HAYBUTTE-MK7 | 115 | 3.2829 | 3.2834 | 0.0005
GEN-2020-083 | 01 - North | 655843 | TRUEOIL -MK7 | 115 | 1.6256 | 1.6358 | 0.0102
GEN-2020-083 | 01 - North | 655844 | TIMBERCK-MK7 | 115 | 5.2804 | 5.2817 | 0.0013
GEN-2020-083 | 01 - North | 655845 | GRDNCRK2-MK7 | 115 | 4.6992 | 4.7004 | 0.0012
GEN-2020-083 | 01 - North | 655846 | F9______-MK7 | 115 | 4.1919 | 4.1927 | 0.0008
GEN-2020-083 | 01 - North | 655850 | NRTINDHL-MK7 | 115 | 3.4866 | 3.4872 | 0.0006
GEN-2020-083 | 01 - North | 655855 | ROOSEVLT-MK7 | 115 | 4.8434 | 4.8446 | 0.0012
GEN-2020-083 | 01 - North | 655856 | STNJOHNY-MK7 | 115 | 6.5579 | 6.56 | 0.0021
GEN-2020-083 | 01 - North | 655860 | SKAAR___-MK7 | 115 | 3.4346 | 3.4807 | 0.0461
GEN-2020-083 | 01 - North | 655861 | HORSECRK-MK7 | 115 | 2.3268 | 2.3271 | 0.0003
GEN-2020-083 | 01 - North | 655863 | CARTWRIT-MK7 | 115 | 3.1436 | 3.1441 | 0.0005
GEN-2020-083 | 01 - North | 655867 | TWNVLYTP-MK7 | 115 | 3.0018 | 3.0022 | 0.0004
GEN-2020-083 | 01 - North | 655869 | TWINVLLY-MK7 | 115 | 2.7665 | 2.7669 | 0.0004
GEN-2020-083 | 01 - North | 655870 | TBGARDEN-MK7 | 115 | 2.6655 | 2.6658 | 0.0003
GEN-2020-083 | 01 - North | 655871 | G9______-MK7 | 115 | 3.9403 | 3.941 | 0.0007
GEN-2020-083 | 01 - North | 655875 | DPLWC___-MK7 | 115 | 7.7351 | 7.7382 | 0.0031
GEN-2020-083 | 01 - North | 655876 | DPLWCTAP-MK7 | 115 | 8.513 | 8.5167 | 0.0037
GEN-2020-083 | 01 - North | 655877 | LITTLMS4-MK7 | 115 | 5.314 | 5.3154 | 0.0014
GEN-2020-083 | 01 - North | 655878 | CRESTWD_-MK7 | 115 | 3.95 | 3.9508 | 0.0008
GEN-2020-083 | 01 - North | 655879 | OASIS___-MK7 | 115 | 4.7356 | 4.7368 | 0.0012
GEN-2020-083 | 01 - North | 655888 | BANKS -MK7 | 115 | 3.4643 | 3.4649 | 0.0006
GEN-2020-083 | 01 - North | 655889 | LC_GAS_P-MK7 | 115 | 6.2923 | 6.2942 | 0.0019
GEN-2020-083 | 01 - North | 655892 | ALEXANDR-MK7 | 115 | 4.0346 | 4.0353 | 0.0007
GEN-2020-083 | 01 - North | 655895 | GARDN-FB-MK7 | 115 | 4.3312 | 4.3321 | 0.0009
GEN-2020-083 | 01 - North | 655897 | COYOTCHR-MK7 | 115 | 5.3262 | 5.3275 | 0.0013
GEN-2020-083 | 01 - North | 655898 | SCHAFER -MK7 | 115 | 3.1299 | 3.1304 | 0.0005
GEN-2020-083 | 01 - North | 655915 | BARRBUTE-MW7 | 115 | 5.3671 | 5.371 | 0.0039
GEN-2020-083 | 01 - North | 655924 | STATELIN-MW7 | 115 | 15.1151 | 15.1473 | 0.0322
GEN-2020-083 | 01 - North | 655925 | JUDSON -MW7 | 115 | 15.2902 | 15.3731 | 0.0829
GEN-2020-083 | 01 - North | 655926 | SW.WLSTN-MW7 | 115 | 8.681 | 8.7076 | 0.0266
GEN-2020-083 | 01 - North | 655931 | BLKTLTAP-MW7 | 115 | 10.2749 | 10.2886 | 0.0137
GEN-2020-083 | 01 - North | 655933 | N.MISRDG-MW7 | 115 | 15.1552 | 15.1946 | 0.0394
GEN-2020-083 | 01 - North | 655934 | N.WLST_T-MW7 | 115 | 13.9213 | 13.9588 | 0.0375
GEN-2020-083 | 01 - North | 655935 | NW.WLSTN-MW7 | 115 | 12.4058 | 12.4426 | 0.0368
GEN-2020-083 | 01 - North | 655936 | N.WILSTN-MW7 | 115 | 13.6085 | 13.6438 | 0.0353
GEN-2020-083 | 01 - North | 655940 | MONT -MW7 | 115 | 15.7003 | 15.7495 | 0.0492
GEN-2020-083 | 01 - North | 655941 | STRNDAHL-MW7 | 115 | 10.1966 | 10.2108 | 0.0142
GEN-2020-083 | 01 - North | 655945 | WHEELS_T-MW7 | 115 | 9.2989 | 9.3072 | 0.0083
GEN-2020-083 | 01 - North | 655957 | EASTFORK-MW7 | 115 | 17.3181 | 17.3586 | 0.0405
GEN-2020-083 | 01 - North | 655966 | OLIVER -MW7 | 115 | 7.0337 | 7.0388 | 0.0051
GEN-2020-083 | 01 - North | 659112 | CULBRTSN-UM7 | 115 | 4.4734 | 4.4757 | 0.0023
GEN-2020-083 | 01 - North | 659138 | NESET___-BE4 | 230 | 13.5793 | 13.5931 | 0.0138
GEN-2020-083 | 01 - North | 659143 | BLAISDEL-BE4 | 230 | 6.3087 | 6.3103 | 0.0016
GEN-2020-083 | 01 - North | 659151 | RICHLAND-BE7 | 115 | 5.8091 | 6.0881 | 0.279
GEN-2020-083 | 01 - North | 659154 | LC_CT4-5-BE7 | 115 | 6.8554 | 6.8563 | 0.0009
GEN-2020-083 | 01 - North | 659180 | KOCH_OIL-BE7 | 115 | 3.7087 | 3.7793 | 0.0706
GEN-2020-083 | 01 - North | 659181 | BICNTNIL-BE7 | 115 | 3.4392 | 3.4685 | 0.0293
GEN-2020-083 | 01 - North | 659183 | CHARL_CK-BE3 | 345 | 11.2621 | 11.2805 | 0.0184
GEN-2020-083 | 01 - North | 659186 | E.SIDNEY-LY7 | 115 | 4.3089 | 4.4298 | 0.1209
GEN-2020-083 | 01 - North | 659191 | SQUAWGAP-BE7 | 115 | 3.4372 | 3.4833 | 0.0461
GEN-2020-083 | 01 - North | 659259 | HEADRESS-CM7 | 115 | 2.9932 | 2.9945 | 0.0013
GEN-2020-083 | 01 - North | 659262 | CULBSN.E-BE7 | 115 | 5.8167 | 5.8206 | 0.0039
GEN-2020-083 | 01 - North | 659269 | CULB_GEN-BE7 | 115 | 5.6974 | 5.7005 | 0.0031
GEN-2020-083 | 01 - North | 659302 | CHARL_CK-BE4 | 230 | 12.0154 | 12.0302 | 0.0148
GEN-2020-083 | 01 - North | 659333 | JUDSON__-BE3 | 345 | 8.9679 | 8.9902 | 0.0223
GEN-2020-083 | 01 - North | 659334 | JUDSON__-BE4 | 230 | 11.7617 | 11.7972 | 0.0355
GEN-2020-083 | 01 - North | 659346 | LC_SWY.S-BE7 | 115 | 6.8559 | 6.8568 | 0.0009
GEN-2020-083 | 01 - North | 659347 | PIONEER1-BE7 | 115 | 15.1151 | 15.1473 | 0.0322
GEN-2020-083 | 01 - North | 659348 | LC_CT1-3-BE7 | 115 | 12.417 | 12.4221 | 0.0051
GEN-2020-083 | 01 - North | 659349 | LC_SWY.N-BE7 | 115 | 12.4171 | 12.4222 | 0.0051
GEN-2020-083 | 01 - North | 659362 | WHEELOCK-BE4 | 230 | 8.0371 | 8.0475 | 0.0104
GEN-2020-083 | 01 - North | 659363 | WHEELOCK-BE7 | 115 | 9.5659 | 9.5747 | 0.0088
GEN-2020-083 | 01 - North | 659390 | PATENTGT-BE3 | 345 | 9.4101 | 9.4251 | 0.015
GEN-2020-083 | 01 - North | 659391 | PATENTGT-MK7 | 115 | 18.5748 | 18.5913 | 0.0165
GEN-2020-083 | 01 - North | 659430 | PIONEER2-BE7 | 115 | 14.3522 | 14.3802 | 0.028
GEN-2020-083 | 01 - North | 659466 | PG.KU17A-BE7 | 115 | 18.4748 | 18.4913 | 0.0165
GEN-2020-083 | 01 - North | 659467 | PG.KU19A-BE7 | 115 | 18.4867 | 18.5032 | 0.0165
GEN-2020-083 | 01 - North | 659535 | BEAVRHIL-GW4 | 230 | 4.5888 | 4.5931 | 0.0043
GEN-2020-083 | 01 - North | 659536 | BEAVRHIL-GW7 | 115 | 3.6896 | 3.691 | 0.0014
GEN-2020-083 | 01 - North | 659542 | REDWATER-MC7 | 115 | 2.2099 | 2.2108 | 0.0009
GEN-2020-083 | 01 - North | 659600 | EFORK_-BE334 | 345 | 8.232 | 8.2497 | 0.0177
GEN-2020-083 | 01 - North | 661003 | WATFRDSOUTH4 | 230 | 6.8849 | 6.8914 | 0.0065
GEN-2020-083 | 01 - North | 661032 | GLENDCT7 | 115 | 6.6129 | 6.6228 | 0.0099
GEN-2020-083 | 01 - North | 661056 | LEWIS 7 | 115 | 5.8722 | 6.1041 | 0.2319
GEN-2020-083 | 01 - North | 661075 | POPLAR 7 | 115 | 2.7899 | 2.7908 | 0.0009
GEN-2020-083 | 01 - North | 661084 | TIOGA4 4 | 230 | 13.5793 | 13.5931 | 0.0138
GEN-2020-083 | 01 - North | 661085 | TIOGA4 7 | 115 | 13.7543 | 13.764 | 0.0097
GEN-2020-083 | 01 - North | 661086 | TIOGA7 7 | 115 | 10.4765 | 10.4832 | 0.0067
GEN-2020-083 | 01 - North | 661087 | RAY JCT7 | 115 | 5.9002 | 5.9046 | 0.0044
GEN-2020-083 | 01 - North | 661089 | LTLMUDY7 | 115 | 7.1142 | 7.1282 | 0.014
GEN-2020-083 | 01 - North | 672603 | BDV 4 | 230 | 5.0553 | 5.0559 | 0.0006
GEN-2020-083 | 01 - North | 763021 | GEN-2018-067 | 115 | 10.1966 | 10.2108 | 0.0142
GEN-2020-083 | 01 - North | 763043 | GEN-2018-069 | 230 | 4.5147 | 4.5189 | 0.0042
GEN-2020-083 | 01 - North | 764180 | GEN-2020-014 | 115 | 6.8559 | 6.8568 | 0.0009
GEN-2020-083 | 01 - North | 764225 | GEN-2020-091 | 345 | 9.2502 | 9.2647 | 0.0145
GEN-2020-083 | 01 - North | 765070 | GEN-2020-083 | 115 | 5.0728 | 5.583 | 0.5102
GEN-2020-091 | 01 - North | 587030 | GEN-2016-004 | 230 | 7.6736 | 7.6753 | 0.0017
GEN-2020-091 | 01 - North | 588210 | GEN-2016-130 | 345 | 13.0449 | 13.0566 | 0.0117
GEN-2020-091 | 01 - North | 588550 | GEN-2017-010 | 230 | 5.15 | 5.1515 | 0.0015
GEN-2020-091 | 01 - North | 615901 | GRE-STANTON4 | 230 | 18.1911 | 18.1921 | 0.001
GEN-2020-091 | 01 - North | 652216 | WATFORD4 | 230 | 6.9437 | 6.9658 | 0.0221
GEN-2020-091 | 01 - North | 652257 | DEVAUL 8 | 69 | 1.1043 | 1.1043 | 0
GEN-2020-091 | 01 - North | 652391 | WILLISTON27 | 115 | 19.632 | 19.6923 | 0.0603
GEN-2020-091 | 01 - North | 652400 | WILISTN4 | 230 | 11.7935 | 11.8709 | 0.0774
GEN-2020-091 | 01 - North | 652408 | WATFORD7 | 115 | 8.8495 | 8.8628 | 0.0133
GEN-2020-091 | 01 - North | 652419 | KILDEER7 | 115 | 5.0902 | 5.0941 | 0.0039
GEN-2020-091 | 01 - North | 652421 | WILISTN7 | 115 | 19.6218 | 19.682 | 0.0602
GEN-2020-091 | 01 - North | 652424 | BELFELD3 | 345 | 6.9896 | 7.0151 | 0.0255
GEN-2020-091 | 01 - North | 652425 | BELFELD4 | 230 | 9.8544 | 9.8753 | 0.0209
GEN-2020-091 | 01 - North | 652441 | GARRISN4 | 230 | 12.2339 | 12.2357 | 0.0018
GEN-2020-091 | 01 - North | 652456 | WASHBRN4 | 230 | 10.7916 | 10.7944 | 0.0028
GEN-2020-091 | 01 - North | 652468 | HEBRON 4 | 230 | 5.8355 | 5.8377 | 0.0022
GEN-2020-091 | 01 - North | 652616 | MINGUSVILLE4 | 230 | 4.5914 | 4.5931 | 0.0017
GEN-2020-091 | 01 - North | 652651 | FAIRVIEW 7 | 115 | 5.5808 | 5.583 | 0.0022
GEN-2020-091 | 01 - North | 655731 | LARK -MG8 | 69 | 0.9759 | 0.9759 | 0
GEN-2020-091 | 01 - North | 655732 | FLASHER -MG8 | 69 | 0.9029 | 0.9029 | 0
GEN-2020-091 | 01 - North | 655740 | CANNON -MG8 | 69 | 0.9097 | 0.9097 | 0
GEN-2020-091 | 01 - North | 655741 | CEDAR -MG8 | 69 | 0.6895 | 0.6895 | 0
GEN-2020-091 | 01 - North | 655742 | GRANT -MG8 | 69 | 0.6177 | 0.6177 | 0
GEN-2020-091 | 01 - North | 655744 | DEVALTP -MG8 | 69 | 1.1105 | 1.1105 | 0
GEN-2020-091 | 01 - North | 655746 | DEVAUL -MG8 | 69 | 1.1164 | 1.1164 | 0
GEN-2020-091 | 01 - North | 655747 | DEVAUL -MG7 | 115 | 1.1076 | 1.1076 | 0
GEN-2020-091 | 01 - North | 655748 | NEWSALEM-MG7 | 115 | 1.5143 | 1.5143 | 0
GEN-2020-091 | 01 - North | 655749 | MANSWTCH-MG7 | 115 | 1.0234 | 1.0235 | 0.0001
GEN-2020-091 | 01 - North | 655750 | ROUGHRDR-MG7 | 115 | 0.9909 | 0.9909 | 0
GEN-2020-091 | 01 - North | 655751 | NRWSTMDN-MG7 | 115 | 0.9913 | 0.9913 | 0
GEN-2020-091 | 01 - North | 655752 | NWMDNTAP-MG7 | 115 | 1.552 | 1.552 | 0
GEN-2020-091 | 01 - North | 655791 | SPRINGLK-LY7 | 115 | 2.0644 | 2.0647 | 0.0003
GEN-2020-091 | 01 - North | 655792 | NOHLEY -LY7 | 115 | 3.8336 | 3.8346 | 0.001
GEN-2020-091 | 01 - North | 655793 | MARLEY -LY7 | 115 | 6.1024 | 6.1082 | 0.0058
GEN-2020-091 | 01 - North | 655830 | MOUNTAIN-MK7 | 115 | 4.196 | 4.2013 | 0.0053
GEN-2020-091 | 01 - North | 655831 | J12_____-MK7 | 115 | 4.0676 | 4.0767 | 0.0091
GEN-2020-091 | 01 - North | 655832 | BLUEBUTE-MK7 | 115 | 8.0055 | 8.0412 | 0.0357
GEN-2020-091 | 01 - North | 655833 | GRSYBTTP-MK7 | 115 | 14.2114 | 14.2619 | 0.0505
GEN-2020-091 | 01 - North | 655834 | GRASSYBT-MK7 | 115 | 6.9675 | 6.9797 | 0.0122
GEN-2020-091 | 01 - North | 655835 | LITTLKNF-MK7 | 115 | 3.1312 | 3.1342 | 0.003
GEN-2020-091 | 01 - North | 655836 | OAKDALE -MK7 | 115 | 5.5652 | 5.5745 | 0.0093
GEN-2020-091 | 01 - North | 655837 | ELMTREE -MK7 | 115 | 3.666 | 3.6734 | 0.0074
GEN-2020-091 | 01 - North | 655838 | INDIANHL-MK7 | 115 | 4.0761 | 4.0893 | 0.0132
GEN-2020-091 | 01 - North | 655839 | SATHERDM-MK7 | 115 | 2.2606 | 2.2612 | 0.0006
GEN-2020-091 | 01 - North | 655840 | CHRRYCRK-MK7 | 115 | 8.8495 | 8.8628 | 0.0133
GEN-2020-091 | 01 - North | 655841 | ARNEGARD-MK7 | 115 | 6.9539 | 6.9587 | 0.0048
GEN-2020-091 | 01 - North | 655842 | HAYBUTTE-MK7 | 115 | 3.2749 | 3.2834 | 0.0085
GEN-2020-091 | 01 - North | 655843 | TRUEOIL -MK7 | 115 | 1.6355 | 1.6358 | 0.0003
GEN-2020-091 | 01 - North | 655844 | TIMBERCK-MK7 | 115 | 5.2596 | 5.2817 | 0.0221
GEN-2020-091 | 01 - North | 655845 | GRDNCRK2-MK7 | 115 | 4.6966 | 4.7004 | 0.0038
GEN-2020-091 | 01 - North | 655846 | F9______-MK7 | 115 | 4.1788 | 4.1927 | 0.0139
GEN-2020-091 | 01 - North | 655847 | SWENSON -MK7 | 115 | 4.3274 | 4.3378 | 0.0104
GEN-2020-091 | 01 - North | 655848 | BERG -MK7 | 115 | 5.7501 | 5.7685 | 0.0184
GEN-2020-091 | 01 - North | 655849 | VEEDER -MK7 | 115 | 9.8593 | 9.9135 | 0.0542
GEN-2020-091 | 01 - North | 655850 | NRTINDHL-MK7 | 115 | 3.4775 | 3.4872 | 0.0097
GEN-2020-091 | 01 - North | 655851 | BIGGULCH-MK7 | 115 | 2.9212 | 2.9237 | 0.0025
GEN-2020-091 | 01 - North | 655852 | L11_____-MK7 | 115 | 3.5761 | 3.5799 | 0.0038
GEN-2020-091 | 01 - North | 655853 | BEARCREK-MK7 | 115 | 8.4184 | 8.4397 | 0.0213
GEN-2020-091 | 01 - North | 655854 | SANDCREK-MK7 | 115 | 3.5324 | 3.5394 | 0.007
GEN-2020-091 | 01 - North | 655855 | ROOSEVLT-MK7 | 115 | 4.8406 | 4.8446 | 0.004
GEN-2020-091 | 01 - North | 655856 | STNJOHNY-MK7 | 115 | 6.526 | 6.56 | 0.034
GEN-2020-091 | 01 - North | 655857 | MOCCASIN-MK7 | 115 | 2.5929 | 2.5967 | 0.0038
GEN-2020-091 | 01 - North | 655858 | TABLEBUT-MK7 | 115 | 4.3595 | 4.37 | 0.0105
GEN-2020-091 | 01 - North | 655859 | CHARLSON-MK7 | 115 | 3.7439 | 3.7517 | 0.0078
GEN-2020-091 | 01 - North | 655860 | SKAAR___-MK7 | 115 | 3.4794 | 3.4807 | 0.0013
GEN-2020-091 | 01 - North | 655861 | HORSECRK-MK7 | 115 | 2.3228 | 2.3271 | 0.0043
GEN-2020-091 | 01 - North | 655863 | CARTWRIT-MK7 | 115 | 3.1363 | 3.1441 | 0.0078
GEN-2020-091 | 01 - North | 655864 | GRAIL -MK7 | 115 | 5.7639 | 5.7824 | 0.0185
GEN-2020-091 | 01 - North | 655865 | STATION8-MK7 | 115 | 5.9117 | 5.9311 | 0.0194
GEN-2020-091 | 01 - North | 655866 | SNDCRKTP-MK7 | 115 | 4.0756 | 4.0848 | 0.0092
GEN-2020-091 | 01 - North | 655867 | TWNVLYTP-MK7 | 115 | 2.9951 | 3.0022 | 0.0071
GEN-2020-091 | 01 - North | 655869 | TWINVLLY-MK7 | 115 | 2.7608 | 2.7669 | 0.0061
GEN-2020-091 | 01 - North | 655870 | TBGARDEN-MK7 | 115 | 2.6602 | 2.6658 | 0.0056
GEN-2020-091 | 01 - North | 655871 | G9______-MK7 | 115 | 3.9287 | 3.941 | 0.0123
GEN-2020-091 | 01 - North | 655873 | BBCOMPTP-MK7 | 115 | 6.9778 | 7.0049 | 0.0271
GEN-2020-091 | 01 - North | 655874 | BBCMPRSS-MK7 | 115 | 6.371 | 6.3936 | 0.0226
GEN-2020-091 | 01 - North | 655875 | DPLWC___-MK7 | 115 | 7.7281 | 7.7382 | 0.0101
GEN-2020-091 | 01 - North | 655876 | DPLWCTAP-MK7 | 115 | 8.5045 | 8.5167 | 0.0122
GEN-2020-091 | 01 - North | 655877 | LITTLMS4-MK7 | 115 | 5.3106 | 5.3154 | 0.0048
GEN-2020-091 | 01 - North | 655878 | CRESTWD_-MK7 | 115 | 3.9482 | 3.9508 | 0.0026
GEN-2020-091 | 01 - North | 655879 | OASIS___-MK7 | 115 | 4.733 | 4.7368 | 0.0038
GEN-2020-091 | 01 - North | 655880 | SCHAFR_T-MK7 | 115 | 5.783 | 5.8016 | 0.0186
GEN-2020-091 | 01 - North | 655881 | DAP_____-MK7 | 115 | 13.1469 | 13.2434 | 0.0965
GEN-2020-091 | 01 - North | 655882 | GALAXYTP-MK7 | 115 | 9.9091 | 9.9639 | 0.0548
GEN-2020-091 | 01 - North | 655883 | GALAXY -MK7 | 115 | 7.8028 | 7.8367 | 0.0339
GEN-2020-091 | 01 - North | 655884 | DEMCKSLK-MK7 | 115 | 5.4475 | 5.464 | 0.0165
GEN-2020-091 | 01 - North | 655885 | NRTHFORK-MK7 | 115 | 4.2498 | 4.2598 | 0.01
GEN-2020-091 | 01 - North | 655886 | KEENE -MK7 | 115 | 5.0638 | 5.078 | 0.0142
GEN-2020-091 | 01 - North | 655888 | BANKS -MK7 | 115 | 3.4554 | 3.4649 | 0.0095
GEN-2020-091 | 01 - North | 655889 | LC_GAS_P-MK7 | 115 | 6.2629 | 6.2942 | 0.0313
GEN-2020-091 | 01 - North | 655891 | KILLDEER-MK7 | 115 | 4.9167 | 4.9203 | 0.0036
GEN-2020-091 | 01 - North | 655892 | ALEXANDR-MK7 | 115 | 4.0224 | 4.0353 | 0.0129
GEN-2020-091 | 01 - North | 655893 | DUNNCNTR-MK7 | 115 | 6.2867 | 6.2985 | 0.0118
GEN-2020-091 | 01 - North | 655894 | HALLIDAY-MK7 | 115 | 3.557 | 3.5608 | 0.0038
GEN-2020-091 | 01 - North | 655895 | GARDN-FB-MK7 | 115 | 4.3289 | 4.3321 | 0.0032
GEN-2020-091 | 01 - North | 655896 | KEENECRN-MK7 | 115 | 3.4595 | 3.4661 | 0.0066
GEN-2020-091 | 01 - North | 655897 | COYOTCHR-MK7 | 115 | 5.3118 | 5.3275 | 0.0157
GEN-2020-091 | 01 - North | 655898 | SCHAFER -MK7 | 115 | 3.1287 | 3.1304 | 0.0017
GEN-2020-091 | 01 - North | 655899 | FNCYBTAP-MK7 | 115 | 6.4124 | 6.4353 | 0.0229
GEN-2020-091 | 01 - North | 655906 | FINSTAD -MW7 | 115 | 20.859 | 20.8863 | 0.0273
GEN-2020-091 | 01 - North | 655925 | JUDSON -MW7 | 115 | 15.3393 | 15.3731 | 0.0338
GEN-2020-091 | 01 - North | 655926 | SW.WLSTN-MW7 | 115 | 8.6967 | 8.7076 | 0.0109
GEN-2020-091 | 01 - North | 655931 | BLKTLTAP-MW7 | 115 | 10.2717 | 10.2886 | 0.0169
GEN-2020-091 | 01 - North | 655933 | N.MISRDG-MW7 | 115 | 15.1552 | 15.1946 | 0.0394
GEN-2020-091 | 01 - North | 655934 | N.WLST_T-MW7 | 115 | 13.9255 | 13.9588 | 0.0333
GEN-2020-091 | 01 - North | 655935 | NW.WLSTN-MW7 | 115 | 12.4168 | 12.4426 | 0.0258
GEN-2020-091 | 01 - North | 655937 | NE.WLSTN-MW7 | 115 | 12.7152 | 12.7436 | 0.0284
GEN-2020-091 | 01 - North | 655940 | MONT -MW7 | 115 | 15.7177 | 15.7495 | 0.0318
GEN-2020-091 | 01 - North | 655956 | TYRONE -MW7 | 115 | 11.8336 | 11.8589 | 0.0253
GEN-2020-091 | 01 - North | 655957 | EASTFORK-MW7 | 115 | 17.2987 | 17.3586 | 0.0599
GEN-2020-091 | 01 - North | 655958 | FOLVAG -MW7 | 115 | 13.9094 | 13.9469 | 0.0375
GEN-2020-091 | 01 - North | 659060 | FINSTAD345 | 345 | 7.476 | 7.4869 | 0.0109
GEN-2020-091 | 01 - North | 659101 | ANTELOPE-BE3 | 345 | 20.5194 | 20.5789 | 0.0595
GEN-2020-091 | 01 - North | 659105 | LELAND_O-BE3 | 345 | 20.1882 | 20.2168 | 0.0286
GEN-2020-091 | 01 - North | 659106 | LELAND_O-BE4 | 230 | 25.9156 | 25.938 | 0.0224
GEN-2020-091 | 01 - North | 659108 | LOGAN___-BE4 | 230 | 6.5518 | 6.5537 | 0.0019
GEN-2020-091 | 01 - North | 659109 | BASIN___-BE7 | 115 | 5.4311 | 5.4316 | 0.0005
GEN-2020-091 | 01 - North | 659120 | BROADLND-BE3 | 345 | 4.8123 | 4.8126 | 0.0003
GEN-2020-091 | 01 - North | 659124 | DICKINSN-BE4 | 230 | 7.3238 | 7.3315 | 0.0077
GEN-2020-091 | 01 - North | 659125 | DICKINSN-BE7 | 115 | 9.5878 | 9.5935 | 0.0057
GEN-2020-091 | 01 - North | 659154 | LC_CT4-5-BE7 | 115 | 6.8534 | 6.8563 | 0.0029
GEN-2020-091 | 01 - North | 659181 | BICNTNIL-BE7 | 115 | 3.4668 | 3.4685 | 0.0017
GEN-2020-091 | 01 - North | 659182 | CHARL_CK-BE7 | 115 | 14.3358 | 14.3871 | 0.0513
GEN-2020-091 | 01 - North | 659183 | CHARL_CK-BE3 | 345 | 11.1706 | 11.2805 | 0.1099
GEN-2020-091 | 01 - North | 659184 | ROUGHRDR-BE7 | 115 | 4.4415 | 4.4451 | 0.0036
GEN-2020-091 | 01 - North | 659185 | FOUREYES-RR7 | 115 | 3.7485 | 3.752 | 0.0035
GEN-2020-091 | 01 - North | 659191 | SQUAWGAP-BE7 | 115 | 3.482 | 3.4833 | 0.0013
GEN-2020-091 | 01 - North | 659195 | DICKINS2-BE7 | 115 | 9.5506 | 9.5562 | 0.0056
GEN-2020-091 | 01 - North | 659199 | BASIN___-BE4 | 230 | 23.454 | 23.4722 | 0.0182
GEN-2020-091 | 01 - North | 659212 | DGC_____-BE3 | 345 | 19.3843 | 19.4374 | 0.0531
GEN-2020-091 | 01 - North | 659218 | COTEAU__-RR3 | 345 | 20.5194 | 20.5789 | 0.0595
GEN-2020-091 | 01 - North | 659222 | COTEAU_1-RR8 | 69 | 9.8825 | 9.8853 | 0.0028
GEN-2020-091 | 01 - North | 659233 | DGC_____-BE4 | 230 | 7.7107 | 7.7162 | 0.0055
GEN-2020-091 | 01 - North | 659236 | DGC UREA-BE8 | 69 | 7.4089 | 7.4104 | 0.0015
GEN-2020-091 | 01 - North | 659247 | MEDORA__-UM4 | 230 | 5.5312 | 5.5362 | 0.005
GEN-2020-091 | 01 - North | 659248 | HALLIDAY-UM7 | 115 | 4.1912 | 4.1926 | 0.0014
GEN-2020-091 | 01 - North | 659262 | CULBSN.E-BE7 | 115 | 5.8192 | 5.8206 | 0.0014
GEN-2020-091 | 01 - North | 659266 | RHAME___-BE4 | 230 | 5.2576 | 5.2591 | 0.0015
GEN-2020-091 | 01 - North | 659267 | RHAME___-BE7 | 115 | 2.0994 | 2.0995 | 0.0001
GEN-2020-091 | 01 - North | 659269 | CULB_GEN-BE7 | 115 | 5.6994 | 5.7005 | 0.0011
GEN-2020-091 | 01 - North | 659302 | CHARL_CK-BE4 | 230 | 11.9493 | 12.0302 | 0.0809
GEN-2020-091 | 01 - North | 659306 | S.HEART_-RR7 | 115 | 2.3144 | 2.3149 | 0.0005
GEN-2020-091 | 01 - North | 659309 | S.HEART_-RR4 | 230 | 9.8544 | 9.8753 | 0.0209
GEN-2020-091 | 01 - North | 659333 | JUDSON__-BE3 | 345 | 8.8904 | 8.9902 | 0.0998
GEN-2020-091 | 01 - North | 659334 | JUDSON__-BE4 | 230 | 11.7137 | 11.7972 | 0.0835
GEN-2020-091 | 01 - North | 659336 | TANDE___-BE3 | 345 | 9.1764 | 9.203 | 0.0266
GEN-2020-091 | 01 - North | 659337 | TANDE___-BE4 | 230 | 13.3562 | 13.3871 | 0.0309
GEN-2020-091 | 01 - North | 659346 | LC_SWY.S-BE7 | 115 | 6.8538 | 6.8568 | 0.003
GEN-2020-091 | 01 - North | 659348 | LC_CT1-3-BE7 | 115 | 12.3379 | 12.4221 | 0.0842
GEN-2020-091 | 01 - North | 659349 | LC_SWY.N-BE7 | 115 | 12.338 | 12.4222 | 0.0842
GEN-2020-091 | 01 - North | 659362 | WHEELOCK-BE4 | 230 | 8.0273 | 8.0475 | 0.0202
GEN-2020-091 | 01 - North | 659363 | WHEELOCK-BE7 | 115 | 9.5617 | 9.5747 | 0.013
GEN-2020-091 | 01 - North | 659384 | ROUNDUP_-BE3 | 345 | 10.0877 | 10.1801 | 0.0924
GEN-2020-091 | 01 - North | 659385 | ROUNDUP_-MK7 | 115 | 12.1087 | 12.1527 | 0.044
GEN-2020-091 | 01 - North | 659387 | KUMMERDG-BE3 | 345 | 7.614 | 7.7117 | 0.0977
GEN-2020-091 | 01 - North | 659388 | KUMMERDG-MK7 | 115 | 14.5896 | 14.7085 | 0.1189
GEN-2020-091 | 01 - North | 659390 | PATENTGT-BE3 | 345 | 9.183 | 9.4251 | 0.2421
GEN-2020-091 | 01 - North | 659391 | PATENTGT-MK7 | 115 | 18.3211 | 18.5913 | 0.2702
GEN-2020-091 | 01 - North | 659400 | ND.SUN._-PP4 | 230 | 5.2808 | 5.2826 | 0.0018
GEN-2020-091 | 01 - North | 659404 | BURKE___-PP3 | 345 | 4.9357 | 4.9429 | 0.0072
GEN-2020-091 | 01 - North | 659420 | AV.LS-BD-BE3 | 345 | 20.5194 | 20.5789 | 0.0595
GEN-2020-091 | 01 - North | 659421 | BD.LS-AV-BE3 | 345 | 4.8123 | 4.8126 | 0.0003
GEN-2020-091 | 01 - North | 659422 | LO.LS-GR-BE3 | 345 | 20.1882 | 20.2168 | 0.0286
GEN-2020-091 | 01 - North | 659424 | LO.LS-FT-BE3 | 345 | 20.1882 | 20.2168 | 0.0286
GEN-2020-091 | 01 - North | 659427 | TN.LS-JD-BE3 | 345 | 9.1764 | 9.203 | 0.0266
GEN-2020-091 | 01 - North | 659442 | 32STREET-RR7 | 115 | 1.939 | 1.9394 | 0.0004
GEN-2020-091 | 01 - North | 659443 | SKUNKHIL-RR7 | 115 | 1.7444 | 1.7448 | 0.0004
GEN-2020-091 | 01 - North | 659448 | DAGLUM__-BE4 | 230 | 6.8457 | 6.8529 | 0.0072
GEN-2020-091 | 01 - North | 659450 | BRADYWND 4 | 230 | 3.6767 | 3.6783 | 0.0016
GEN-2020-091 | 01 - North | 659466 | PG.KU17A-BE7 | 115 | 18.2223 | 18.4913 | 0.269
GEN-2020-091 | 01 - North | 659467 | PG.KU19A-BE7 | 115 | 18.2341 | 18.5032 | 0.2691
GEN-2020-091 | 01 - North | 659479 | TRADEWND-UA3 | 345 | 6.5043 | 6.5168 | 0.0125
GEN-2020-091 | 01 - North | 659535 | BEAVRHIL-GW4 | 230 | 4.5914 | 4.5931 | 0.0017
GEN-2020-091 | 01 - North | 659536 | BEAVRHIL-GW7 | 115 | 3.6904 | 3.691 | 0.0006
GEN-2020-091 | 01 - North | 659544 | PRNGHORN-RR7 | 115 | 1.939 | 1.9394 | 0.0004
GEN-2020-091 | 01 - North | 659550 | LNGBUTTE-RR4 | 230 | 5.6927 | 5.6948 | 0.0021
GEN-2020-091 | 01 - North | 659551 | LNGBUTTE-RR7 | 115 | 3.5452 | 3.5456 | 0.0004
GEN-2020-091 | 01 - North | 659553 | RAIDER__-RR7 | 115 | 2.3943 | 2.3945 | 0.0002
GEN-2020-091 | 01 - North | 659554 | REDTRAIL-RR7 | 115 | 2.3708 | 2.3709 | 0.0001
GEN-2020-091 | 01 - North | 659555 | RICHRDTN-RR7 | 115 | 2.1936 | 2.1938 | 0.0002
GEN-2020-091 | 01 - North | 659576 | BEPCPRXCC1 3 | 345 | 19.6406 | 19.6936 | 0.053
GEN-2020-091 | 01 - North | 659584 | BEPCPRXCC3 7 | 115 | 14.3382 | 14.453 | 0.1148
GEN-2020-091 | 01 - North | 659600 | EFORK_-BE334 | 345 | 8.1943 | 8.2497 | 0.0554
GEN-2020-091 | 01 - North | 661003 | WATFRDSOUTH4 | 230 | 6.8699 | 6.8914 | 0.0215
GEN-2020-091 | 01 - North | 661011 | BEULAH27 | 115 | 9.9141 | 9.9155 | 0.0014
GEN-2020-091 | 01 - North | 661084 | TIOGA4 4 | 230 | 13.562 | 13.5931 | 0.0311
GEN-2020-091 | 01 - North | 661089 | LTLMUDY7 | 115 | 7.1214 | 7.1282 | 0.0068
GEN-2020-091 | 01 - North | 760998 | GEN-2017-214 | 230 | 3.2409 | 3.2412 | 0.0003
GEN-2020-091 | 01 - North | 762537 | GEN-2018-008 | 345 | 4.439 | 4.4394 | 0.0004
GEN-2020-091 | 01 - North | 762544 | G18-008-TAP | 345 | 4.4435 | 4.4438 | 0.0003
GEN-2020-091 | 01 - North | 763043 | GEN-2018-069 | 230 | 4.5172 | 4.5189 | 0.0017
GEN-2020-091 | 01 - North | 763703 | GEN-2019-037 | 345 | 12.1923 | 12.2025 | 0.0102
GEN-2020-091 | 01 - North | 764180 | GEN-2020-014 | 115 | 6.8538 | 6.8568 | 0.003
GEN-2020-091 | 01 - North | 764210 | GEN-2020-021 | 345 | 3.6535 | 3.6537 | 0.0002
GEN-2020-091 | 01 - North | 764220 | G20-021-TAP | 345 | 4.2846 | 4.2849 | 0.0003
GEN-2020-091 | 01 - North | 764225 | GEN-2020-091 | 345 | 9.0225 | 9.2647 | 0.2422
GEN-2020-091 | 01 - North | 765070 | GEN-2020-083 | 115 | 5.5808 | 5.583 | 0.0022
GEN-2020-001 | 02 - Nebraska | 531451 | MINGO 7 | 345 | 6.1834 | 6.1855 | 0.0021
GEN-2020-001 | 02 - Nebraska | 531632 | GEN-2015-065 | 345 | 5.4834 | 5.485 | 0.0016
GEN-2020-001 | 02 - Nebraska | 584650 | GEN-2015-023 | 345 | 12.9241 | 12.9266 | 0.0025
GEN-2020-001 | 02 - Nebraska | 587680 | GEN-2016-074 | 345 | 6.3955 | 6.3985 | 0.003
GEN-2020-001 | 02 - Nebraska | 588220 | GEN-2016-147 | 115 | 4.4344 | 4.4633 | 0.0289
GEN-2020-001 | 02 - Nebraska | 640183 | GENTLMN3 | 345 | 16.1516 | 16.2446 | 0.093
GEN-2020-001 | 02 - Nebraska | 640184 | GENTLMN4 | 230 | 19.3777 | 19.4534 | 0.0757
GEN-2020-001 | 02 - Nebraska | 640252 | KEYSTON3 | 345 | 8.7985 | 8.9089 | 0.1104
GEN-2020-001 | 02 - Nebraska | 640253 | KEYSTON7 | 115 | 14.8457 | 14.9372 | 0.0915
GEN-2020-001 | 02 - Nebraska | 640255 | KINGSLY7 | 115 | 9.2813 | 9.3145 | 0.0332
GEN-2020-001 | 02 - Nebraska | 640286 | N.PLATT4 | 230 | 13.3327 | 13.3642 | 0.0315
GEN-2020-001 | 02 - Nebraska | 640302 | OGALALA4 | 230 | 7.8947 | 7.9478 | 0.0531
GEN-2020-001 | 02 - Nebraska | 640304 | OGALALANPPD7 | 115 | 14.8708 | 14.9615 | 0.0907
GEN-2020-001 | 02 - Nebraska | 640325 | REDWILO3 | 345 | 6.5094 | 6.5169 | 0.0075
GEN-2020-001 | 02 - Nebraska | 640326 | REDWILO7 | 115 | 14.0608 | 14.073 | 0.0122
GEN-2020-001 | 02 - Nebraska | 640338 | SCOTBLF7 | 115 | 6.1939 | 6.2325 | 0.0386
GEN-2020-001 | 02 - Nebraska | 640374 | SWEET W3 | 345 | 11.3084 | 11.3183 | 0.0099
GEN-2020-001 | 02 - Nebraska | 640381 | THEDFRD7 | 115 | 9.7462 | 9.7511 | 0.0049
GEN-2020-001 | 02 - Nebraska | 640396 | VICTRYH4 | 230 | 3.7325 | 3.7614 | 0.0289
GEN-2020-001 | 02 - Nebraska | 640397 | VICTRYH7 | 115 | 6.2434 | 6.2822 | 0.0388
GEN-2020-001 | 02 - Nebraska | 640404 | WAYSIDE4 | 230 | 2.7998 | 2.8067 | 0.0069
GEN-2020-001 | 02 - Nebraska | 640500 | THEDFRD3 | 345 | 6.3239 | 6.3307 | 0.0068
GEN-2020-001 | 02 - Nebraska | 640510 | HOLT.CO3 | 345 | 13.1 | 13.1026 | 0.0026
GEN-2020-001 | 02 - Nebraska | 640529 | BOBCAT.C 3 | 345 | 4.8903 | 4.9758 | 0.0855
GEN-2020-001 | 02 - Nebraska | 640530 | BOBCAT.C 7 | 115 | 8.6895 | 8.7753 | 0.0858
GEN-2020-001 | 02 - Nebraska | 652573 | STEGALL4 | 230 | 5.2513 | 5.3099 | 0.0586
GEN-2020-001 | 02 - Nebraska | 652873 | STEGALL-LNX3 | 230 | 5.2355 | 5.2936 | 0.0581
GEN-2020-001 | 02 - Nebraska | 653300 | CHAPPEL7 | 115 | 3.5 | 3.512 | 0.012
GEN-2020-001 | 02 - Nebraska | 653571 | GR ISLD3 | 345 | 13.5626 | 13.5665 | 0.0039
GEN-2020-001 | 02 - Nebraska | 653572 | SIDNEY 7 | 115 | 4.5369 | 4.5673 | 0.0304
GEN-2020-001 | 02 - Nebraska | 659131 | LARAMIE_-MB3 | 345 | 6.9783 | 7.0663 | 0.088
GEN-2020-001 | 02 - Nebraska | 659133 | SIDNEY__-MB3 | 345 | 6.0099 | 6.3175 | 0.3076
GEN-2020-001 | 02 - Nebraska | 659134 | SIDNEY___TS4 | 230 | 6.3464 | 6.5134 | 0.167
GEN-2020-001 | 02 - Nebraska | 659135 | STEGALL_-MB3 | 345 | 4.8903 | 4.9758 | 0.0855
GEN-2020-001 | 02 - Nebraska | 659206 | STEGALL_-MB4 | 230 | 5.4944 | 5.5598 | 0.0654
GEN-2020-001 | 02 - Nebraska | 659210 | SIDNEY__-MB4 | 230 | 6.7614 | 6.9676 | 0.2062
GEN-2020-001 | 02 - Nebraska | 659425 | SD.LS-KS-MB3 | 345 | 6.0099 | 6.3175 | 0.3076
GEN-2020-001 | 02 - Nebraska | 659426 | SD.LS-LR-MB3 | 345 | 6.0099 | 6.3175 | 0.3076
GEN-2020-001 | 02 - Nebraska | 659800 | GRANTNB_-TS7 | 115 | 6.4938 | 6.5083 | 0.0145
GEN-2020-001 | 02 - Nebraska | 659801 | OGALALA_-TS7 | 115 | 14.8708 | 14.9615 | 0.0907
GEN-2020-001 | 02 - Nebraska | 659817 | COLTON__-TS7 | 115 | 3.9329 | 3.9537 | 0.0208
GEN-2020-001 | 02 - Nebraska | 659821 | GERINGT_-TS7 | 115 | 5.5884 | 5.6195 | 0.0311
GEN-2020-001 | 02 - Nebraska | 659824 | MCONGHY_-TS7 | 115 | 5.5437 | 5.5562 | 0.0125
GEN-2020-001 | 02 - Nebraska | 659825 | ARTHUR__-TS7 | 115 | 2.1677 | 2.1696 | 0.0019
GEN-2020-001 | 02 - Nebraska | 659826 | HYANNIS_-TS7 | 115 | 1.2209 | 1.2215 | 0.0006
GEN-2020-001 | 02 - Nebraska | 659829 | DH_CS_EA-TS4 | 230 | 5.2513 | 5.3099 | 0.0586
GEN-2020-001 | 02 - Nebraska | 760767 | GEN-2017-144 | 345 | 12.2242 | 12.2264 | 0.0022
GEN-2020-001 | 02 - Nebraska | 763406 | GEN-2018-125 | 345 | 7.2117 | 7.2211 | 0.0094
GEN-2020-001 | 02 - Nebraska | 763410 | G18-125-TAP | 345 | 7.5408 | 7.5511 | 0.0103
GEN-2020-001 | 02 - Nebraska | 764255 | GEN-2020-001 | 345 | 5.4586 | 5.7676 | 0.309
GEN-2020-001 | 02 - Nebraska | 764420 | GEN-2020-011 | 345 | 9.8044 | 9.8084 | 0.004
GEN-2020-001 | 02 - Nebraska | 764430 | G20-011-TAP | 345 | 9.8044 | 9.8084 | 0.004
GEN-2020-001 | 02 - Nebraska | 764431 | G20-011-SS1 | 345 | 9.794 | 9.798 | 0.004
GEN-2020-001 | 02 - Nebraska | 764432 | G20-011-SS2 | 345 | 9.6818 | 9.6857 | 0.0039
GEN-2020-001 | 02 - Nebraska | 764433 | G20-011-SS3 | 345 | 9.7178 | 9.7217 | 0.0039
GEN-2020-001 | 02 - Nebraska | 764434 | G20-011-SS4 | 345 | 9.5233 | 9.5271 | 0.0038
GEN-2020-002 | 02 - Nebraska | 640155 | DAVEY 7 | 115 | 11.422 | 11.4243 | 0.0023
GEN-2020-002 | 02 - Nebraska | 640320 | PLTSMTH8 | 69 | 5.4742 | 5.4765 | 0.0023
GEN-2020-002 | 02 - Nebraska | 646209 | S1209 5 | 161 | 48.3677 | 48.4181 | 0.0504
GEN-2020-002 | 02 - Nebraska | 646214 | S1214 5 | 161 | 12.8734 | 12.9523 | 0.0789
GEN-2020-002 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.7444 | 34.7844 | 0.04
GEN-2020-002 | 02 - Nebraska | 646260 | S1260 5 | 161 | 42.8765 | 42.944 | 0.0675
GEN-2020-002 | 02 - Nebraska | 646281 | S1281 5 | 161 | 40.7847 | 40.8654 | 0.0807
GEN-2020-002 | 02 - Nebraska | 646287 | S1287 5 | 161 | 23.6142 | 23.6795 | 0.0653
GEN-2020-002 | 02 - Nebraska | 646361 | S1361 5 | 161 | 44.315 | 44.3845 | 0.0695
GEN-2020-002 | 02 - Nebraska | 646363 | S1363 5 | 161 | 37.8686 | 37.9198 | 0.0512
GEN-2020-002 | 02 - Nebraska | 647014 | S914A 8 | 69 | 11.4006 | 11.7437 | 0.3431
GEN-2020-002 | 02 - Nebraska | 647079 | 979TP 8 | 69 | 7.0307 | 7.0421 | 0.0114
GEN-2020-002 | 02 - Nebraska | 647091 | 991TP 8 | 69 | 11.5722 | 11.6077 | 0.0355
GEN-2020-002 | 02 - Nebraska | 647100 | ASH GRV8 | 69 | 6.9371 | 6.9562 | 0.0191
GEN-2020-002 | 02 - Nebraska | 647104 | MUD LNG8 | 69 | 14.691 | 14.7031 | 0.0121
GEN-2020-002 | 02 - Nebraska | 647427 | FREM G 8 | 69 | 14.0599 | 14.0925 | 0.0326
GEN-2020-002 | 02 - Nebraska | 647846 | S6846 8 | 69 | 7.3754 | 8.0553 | 0.6799
GEN-2020-002 | 02 - Nebraska | 647900 | S900 8 | 69 | 8.0832 | 8.1092 | 0.026
GEN-2020-002 | 02 - Nebraska | 647902 | S902 8 | 69 | 8.9726 | 9.1911 | 0.2185
GEN-2020-002 | 02 - Nebraska | 647904 | S904 8 | 69 | 8.7477 | 8.7528 | 0.0051
GEN-2020-002 | 02 - Nebraska | 647909 | S909 8 | 69 | 27.1483 | 27.2018 | 0.0535
GEN-2020-002 | 02 - Nebraska | 647914 | S914 8 | 69 | 7.8025 | 7.9155 | 0.113
GEN-2020-002 | 02 - Nebraska | 647918 | S918 8 | 69 | 22.9985 | 23.0211 | 0.0226
GEN-2020-002 | 02 - Nebraska | 647921 | S921 8 | 69 | 26.5417 | 26.5599 | 0.0182
GEN-2020-002 | 02 - Nebraska | 647939 | S939 8 | 69 | 20.1785 | 20.2016 | 0.0231
GEN-2020-002 | 02 - Nebraska | 647960 | S960 8 | 69 | 7.4816 | 7.4904 | 0.0088
GEN-2020-002 | 02 - Nebraska | 647972 | S972 8 | 69 | 4.285 | 4.2897 | 0.0047
GEN-2020-002 | 02 - Nebraska | 647979 | S979 8 | 69 | 6.8811 | 6.8921 | 0.011
GEN-2020-002 | 02 - Nebraska | 647982 | S982 8 | 69 | 3.8355 | 3.8378 | 0.0023
GEN-2020-002 | 02 - Nebraska | 647983 | S983 8 | 69 | 7.1754 | 7.624 | 0.4486
GEN-2020-002 | 02 - Nebraska | 647984 | S984 8 | 69 | 7.8574 | 7.9748 | 0.1174
GEN-2020-002 | 02 - Nebraska | 647985 | S985 8 | 69 | 8.1566 | 8.1623 | 0.0057
GEN-2020-002 | 02 - Nebraska | 647988 | S988 8 | 69 | 2.8888 | 2.9105 | 0.0217
GEN-2020-002 | 02 - Nebraska | 647991 | S991 8 | 69 | 9.7462 | 9.7714 | 0.0252
GEN-2020-002 | 02 - Nebraska | 650169 | 70&BLUFF 5 | 161 | 8.9295 | 8.9442 | 0.0147
GEN-2020-002 | 02 - Nebraska | 650261 | 56&I80 7 | 115 | 23.0447 | 23.0536 | 0.0089
GEN-2020-002 | 02 - Nebraska | 650269 | 70&BLUFF 7 | 115 | 25.7265 | 25.7389 | 0.0124
GEN-2020-002 | 02 - Nebraska | 650275 | 84&BLUFF 7 | 115 | 27.0776 | 27.089 | 0.0114
GEN-2020-002 | 02 - Nebraska | 650277 | TBGS_A 7 | 115 | 25.7616 | 25.7719 | 0.0103
GEN-2020-002 | 02 - Nebraska | 650278 | TBGS_B 7 | 115 | 25.9431 | 25.9534 | 0.0103
GEN-2020-002 | 02 - Nebraska | 764570 | GEN-2020-002 | 69 | 7.3754 | 8.0553 | 0.6799
GEN-2020-002 | 02 - Nebraska | 764600 | GEN-2020-025 | 161 | 37.8686 | 37.9198 | 0.0512
GEN-2020-002 | 02 - Nebraska | 764615 | GEN-2020-027 | 161 | 37.1791 | 37.2285 | 0.0494
GEN-2020-002 | 02 - Nebraska | 764630 | GEN-2020-028 | 161 | 37.8686 | 37.9198 | 0.0512
GEN-2020-002 | 02 - Nebraska | 764660 | GEN-2020-031 | 161 | 37.8686 | 37.9198 | 0.0512
GEN-2020-011 | 02 - Nebraska | 530583 | POSTROCK7 | 345 | 7.9008 | 7.9233 | 0.0225
GEN-2020-011 | 02 - Nebraska | 530584 | POSTROCK6 | 230 | 10.7773 | 10.7949 | 0.0176
GEN-2020-011 | 02 - Nebraska | 530702 | BUCKEYE_230 | 230 | 7.9711 | 7.9803 | 0.0092
GEN-2020-011 | 02 - Nebraska | 531429 | MINGO 3 | 115 | 12.6443 | 12.6475 | 0.0032
GEN-2020-011 | 02 - Nebraska | 531451 | MINGO 7 | 345 | 6.1831 | 6.1855 | 0.0024
GEN-2020-011 | 02 - Nebraska | 531465 | SETAB 7 | 345 | 6.7954 | 6.7971 | 0.0017
GEN-2020-011 | 02 - Nebraska | 531469 | SPERVIL7 | 345 | 11.2037 | 11.211 | 0.0073
GEN-2020-011 | 02 - Nebraska | 531623 | EASTFORK3 | 115 | 10.0536 | 10.0556 | 0.002
GEN-2020-011 | 02 - Nebraska | 531632 | GEN-2015-065 | 345 | 5.4832 | 5.485 | 0.0018
GEN-2020-011 | 02 - Nebraska | 560082 | G16-050-TAP | 345 | 7.4175 | 7.5497 | 0.1322
GEN-2020-011 | 02 - Nebraska | 584650 | GEN-2015-023 | 345 | 12.9149 | 12.9266 | 0.0117
GEN-2020-011 | 02 - Nebraska | 585241 | GEN-2015-088 | 345 | 12.3293 | 12.364 | 0.0347
GEN-2020-011 | 02 - Nebraska | 587350 | GEN-2016-050 | 345 | 6.2286 | 6.3186 | 0.09
GEN-2020-011 | 02 - Nebraska | 587680 | GEN-2016-074 | 345 | 6.3216 | 6.3985 | 0.0769
GEN-2020-011 | 02 - Nebraska | 640063 | AURORA_7 | 115 | 7.286 | 7.2904 | 0.0044
GEN-2020-011 | 02 - Nebraska | 640065 | AXTELL 3 | 345 | 9.8908 | 10.2613 | 0.3705
GEN-2020-011 | 02 - Nebraska | 640066 | AXTELL 7 | 115 | 15.196 | 15.3509 | 0.1549
GEN-2020-011 | 02 - Nebraska | 640082 | BEVERLY7 | 115 | 5.1726 | 5.1738 | 0.0012
GEN-2020-011 | 02 - Nebraska | 640083 | BEVERLY8 | 69 | 4.6036 | 4.6041 | 0.0005
GEN-2020-011 | 02 - Nebraska | 640093 | C.CREEK4 | 230 | 7.2807 | 7.2917 | 0.011
GEN-2020-011 | 02 - Nebraska | 640096 | CALAMS 7 | 115 | 3.5605 | 3.5607 | 0.0002
GEN-2020-011 | 02 - Nebraska | 640103 | CANADAY7 | 115 | 13.8339 | 13.8539 | 0.02
GEN-2020-011 | 02 - Nebraska | 640107 | CENCITY7 | 115 | 5.2938 | 5.2957 | 0.0019
GEN-2020-011 | 02 - Nebraska | 640131 | COLMB.W4 | 230 | 10.37 | 10.3748 | 0.0048
GEN-2020-011 | 02 - Nebraska | 640133 | COLMBUS4 | 230 | 12.1487 | 12.1541 | 0.0054
GEN-2020-011 | 02 - Nebraska | 640161 | ELMCRK_7 | 115 | 6.2011 | 6.2095 | 0.0084
GEN-2020-011 | 02 - Nebraska | 640162 | ELMCRK 8 | 69 | 3.8694 | 3.8714 | 0.002
GEN-2020-011 | 02 - Nebraska | 640178 | GENEVA 7 | 115 | 10.0192 | 10.0249 | 0.0057
GEN-2020-011 | 02 - Nebraska | 640179 | GENEVA 8 | 69 | 4.3206 | 4.3212 | 0.0006
GEN-2020-011 | 02 - Nebraska | 640183 | GENTLMN3 | 345 | 16.1841 | 16.2446 | 0.0605
GEN-2020-011 | 02 - Nebraska | 640184 | GENTLMN4 | 230 | 19.4171 | 19.4534 | 0.0363
GEN-2020-011 | 02 - Nebraska | 640194 | GOSPER 7 | 115 | 4.5544 | 4.556 | 0.0016
GEN-2020-011 | 02 - Nebraska | 640200 | GR ISLD4 | 230 | 17.6756 | 17.749 | 0.0734
GEN-2020-011 | 02 - Nebraska | 640201 | GR ISLD7 | 115 | 23.8877 | 23.9447 | 0.057
GEN-2020-011 | 02 - Nebraska | 640206 | GUIDE R7 | 115 | 4.3881 | 4.3912 | 0.0031
GEN-2020-011 | 02 - Nebraska | 640207 | GUIDE R8 | 69 | 2.2475 | 2.248 | 0.0005
GEN-2020-011 | 02 - Nebraska | 640214 | HASTING4 | 230 | 7.621 | 7.6356 | 0.0146
GEN-2020-011 | 02 - Nebraska | 640215 | HASTING7 | 115 | 19.6281 | 19.6814 | 0.0533
GEN-2020-011 | 02 - Nebraska | 640222 | HILDRTH7 | 115 | 4.6015 | 4.6076 | 0.0061
GEN-2020-011 | 02 - Nebraska | 640223 | HILDRTH8 | 69 | 3.6303 | 3.6326 | 0.0023
GEN-2020-011 | 02 - Nebraska | 640224 | HOLDREG7 | 115 | 7.3571 | 7.3731 | 0.016
GEN-2020-011 | 02 - Nebraska | 640242 | JOHN.2 7 | 115 | 12.8238 | 12.8408 | 0.017
GEN-2020-011 | 02 - Nebraska | 640244 | JOHN.LK7 | 115 | 8.9524 | 8.9602 | 0.0078
GEN-2020-011 | 02 - Nebraska | 640245 | JOHN.LK8 | 69 | 4.2882 | 4.2893 | 0.0011
GEN-2020-011 | 02 - Nebraska | 640248 | KEAR.NE7 | 115 | 9.8314 | 9.8583 | 0.0269
GEN-2020-011 | 02 - Nebraska | 640250 | KEARNEY7 | 115 | 12.5214 | 12.5742 | 0.0528
GEN-2020-011 | 02 - Nebraska | 640252 | KEYSTON3 | 345 | 8.8956 | 8.9089 | 0.0133
GEN-2020-011 | 02 - Nebraska | 640253 | KEYSTON7 | 115 | 14.9269 | 14.9372 | 0.0103
GEN-2020-011 | 02 - Nebraska | 640255 | KINGSLY7 | 115 | 9.3107 | 9.3145 | 0.0038
GEN-2020-011 | 02 - Nebraska | 640261 | LOWELL 7 | 115 | 8.4986 | 8.5249 | 0.0263
GEN-2020-011 | 02 - Nebraska | 640262 | LOWELL 8 | 69 | 4.2238 | 4.2276 | 0.0038
GEN-2020-011 | 02 - Nebraska | 640269 | MCCOOK 7 | 115 | 9.8636 | 9.8678 | 0.0042
GEN-2020-011 | 02 - Nebraska | 640270 | MCCOOK 8 | 69 | 4.7616 | 4.7622 | 0.0006
GEN-2020-011 | 02 - Nebraska | 640271 | MCCOOL 3 | 345 | 11.5916 | 11.6185 | 0.0269
GEN-2020-011 | 02 - Nebraska | 640272 | MCCOOL 7 | 115 | 14.8072 | 14.8207 | 0.0135
GEN-2020-011 | 02 - Nebraska | 640273 | MCCOOL 8 | 69 | 5.7386 | 5.7398 | 0.0012
GEN-2020-011 | 02 - Nebraska | 640275 | MINDEN 7 | 115 | 7.5214 | 7.5496 | 0.0282
GEN-2020-011 | 02 - Nebraska | 640277 | MOORE 3 | 345 | 23.8574 | 23.8992 | 0.0418
GEN-2020-011 | 02 - Nebraska | 640278 | SHELDON7 | 115 | 44.5571 | 44.587 | 0.0299
GEN-2020-011 | 02 - Nebraska | 640286 | N.PLATT4 | 230 | 13.3455 | 13.3642 | 0.0187
GEN-2020-011 | 02 - Nebraska | 640287 | N.PLATT7 | 115 | 18.8597 | 18.8782 | 0.0185
GEN-2020-011 | 02 - Nebraska | 640288 | N.PLATT8 | 69 | 5.1284 | 5.1292 | 0.0008
GEN-2020-011 | 02 - Nebraska | 640302 | OGALALA4 | 230 | 7.9425 | 7.9478 | 0.0053
GEN-2020-011 | 02 - Nebraska | 640304 | OGALALANPPD7 | 115 | 14.9517 | 14.9615 | 0.0098
GEN-2020-011 | 02 - Nebraska | 640310 | ORLEANS7 | 115 | 2.6231 | 2.6251 | 0.002
GEN-2020-011 | 02 - Nebraska | 640311 | ORLEANS8 | 69 | 2.5601 | 2.5613 | 0.0012
GEN-2020-011 | 02 - Nebraska | 640312 | PAULINE3 | 345 | 8.3765 | 8.4754 | 0.0989
GEN-2020-011 | 02 - Nebraska | 640313 | PAULINE7 | 115 | 16.94 | 17.0184 | 0.0784
GEN-2020-011 | 02 - Nebraska | 640314 | PAULINE8 | 69 | 4.9431 | 4.9471 | 0.004
GEN-2020-011 | 02 - Nebraska | 640321 | PROSSER7 | 115 | 6.9891 | 7.0008 | 0.0117
GEN-2020-011 | 02 - Nebraska | 640322 | PROSSER8 | 69 | 3.8968 | 3.899 | 0.0022
GEN-2020-011 | 02 - Nebraska | 640325 | REDWILO3 | 345 | 6.5114 | 6.5169 | 0.0055
GEN-2020-011 | 02 - Nebraska | 640326 | REDWILO7 | 115 | 14.0643 | 14.073 | 0.0087
GEN-2020-011 | 02 - Nebraska | 640330 | RIVERDL4 | 230 | 7.5836 | 7.601 | 0.0174
GEN-2020-011 | 02 - Nebraska | 640331 | RIVERDL7 | 115 | 13.3985 | 13.4338 | 0.0353
GEN-2020-011 | 02 - Nebraska | 640332 | RIVERDL8 | 69 | 6.7169 | 6.7222 | 0.0053
GEN-2020-011 | 02 - Nebraska | 640353 | ST.LIB 7 | 115 | 9.9419 | 9.9508 | 0.0089
GEN-2020-011 | 02 - Nebraska | 640355 | ST.PAUL7 | 115 | 3.9833 | 3.9847 | 0.0014
GEN-2020-011 | 02 - Nebraska | 640359 | STAPLETON 7 | 115 | 4.2671 | 4.268 | 0.0009
GEN-2020-011 | 02 - Nebraska | 640360 | STAPLETON 8 | 69 | 3.4716 | 3.472 | 0.0004
GEN-2020-011 | 02 - Nebraska | 640365 | STOCKVL7 | 115 | 4.8423 | 4.8434 | 0.0011
GEN-2020-011 | 02 - Nebraska | 640366 | STOCKVL8 | 69 | 3.4595 | 3.4598 | 0.0003
GEN-2020-011 | 02 - Nebraska | 640374 | SWEET W3 | 345 | 11.0684 | 11.3183 | 0.2499
GEN-2020-011 | 02 - Nebraska | 640381 | THEDFRD7 | 115 | 9.7468 | 9.7511 | 0.0043
GEN-2020-011 | 02 - Nebraska | 640383 | TOWER 7 | 115 | 9.45 | 9.4753 | 0.0253
GEN-2020-011 | 02 - Nebraska | 640407 | WESTMIN7 | 115 | 8.1263 | 8.1328 | 0.0065
GEN-2020-011 | 02 - Nebraska | 640413 | YORK SW7 | 115 | 8.4265 | 8.4306 | 0.0041
GEN-2020-011 | 02 - Nebraska | 640416 | AURORA_8 | 69 | 4.0875 | 4.0883 | 0.0008
GEN-2020-011 | 02 - Nebraska | 640447 | YORK.SW T2 8 | 69 | 2.5298 | 2.5301 | 0.0003
GEN-2020-011 | 02 - Nebraska | 640448 | HOLDREGE 8 | 69 | 4.039 | 4.0418 | 0.0028
GEN-2020-011 | 02 - Nebraska | 640500 | THEDFRD3 | 345 | 6.3246 | 6.3307 | 0.0061
GEN-2020-011 | 02 - Nebraska | 640510 | HOLT.CO3 | 345 | 13.0906 | 13.1026 | 0.012
GEN-2020-011 | 02 - Nebraska | 640520 | ANTELOPE 3 | 345 | 12.6255 | 12.6319 | 0.0064
GEN-2020-011 | 02 - Nebraska | 640525 | TOBIAS 3 | 345 | 12.3293 | 12.364 | 0.0347
GEN-2020-011 | 02 - Nebraska | 640583 | ROSEMONT 7 | 115 | 6.7929 | 6.8024 | 0.0095
GEN-2020-011 | 02 - Nebraska | 640584 | COTTONWD 7 | 115 | 5.4849 | 5.4908 | 0.0059
GEN-2020-011 | 02 - Nebraska | 640590 | MONOLITH 3 | 345 | 23.331 | 23.3699 | 0.0389
GEN-2020-011 | 02 - Nebraska | 641087 | EGYCNTR7 | 115 | 18.2279 | 18.2671 | 0.0392
GEN-2020-011 | 02 - Nebraska | 641088 | HASTCTY7 | 115 | 19.6281 | 19.6814 | 0.0533
GEN-2020-011 | 02 - Nebraska | 642071 | SUB-D 7 | 115 | 17.5526 | 17.5817 | 0.0291
GEN-2020-011 | 02 - Nebraska | 642072 | SUB-E 7 | 115 | 17.2456 | 17.2735 | 0.0279
GEN-2020-011 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17.8237 | 17.8395 | 0.0158
GEN-2020-011 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21.3473 | 21.3651 | 0.0178
GEN-2020-011 | 02 - Nebraska | 652832 | GRPRAR1-LNX3 | 345 | 9.1664 | 9.1694 | 0.003
GEN-2020-011 | 02 - Nebraska | 653571 | GR ISLD3 | 345 | 13.4934 | 13.5665 | 0.0731
GEN-2020-011 | 02 - Nebraska | 653871 | GR ISLD-LNX3 | 345 | 13.3701 | 13.4415 | 0.0714
GEN-2020-011 | 02 - Nebraska | 659133 | SIDNEY__-MB3 | 345 | 6.3147 | 6.3175 | 0.0028
GEN-2020-011 | 02 - Nebraska | 659134 | SIDNEY___TS4 | 230 | 6.5112 | 6.5134 | 0.0022
GEN-2020-011 | 02 - Nebraska | 659425 | SD.LS-KS-MB3 | 345 | 6.3147 | 6.3175 | 0.0028
GEN-2020-011 | 02 - Nebraska | 760767 | GEN-2017-144 | 345 | 12.216 | 12.2264 | 0.0104
GEN-2020-011 | 02 - Nebraska | 761208 | GEN-2017-210 | 345 | 10.1357 | 10.1559 | 0.0202
GEN-2020-011 | 02 - Nebraska | 761292 | GEN-2017-181 | 345 | 6.9997 | 7.0097 | 0.01
GEN-2020-011 | 02 - Nebraska | 761313 | GEN-2017-182 | 345 | 5.8453 | 5.8522 | 0.0069
GEN-2020-011 | 02 - Nebraska | 763032 | GEN-2018-068 | 345 | 9.4532 | 9.4566 | 0.0034
GEN-2020-011 | 02 - Nebraska | 763406 | GEN-2018-125 | 345 | 7.1794 | 7.2211 | 0.0417
GEN-2020-011 | 02 - Nebraska | 763410 | G18-125-TAP | 345 | 7.5052 | 7.5511 | 0.0459
GEN-2020-011 | 02 - Nebraska | 763439 | GEN-2018-131 | 345 | 12.6064 | 12.6127 | 0.0063
GEN-2020-011 | 02 - Nebraska | 763450 | GEN-2018-132 | 345 | 11.6647 | 11.6702 | 0.0055
GEN-2020-011 | 02 - Nebraska | 764255 | GEN-2020-001 | 345 | 5.7653 | 5.7676 | 0.0023
GEN-2020-011 | 02 - Nebraska | 764420 | GEN-2020-011 | 345 | 9.2859 | 9.8084 | 0.5225
GEN-2020-011 | 02 - Nebraska | 764430 | G20-011-TAP | 345 | 9.2859 | 9.8084 | 0.5225
GEN-2020-011 | 02 - Nebraska | 764431 | G20-011-SS1 | 345 | 9.276 | 9.798 | 0.522
GEN-2020-011 | 02 - Nebraska | 764432 | G20-011-SS2 | 345 | 9.1725 | 9.6857 | 0.5132
GEN-2020-011 | 02 - Nebraska | 764433 | G20-011-SS3 | 345 | 9.2038 | 9.7217 | 0.5179
GEN-2020-011 | 02 - Nebraska | 764434 | G20-011-SS4 | 345 | 9.0243 | 9.5271 | 0.5028
GEN-2020-011 | 02 - Nebraska | 764435 | GEN-2020-013 | 115 | 7.1627 | 7.1777 | 0.015
GEN-2020-011 | 02 - Nebraska | 764445 | G20-013-TAP | 115 | 7.1729 | 7.188 | 0.0151
GEN-2020-011 | 02 - Nebraska | 764446 | G20-013-SS1 | 115 | 7.1442 | 7.1592 | 0.015
GEN-2020-011 | 02 - Nebraska | 764447 | G20-013-SS2 | 115 | 6.8506 | 6.8641 | 0.0135
GEN-2020-011 | 02 - Nebraska | 764448 | G20-013-SS3 | 115 | 6.784 | 6.7973 | 0.0133
GEN-2020-011 | 02 - Nebraska | 765025 | GEN-2020-070 | 345 | 6.8563 | 6.8887 | 0.0324
GEN-2020-011 | 02 - Nebraska | 765035 | G20-070-TAP | 345 | 6.8563 | 6.8887 | 0.0324
GEN-2020-013 | 02 - Nebraska | 560082 | G16-050-TAP | 345 | 7.5169 | 7.5497 | 0.0328
GEN-2020-013 | 02 - Nebraska | 585241 | GEN-2015-088 | 345 | 12.3465 | 12.364 | 0.0175
GEN-2020-013 | 02 - Nebraska | 587350 | GEN-2016-050 | 345 | 6.2963 | 6.3186 | 0.0223
GEN-2020-013 | 02 - Nebraska | 587680 | GEN-2016-074 | 345 | 6.3858 | 6.3985 | 0.0127
GEN-2020-013 | 02 - Nebraska | 640065 | AXTELL 3 | 345 | 10.1686 | 10.2613 | 0.0927
GEN-2020-013 | 02 - Nebraska | 640066 | AXTELL 7 | 115 | 14.9664 | 15.3509 | 0.3845
GEN-2020-013 | 02 - Nebraska | 640093 | C.CREEK4 | 230 | 7.2474 | 7.2917 | 0.0443
GEN-2020-013 | 02 - Nebraska | 640100 | CAMBRIG7 | 115 | 4.3803 | 4.3878 | 0.0075
GEN-2020-013 | 02 - Nebraska | 640101 | CAMBRIG8 | 69 | 2.3294 | 2.3307 | 0.0013
GEN-2020-013 | 02 - Nebraska | 640102 | CANADAY4 | 230 | 6.3291 | 6.377 | 0.0479
GEN-2020-013 | 02 - Nebraska | 640103 | CANADAY7 | 115 | 13.6833 | 13.8539 | 0.1706
GEN-2020-013 | 02 - Nebraska | 640144 | COZAD 7 | 115 | 4.5955 | 4.6109 | 0.0154
GEN-2020-013 | 02 - Nebraska | 640145 | COZAD 8 | 69 | 3.4113 | 3.4164 | 0.0051
GEN-2020-013 | 02 - Nebraska | 640161 | ELMCRK_7 | 115 | 6.1747 | 6.2095 | 0.0348
GEN-2020-013 | 02 - Nebraska | 640162 | ELMCRK 8 | 69 | 3.8632 | 3.8714 | 0.0082
GEN-2020-013 | 02 - Nebraska | 640194 | GOSPER 7 | 115 | 4.5448 | 4.556 | 0.0112
GEN-2020-013 | 02 - Nebraska | 640196 | GOTHNBG7 | 115 | 4.4652 | 4.4762 | 0.011
GEN-2020-013 | 02 - Nebraska | 640197 | GOTHNBG8 | 69 | 2.6084 | 2.6107 | 0.0023
GEN-2020-013 | 02 - Nebraska | 640206 | GUIDE R7 | 115 | 4.3863 | 4.3912 | 0.0049
GEN-2020-013 | 02 - Nebraska | 640207 | GUIDE R8 | 69 | 2.2472 | 2.248 | 0.0008
GEN-2020-013 | 02 - Nebraska | 640215 | HASTING7 | 115 | 19.6052 | 19.6814 | 0.0762
GEN-2020-013 | 02 - Nebraska | 640222 | HILDRTH7 | 115 | 4.3963 | 4.6076 | 0.2113
GEN-2020-013 | 02 - Nebraska | 640223 | HILDRTH8 | 69 | 3.5535 | 3.6326 | 0.0791
GEN-2020-013 | 02 - Nebraska | 640224 | HOLDREG7 | 115 | 6.3098 | 7.3731 | 1.0633
GEN-2020-013 | 02 - Nebraska | 640238 | JEFFREY7 | 115 | 6.2162 | 6.2304 | 0.0142
GEN-2020-013 | 02 - Nebraska | 640240 | JOHN.1 7 | 115 | 8.4657 | 8.5373 | 0.0716
GEN-2020-013 | 02 - Nebraska | 640242 | JOHN.2 7 | 115 | 12.6592 | 12.8408 | 0.1816
GEN-2020-013 | 02 - Nebraska | 640244 | JOHN.LK7 | 115 | 8.8798 | 8.9602 | 0.0804
GEN-2020-013 | 02 - Nebraska | 640245 | JOHN.LK8 | 69 | 4.2781 | 4.2893 | 0.0112
GEN-2020-013 | 02 - Nebraska | 640248 | KEAR.NE7 | 115 | 9.7848 | 9.8583 | 0.0735
GEN-2020-013 | 02 - Nebraska | 640250 | KEARNEY7 | 115 | 12.4297 | 12.5742 | 0.1445
GEN-2020-013 | 02 - Nebraska | 640256 | LXNGTN 7 | 115 | 7.1576 | 7.1992 | 0.0416
GEN-2020-013 | 02 - Nebraska | 640257 | LEXNGTN8 | 69 | 3.7569 | 3.7639 | 0.007
GEN-2020-013 | 02 - Nebraska | 640261 | LOWELL 7 | 115 | 8.4602 | 8.5249 | 0.0647
GEN-2020-013 | 02 - Nebraska | 640262 | LOWELL 8 | 69 | 4.2181 | 4.2276 | 0.0095
GEN-2020-013 | 02 - Nebraska | 640269 | MCCOOK 7 | 115 | 9.8616 | 9.8678 | 0.0062
GEN-2020-013 | 02 - Nebraska | 640270 | MCCOOK 8 | 69 | 4.7614 | 4.7622 | 0.0008
GEN-2020-013 | 02 - Nebraska | 640275 | MINDEN 7 | 115 | 7.4794 | 7.5496 | 0.0702
GEN-2020-013 | 02 - Nebraska | 640310 | ORLEANS7 | 115 | 2.4657 | 2.6251 | 0.1594
GEN-2020-013 | 02 - Nebraska | 640311 | ORLEANS8 | 69 | 2.4687 | 2.5613 | 0.0926
GEN-2020-013 | 02 - Nebraska | 640312 | PAULINE3 | 345 | 8.4266 | 8.4754 | 0.0488
GEN-2020-013 | 02 - Nebraska | 640313 | PAULINE7 | 115 | 16.8881 | 17.0184 | 0.1303
GEN-2020-013 | 02 - Nebraska | 640314 | PAULINE8 | 69 | 4.9404 | 4.9471 | 0.0067
GEN-2020-013 | 02 - Nebraska | 640321 | PROSSER7 | 115 | 6.9767 | 7.0008 | 0.0241
GEN-2020-013 | 02 - Nebraska | 640322 | PROSSER8 | 69 | 3.8945 | 3.899 | 0.0045
GEN-2020-013 | 02 - Nebraska | 640331 | RIVERDL7 | 115 | 13.3381 | 13.4338 | 0.0957
GEN-2020-013 | 02 - Nebraska | 640332 | RIVERDL8 | 69 | 6.7078 | 6.7222 | 0.0144
GEN-2020-013 | 02 - Nebraska | 640374 | SWEET W3 | 345 | 11.2769 | 11.3183 | 0.0414
GEN-2020-013 | 02 - Nebraska | 640383 | TOWER 7 | 115 | 9.406 | 9.4753 | 0.0693
GEN-2020-013 | 02 - Nebraska | 640407 | WESTMIN7 | 115 | 8.066 | 8.1328 | 0.0668
GEN-2020-013 | 02 - Nebraska | 640448 | HOLDREGE 8 | 69 | 3.8342 | 4.0418 | 0.2076
GEN-2020-013 | 02 - Nebraska | 640525 | TOBIAS 3 | 345 | 12.3465 | 12.364 | 0.0175
GEN-2020-013 | 02 - Nebraska | 640583 | ROSEMONT 7 | 115 | 6.7871 | 6.8024 | 0.0153
GEN-2020-013 | 02 - Nebraska | 640584 | COTTONWD 7 | 115 | 5.4813 | 5.4908 | 0.0095
GEN-2020-013 | 02 - Nebraska | 641087 | EGYCNTR7 | 115 | 18.2115 | 18.2671 | 0.0556
GEN-2020-013 | 02 - Nebraska | 641088 | HASTCTY7 | 115 | 19.6052 | 19.6814 | 0.0762
GEN-2020-013 | 02 - Nebraska | 761292 | GEN-2017-181 | 345 | 7.0047 | 7.0097 | 0.005
GEN-2020-013 | 02 - Nebraska | 761313 | GEN-2017-182 | 345 | 5.8487 | 5.8522 | 0.0035
GEN-2020-013 | 02 - Nebraska | 764420 | GEN-2020-011 | 345 | 9.7448 | 9.8084 | 0.0636
GEN-2020-013 | 02 - Nebraska | 764430 | G20-011-TAP | 345 | 9.7448 | 9.8084 | 0.0636
GEN-2020-013 | 02 - Nebraska | 764431 | G20-011-SS1 | 345 | 9.7345 | 9.798 | 0.0635
GEN-2020-013 | 02 - Nebraska | 764432 | G20-011-SS2 | 345 | 9.6236 | 9.6857 | 0.0621
GEN-2020-013 | 02 - Nebraska | 764433 | G20-011-SS3 | 345 | 9.6592 | 9.7217 | 0.0625
GEN-2020-013 | 02 - Nebraska | 764434 | G20-011-SS4 | 345 | 9.467 | 9.5271 | 0.0601
GEN-2020-013 | 02 - Nebraska | 764435 | GEN-2020-013 | 115 | 6.1102 | 7.1777 | 1.0675
GEN-2020-013 | 02 - Nebraska | 764445 | G20-013-TAP | 115 | 6.1209 | 7.188 | 1.0671
GEN-2020-013 | 02 - Nebraska | 764446 | G20-013-SS1 | 115 | 6.0953 | 7.1592 | 1.0639
GEN-2020-013 | 02 - Nebraska | 764447 | G20-013-SS2 | 115 | 5.8256 | 6.8641 | 1.0385
GEN-2020-013 | 02 - Nebraska | 764448 | G20-013-SS3 | 115 | 5.7718 | 6.7973 | 1.0255
GEN-2020-013 | 02 - Nebraska | 765025 | GEN-2020-070 | 345 | 6.8806 | 6.8887 | 0.0081
GEN-2020-013 | 02 - Nebraska | 765035 | G20-070-TAP | 345 | 6.8806 | 6.8887 | 0.0081
GEN-2020-025 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.5211 | 30.5745 | 0.0534
GEN-2020-025 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.427 | 23.4917 | 0.0647
GEN-2020-025 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.2485 | 30.4229 | 0.1744
GEN-2020-025 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.4844 | 33.718 | 0.2336
GEN-2020-025 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.6037 | 35.7822 | 0.1785
GEN-2020-025 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30.0585 | 30.0963 | 0.0378
GEN-2020-025 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.1208 | 26.2179 | 0.0971
GEN-2020-025 | 02 - Nebraska | 645740 | S3740 3 | 345 | 24.3048 | 24.3832 | 0.0784
GEN-2020-025 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.8518 | 24.0017 | 0.1499
GEN-2020-025 | 02 - Nebraska | 646214 | S1214 5 | 161 | 12.9069 | 12.9523 | 0.0454
GEN-2020-025 | 02 - Nebraska | 646221 | S1221 5 | 161 | 36.1727 | 36.3278 | 0.1551
GEN-2020-025 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.0481 | 44.2376 | 0.1895
GEN-2020-025 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26.9153 | 26.9988 | 0.0835
GEN-2020-025 | 02 - Nebraska | 646233 | S1233 5 | 161 | 29.9918 | 30.1276 | 0.1358
GEN-2020-025 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27.3916 | 27.4924 | 0.1008
GEN-2020-025 | 02 - Nebraska | 646249 | S1249 5 | 161 | 26.0699 | 26.2201 | 0.1502
GEN-2020-025 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.2406 | 33.3039 | 0.0633
GEN-2020-025 | 02 - Nebraska | 646253 | S1253 5 | 161 | 28.1974 | 28.3027 | 0.1053
GEN-2020-025 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.4801 | 34.7844 | 0.3043
GEN-2020-025 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.4419 | 50.8724 | 0.4305
GEN-2020-025 | 02 - Nebraska | 646256 | S1256 5 | 161 | 23.3596 | 23.458 | 0.0984
GEN-2020-025 | 02 - Nebraska | 646259 | S1259 5 | 161 | 40.0221 | 40.3943 | 0.3722
GEN-2020-025 | 02 - Nebraska | 646260 | S1260 5 | 161 | 42.2669 | 42.944 | 0.6771
GEN-2020-025 | 02 - Nebraska | 646278 | S1278 5 | 161 | 28.0861 | 28.2329 | 0.1468
GEN-2020-025 | 02 - Nebraska | 646281 | S1281 5 | 161 | 40.1621 | 40.8654 | 0.7033
GEN-2020-025 | 02 - Nebraska | 646287 | S1287 5 | 161 | 23.4658 | 23.6795 | 0.2137
GEN-2020-025 | 02 - Nebraska | 646361 | S1361 5 | 161 | 43.6863 | 44.3845 | 0.6982
GEN-2020-025 | 02 - Nebraska | 646362 | S1362 5 | 161 | 40.75 | 41.4833 | 0.7333
GEN-2020-025 | 02 - Nebraska | 646363 | S1363 5 | 161 | 36.8741 | 37.9198 | 1.0457
GEN-2020-025 | 02 - Nebraska | 647014 | S914A 8 | 69 | 11.7325 | 11.7437 | 0.0112
GEN-2020-025 | 02 - Nebraska | 647079 | 979TP 8 | 69 | 7.0376 | 7.0421 | 0.0045
GEN-2020-025 | 02 - Nebraska | 647100 | ASH GRV8 | 69 | 6.9529 | 6.9562 | 0.0033
GEN-2020-025 | 02 - Nebraska | 647846 | S6846 8 | 69 | 8.052 | 8.0553 | 0.0033
GEN-2020-025 | 02 - Nebraska | 647900 | S900 8 | 69 | 8.1047 | 8.1092 | 0.0045
GEN-2020-025 | 02 - Nebraska | 647914 | S914 8 | 69 | 7.9106 | 7.9155 | 0.0049
GEN-2020-025 | 02 - Nebraska | 647921 | S921 8 | 69 | 26.534 | 26.5599 | 0.0259
GEN-2020-025 | 02 - Nebraska | 647960 | S960 8 | 69 | 7.4844 | 7.4904 | 0.006
GEN-2020-025 | 02 - Nebraska | 647979 | S979 8 | 69 | 6.8877 | 6.8921 | 0.0044
GEN-2020-025 | 02 - Nebraska | 647988 | S988 8 | 69 | 2.9098 | 2.9105 | 0.0007
GEN-2020-025 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17.8278 | 17.8395 | 0.0117
GEN-2020-025 | 02 - Nebraska | 650169 | 70&BLUFF 5 | 161 | 8.9344 | 8.9442 | 0.0098
GEN-2020-025 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.4484 | 21.476 | 0.0276
GEN-2020-025 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21.344 | 21.3651 | 0.0211
GEN-2020-025 | 02 - Nebraska | 650269 | 70&BLUFF 7 | 115 | 25.724 | 25.7389 | 0.0149
GEN-2020-025 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32.4036 | 32.4229 | 0.0193
GEN-2020-025 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.372 | 22.4309 | 0.0589
GEN-2020-025 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 24.3032 | 24.3816 | 0.0784
GEN-2020-025 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.7679 | 17.7927 | 0.0248
GEN-2020-025 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.4013 | 17.425 | 0.0237
GEN-2020-025 | 02 - Nebraska | 764570 | GEN-2020-002 | 69 | 8.052 | 8.0553 | 0.0033
GEN-2020-025 | 02 - Nebraska | 764600 | GEN-2020-025 | 161 | 36.8741 | 37.9198 | 1.0457
GEN-2020-025 | 02 - Nebraska | 764615 | GEN-2020-027 | 161 | 36.2204 | 37.2285 | 1.0081
GEN-2020-025 | 02 - Nebraska | 764630 | GEN-2020-028 | 161 | 36.8741 | 37.9198 | 1.0457
GEN-2020-025 | 02 - Nebraska | 764660 | GEN-2020-031 | 161 | 36.8741 | 37.9198 | 1.0457
GEN-2020-025 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 24.0277 | 24.1043 | 0.0766
GEN-2020-025 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 24.3048 | 24.3832 | 0.0784
GEN-2020-027 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.5663 | 30.5745 | 0.0082
GEN-2020-027 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.4818 | 23.4917 | 0.0099
GEN-2020-027 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.396 | 30.4229 | 0.0269
GEN-2020-027 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.682 | 33.718 | 0.036
GEN-2020-027 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.7547 | 35.7822 | 0.0275
GEN-2020-027 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30.0905 | 30.0963 | 0.0058
GEN-2020-027 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.203 | 26.2179 | 0.0149
GEN-2020-027 | 02 - Nebraska | 645740 | S3740 3 | 345 | 24.3712 | 24.3832 | 0.012
GEN-2020-027 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.9786 | 24.0017 | 0.0231
GEN-2020-027 | 02 - Nebraska | 646214 | S1214 5 | 161 | 12.9453 | 12.9523 | 0.007
GEN-2020-027 | 02 - Nebraska | 646221 | S1221 5 | 161 | 36.304 | 36.3278 | 0.0238
GEN-2020-027 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.2085 | 44.2376 | 0.0291
GEN-2020-027 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26.986 | 26.9988 | 0.0128
GEN-2020-027 | 02 - Nebraska | 646233 | S1233 5 | 161 | 30.1068 | 30.1276 | 0.0208
GEN-2020-027 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27.4769 | 27.4924 | 0.0155
GEN-2020-027 | 02 - Nebraska | 646249 | S1249 5 | 161 | 26.1969 | 26.2201 | 0.0232
GEN-2020-027 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.2942 | 33.3039 | 0.0097
GEN-2020-027 | 02 - Nebraska | 646253 | S1253 5 | 161 | 28.2866 | 28.3027 | 0.0161
GEN-2020-027 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.7375 | 34.7844 | 0.0469
GEN-2020-027 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.8059 | 50.8724 | 0.0665
GEN-2020-027 | 02 - Nebraska | 646256 | S1256 5 | 161 | 23.4429 | 23.458 | 0.0151
GEN-2020-027 | 02 - Nebraska | 646259 | S1259 5 | 161 | 40.3368 | 40.3943 | 0.0575
GEN-2020-027 | 02 - Nebraska | 646260 | S1260 5 | 161 | 42.8388 | 42.944 | 0.1052
GEN-2020-027 | 02 - Nebraska | 646278 | S1278 5 | 161 | 28.2103 | 28.2329 | 0.0226
GEN-2020-027 | 02 - Nebraska | 646281 | S1281 5 | 161 | 40.756 | 40.8654 | 0.1094
GEN-2020-027 | 02 - Nebraska | 646287 | S1287 5 | 161 | 23.6465 | 23.6795 | 0.033
GEN-2020-027 | 02 - Nebraska | 646361 | S1361 5 | 161 | 44.276 | 44.3845 | 0.1085
GEN-2020-027 | 02 - Nebraska | 646362 | S1362 5 | 161 | 41.3692 | 41.4833 | 0.1141
GEN-2020-027 | 02 - Nebraska | 646363 | S1363 5 | 161 | 37.7557 | 37.9198 | 0.1641
GEN-2020-027 | 02 - Nebraska | 647014 | S914A 8 | 69 | 11.742 | 11.7437 | 0.0017
GEN-2020-027 | 02 - Nebraska | 647079 | 979TP 8 | 69 | 7.0414 | 7.0421 | 0.0007
GEN-2020-027 | 02 - Nebraska | 647100 | ASH GRV8 | 69 | 6.9557 | 6.9562 | 0.0005
GEN-2020-027 | 02 - Nebraska | 647846 | S6846 8 | 69 | 8.0548 | 8.0553 | 0.0005
GEN-2020-027 | 02 - Nebraska | 647900 | S900 8 | 69 | 8.1085 | 8.1092 | 0.0007
GEN-2020-027 | 02 - Nebraska | 647914 | S914 8 | 69 | 7.9148 | 7.9155 | 0.0007
GEN-2020-027 | 02 - Nebraska | 647921 | S921 8 | 69 | 26.556 | 26.5599 | 0.0039
GEN-2020-027 | 02 - Nebraska | 647960 | S960 8 | 69 | 7.4894 | 7.4904 | 0.001
GEN-2020-027 | 02 - Nebraska | 647979 | S979 8 | 69 | 6.8914 | 6.8921 | 0.0007
GEN-2020-027 | 02 - Nebraska | 647988 | S988 8 | 69 | 2.9104 | 2.9105 | 0.0001
GEN-2020-027 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17.8377 | 17.8395 | 0.0018
GEN-2020-027 | 02 - Nebraska | 650169 | 70&BLUFF 5 | 161 | 8.9427 | 8.9442 | 0.0015
GEN-2020-027 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.4717 | 21.476 | 0.0043
GEN-2020-027 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21.3618 | 21.3651 | 0.0033
GEN-2020-027 | 02 - Nebraska | 650269 | 70&BLUFF 7 | 115 | 25.7366 | 25.7389 | 0.0023
GEN-2020-027 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32.4199 | 32.4229 | 0.003
GEN-2020-027 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.4219 | 22.4309 | 0.009
GEN-2020-027 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 24.3695 | 24.3816 | 0.0121
GEN-2020-027 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.7889 | 17.7927 | 0.0038
GEN-2020-027 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.4214 | 17.425 | 0.0036
GEN-2020-027 | 02 - Nebraska | 764570 | GEN-2020-002 | 69 | 8.0548 | 8.0553 | 0.0005
GEN-2020-027 | 02 - Nebraska | 764600 | GEN-2020-025 | 161 | 37.7557 | 37.9198 | 0.1641
GEN-2020-027 | 02 - Nebraska | 764615 | GEN-2020-027 | 161 | 37.0643 | 37.2285 | 0.1642
GEN-2020-027 | 02 - Nebraska | 764630 | GEN-2020-028 | 161 | 37.7557 | 37.9198 | 0.1641
GEN-2020-027 | 02 - Nebraska | 764660 | GEN-2020-031 | 161 | 37.7557 | 37.9198 | 0.1641
GEN-2020-027 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 24.0925 | 24.1043 | 0.0118
GEN-2020-027 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 24.3712 | 24.3832 | 0.012
GEN-2020-028 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.5211 | 30.5745 | 0.0534
GEN-2020-028 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.427 | 23.4917 | 0.0647
GEN-2020-028 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.2485 | 30.4229 | 0.1744
GEN-2020-028 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.4844 | 33.718 | 0.2336
GEN-2020-028 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.6037 | 35.7822 | 0.1785
GEN-2020-028 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30.0585 | 30.0963 | 0.0378
GEN-2020-028 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.1208 | 26.2179 | 0.0971
GEN-2020-028 | 02 - Nebraska | 645740 | S3740 3 | 345 | 24.3048 | 24.3832 | 0.0784
GEN-2020-028 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.8518 | 24.0017 | 0.1499
GEN-2020-028 | 02 - Nebraska | 646214 | S1214 5 | 161 | 12.9069 | 12.9523 | 0.0454
GEN-2020-028 | 02 - Nebraska | 646221 | S1221 5 | 161 | 36.1727 | 36.3278 | 0.1551
GEN-2020-028 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.0481 | 44.2376 | 0.1895
GEN-2020-028 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26.9153 | 26.9988 | 0.0835
GEN-2020-028 | 02 - Nebraska | 646233 | S1233 5 | 161 | 29.9918 | 30.1276 | 0.1358
GEN-2020-028 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27.3916 | 27.4924 | 0.1008
GEN-2020-028 | 02 - Nebraska | 646249 | S1249 5 | 161 | 26.0699 | 26.2201 | 0.1502
GEN-2020-028 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.2406 | 33.3039 | 0.0633
GEN-2020-028 | 02 - Nebraska | 646253 | S1253 5 | 161 | 28.1974 | 28.3027 | 0.1053
GEN-2020-028 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.4801 | 34.7844 | 0.3043
GEN-2020-028 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.4419 | 50.8724 | 0.4305
GEN-2020-028 | 02 - Nebraska | 646256 | S1256 5 | 161 | 23.3596 | 23.458 | 0.0984
GEN-2020-028 | 02 - Nebraska | 646259 | S1259 5 | 161 | 40.0221 | 40.3943 | 0.3722
GEN-2020-028 | 02 - Nebraska | 646260 | S1260 5 | 161 | 42.2669 | 42.944 | 0.6771
GEN-2020-028 | 02 - Nebraska | 646278 | S1278 5 | 161 | 28.0861 | 28.2329 | 0.1468
GEN-2020-028 | 02 - Nebraska | 646281 | S1281 5 | 161 | 40.1621 | 40.8654 | 0.7033
GEN-2020-028 | 02 - Nebraska | 646287 | S1287 5 | 161 | 23.4658 | 23.6795 | 0.2137
GEN-2020-028 | 02 - Nebraska | 646361 | S1361 5 | 161 | 43.6863 | 44.3845 | 0.6982
GEN-2020-028 | 02 - Nebraska | 646362 | S1362 5 | 161 | 40.75 | 41.4833 | 0.7333
GEN-2020-028 | 02 - Nebraska | 646363 | S1363 5 | 161 | 36.8741 | 37.9198 | 1.0457
GEN-2020-028 | 02 - Nebraska | 647014 | S914A 8 | 69 | 11.7325 | 11.7437 | 0.0112
GEN-2020-028 | 02 - Nebraska | 647079 | 979TP 8 | 69 | 7.0376 | 7.0421 | 0.0045
GEN-2020-028 | 02 - Nebraska | 647100 | ASH GRV8 | 69 | 6.9529 | 6.9562 | 0.0033
GEN-2020-028 | 02 - Nebraska | 647846 | S6846 8 | 69 | 8.052 | 8.0553 | 0.0033
GEN-2020-028 | 02 - Nebraska | 647900 | S900 8 | 69 | 8.1047 | 8.1092 | 0.0045
GEN-2020-028 | 02 - Nebraska | 647914 | S914 8 | 69 | 7.9106 | 7.9155 | 0.0049
GEN-2020-028 | 02 - Nebraska | 647921 | S921 8 | 69 | 26.534 | 26.5599 | 0.0259
GEN-2020-028 | 02 - Nebraska | 647960 | S960 8 | 69 | 7.4844 | 7.4904 | 0.006
GEN-2020-028 | 02 - Nebraska | 647979 | S979 8 | 69 | 6.8877 | 6.8921 | 0.0044
GEN-2020-028 | 02 - Nebraska | 647988 | S988 8 | 69 | 2.9098 | 2.9105 | 0.0007
GEN-2020-028 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17.8278 | 17.8395 | 0.0117
GEN-2020-028 | 02 - Nebraska | 650169 | 70&BLUFF 5 | 161 | 8.9344 | 8.9442 | 0.0098
GEN-2020-028 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.4484 | 21.476 | 0.0276
GEN-2020-028 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21.344 | 21.3651 | 0.0211
GEN-2020-028 | 02 - Nebraska | 650269 | 70&BLUFF 7 | 115 | 25.724 | 25.7389 | 0.0149
GEN-2020-028 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32.4036 | 32.4229 | 0.0193
GEN-2020-028 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.372 | 22.4309 | 0.0589
GEN-2020-028 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 24.3032 | 24.3816 | 0.0784
GEN-2020-028 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.7679 | 17.7927 | 0.0248
GEN-2020-028 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.4013 | 17.425 | 0.0237
GEN-2020-028 | 02 - Nebraska | 764570 | GEN-2020-002 | 69 | 8.052 | 8.0553 | 0.0033
GEN-2020-028 | 02 - Nebraska | 764600 | GEN-2020-025 | 161 | 36.8741 | 37.9198 | 1.0457
GEN-2020-028 | 02 - Nebraska | 764615 | GEN-2020-027 | 161 | 36.2204 | 37.2285 | 1.0081
GEN-2020-028 | 02 - Nebraska | 764630 | GEN-2020-028 | 161 | 36.8741 | 37.9198 | 1.0457
GEN-2020-028 | 02 - Nebraska | 764660 | GEN-2020-031 | 161 | 36.8741 | 37.9198 | 1.0457
GEN-2020-028 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 24.0277 | 24.1043 | 0.0766
GEN-2020-028 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 24.3048 | 24.3832 | 0.0784
GEN-2020-030 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.5665 | 30.5745 | 0.008
GEN-2020-030 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.482 | 23.4917 | 0.0097
GEN-2020-030 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.3967 | 30.4229 | 0.0262
GEN-2020-030 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.6829 | 33.718 | 0.0351
GEN-2020-030 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.7555 | 35.7822 | 0.0267
GEN-2020-030 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30.0907 | 30.0963 | 0.0056
GEN-2020-030 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.2034 | 26.2179 | 0.0145
GEN-2020-030 | 02 - Nebraska | 645740 | S3740 3 | 345 | 24.3715 | 24.3832 | 0.0117
GEN-2020-030 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.9792 | 24.0017 | 0.0225
GEN-2020-030 | 02 - Nebraska | 646214 | S1214 5 | 161 | 12.9455 | 12.9523 | 0.0068
GEN-2020-030 | 02 - Nebraska | 646221 | S1221 5 | 161 | 36.3046 | 36.3278 | 0.0232
GEN-2020-030 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.2092 | 44.2376 | 0.0284
GEN-2020-030 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26.9863 | 26.9988 | 0.0125
GEN-2020-030 | 02 - Nebraska | 646233 | S1233 5 | 161 | 30.1073 | 30.1276 | 0.0203
GEN-2020-030 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27.4773 | 27.4924 | 0.0151
GEN-2020-030 | 02 - Nebraska | 646249 | S1249 5 | 161 | 26.1976 | 26.2201 | 0.0225
GEN-2020-030 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.2944 | 33.3039 | 0.0095
GEN-2020-030 | 02 - Nebraska | 646253 | S1253 5 | 161 | 28.287 | 28.3027 | 0.0157
GEN-2020-030 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.7387 | 34.7844 | 0.0457
GEN-2020-030 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.8077 | 50.8724 | 0.0647
GEN-2020-030 | 02 - Nebraska | 646256 | S1256 5 | 161 | 23.4433 | 23.458 | 0.0147
GEN-2020-030 | 02 - Nebraska | 646259 | S1259 5 | 161 | 40.3383 | 40.3943 | 0.056
GEN-2020-030 | 02 - Nebraska | 646260 | S1260 5 | 161 | 42.8416 | 42.944 | 0.1024
GEN-2020-030 | 02 - Nebraska | 646278 | S1278 5 | 161 | 28.2109 | 28.2329 | 0.022
GEN-2020-030 | 02 - Nebraska | 646281 | S1281 5 | 161 | 40.7589 | 40.8654 | 0.1065
GEN-2020-030 | 02 - Nebraska | 646287 | S1287 5 | 161 | 23.6474 | 23.6795 | 0.0321
GEN-2020-030 | 02 - Nebraska | 646361 | S1361 5 | 161 | 44.2789 | 44.3845 | 0.1056
GEN-2020-030 | 02 - Nebraska | 646362 | S1362 5 | 161 | 41.3723 | 41.4833 | 0.111
GEN-2020-030 | 02 - Nebraska | 646363 | S1363 5 | 161 | 37.7601 | 37.9198 | 0.1597
GEN-2020-030 | 02 - Nebraska | 647014 | S914A 8 | 69 | 11.742 | 11.7437 | 0.0017
GEN-2020-030 | 02 - Nebraska | 647079 | 979TP 8 | 69 | 7.0415 | 7.0421 | 0.0006
GEN-2020-030 | 02 - Nebraska | 647100 | ASH GRV8 | 69 | 6.9557 | 6.9562 | 0.0005
GEN-2020-030 | 02 - Nebraska | 647846 | S6846 8 | 69 | 8.0548 | 8.0553 | 0.0005
GEN-2020-030 | 02 - Nebraska | 647900 | S900 8 | 69 | 8.1085 | 8.1092 | 0.0007
GEN-2020-030 | 02 - Nebraska | 647914 | S914 8 | 69 | 7.9148 | 7.9155 | 0.0007
GEN-2020-030 | 02 - Nebraska | 647921 | S921 8 | 69 | 26.5561 | 26.5599 | 0.0038
GEN-2020-030 | 02 - Nebraska | 647960 | S960 8 | 69 | 7.4895 | 7.4904 | 0.0009
GEN-2020-030 | 02 - Nebraska | 647979 | S979 8 | 69 | 6.8915 | 6.8921 | 0.0006
GEN-2020-030 | 02 - Nebraska | 647988 | S988 8 | 69 | 2.9104 | 2.9105 | 0.0001
GEN-2020-030 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17.8377 | 17.8395 | 0.0018
GEN-2020-030 | 02 - Nebraska | 650169 | 70&BLUFF 5 | 161 | 8.9428 | 8.9442 | 0.0014
GEN-2020-030 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.4718 | 21.476 | 0.0042
GEN-2020-030 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21.3619 | 21.3651 | 0.0032
GEN-2020-030 | 02 - Nebraska | 650269 | 70&BLUFF 7 | 115 | 25.7367 | 25.7389 | 0.0022
GEN-2020-030 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32.42 | 32.4229 | 0.0029
GEN-2020-030 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.4221 | 22.4309 | 0.0088
GEN-2020-030 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 24.3698 | 24.3816 | 0.0118
GEN-2020-030 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.789 | 17.7927 | 0.0037
GEN-2020-030 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.4215 | 17.425 | 0.0035
GEN-2020-030 | 02 - Nebraska | 764570 | GEN-2020-002 | 69 | 8.0548 | 8.0553 | 0.0005
GEN-2020-030 | 02 - Nebraska | 764600 | GEN-2020-025 | 161 | 37.7601 | 37.9198 | 0.1597
GEN-2020-030 | 02 - Nebraska | 764615 | GEN-2020-027 | 161 | 37.0687 | 37.2285 | 0.1598
GEN-2020-030 | 02 - Nebraska | 764630 | GEN-2020-028 | 161 | 37.7601 | 37.9198 | 0.1597
GEN-2020-030 | 02 - Nebraska | 764660 | GEN-2020-031 | 161 | 37.7601 | 37.9198 | 0.1597
GEN-2020-030 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 24.0928 | 24.1043 | 0.0115
GEN-2020-030 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 24.3715 | 24.3832 | 0.0117
GEN-2020-031 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.5145 | 30.5745 | 0.06
GEN-2020-031 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.419 | 23.4917 | 0.0727
GEN-2020-031 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.227 | 30.4229 | 0.1959
GEN-2020-031 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.4556 | 33.718 | 0.2624
GEN-2020-031 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.5817 | 35.7822 | 0.2005
GEN-2020-031 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30.0538 | 30.0963 | 0.0425
GEN-2020-031 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.1088 | 26.2179 | 0.1091
GEN-2020-031 | 02 - Nebraska | 645740 | S3740 3 | 345 | 24.2951 | 24.3832 | 0.0881
GEN-2020-031 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.8334 | 24.0017 | 0.1683
GEN-2020-031 | 02 - Nebraska | 646214 | S1214 5 | 161 | 12.9012 | 12.9523 | 0.0511
GEN-2020-031 | 02 - Nebraska | 646221 | S1221 5 | 161 | 36.1536 | 36.3278 | 0.1742
GEN-2020-031 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.0247 | 44.2376 | 0.2129
GEN-2020-031 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26.9049 | 26.9988 | 0.0939
GEN-2020-031 | 02 - Nebraska | 646233 | S1233 5 | 161 | 29.9751 | 30.1276 | 0.1525
GEN-2020-031 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27.3791 | 27.4924 | 0.1133
GEN-2020-031 | 02 - Nebraska | 646249 | S1249 5 | 161 | 26.0514 | 26.2201 | 0.1687
GEN-2020-031 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.2327 | 33.3039 | 0.0712
GEN-2020-031 | 02 - Nebraska | 646253 | S1253 5 | 161 | 28.1844 | 28.3027 | 0.1183
GEN-2020-031 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.4427 | 34.7844 | 0.3417
GEN-2020-031 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.389 | 50.8724 | 0.4834
GEN-2020-031 | 02 - Nebraska | 646256 | S1256 5 | 161 | 23.3475 | 23.458 | 0.1105
GEN-2020-031 | 02 - Nebraska | 646259 | S1259 5 | 161 | 39.9764 | 40.3943 | 0.4179
GEN-2020-031 | 02 - Nebraska | 646260 | S1260 5 | 161 | 42.1844 | 42.944 | 0.7596
GEN-2020-031 | 02 - Nebraska | 646278 | S1278 5 | 161 | 28.068 | 28.2329 | 0.1649
GEN-2020-031 | 02 - Nebraska | 646281 | S1281 5 | 161 | 40.0765 | 40.8654 | 0.7889
GEN-2020-031 | 02 - Nebraska | 646287 | S1287 5 | 161 | 23.4395 | 23.6795 | 0.24
GEN-2020-031 | 02 - Nebraska | 646361 | S1361 5 | 161 | 43.6012 | 44.3845 | 0.7833
GEN-2020-031 | 02 - Nebraska | 646362 | S1362 5 | 161 | 40.6608 | 41.4833 | 0.8225
GEN-2020-031 | 02 - Nebraska | 646363 | S1363 5 | 161 | 36.7484 | 37.9198 | 1.1714
GEN-2020-031 | 02 - Nebraska | 647014 | S914A 8 | 69 | 11.7311 | 11.7437 | 0.0126
GEN-2020-031 | 02 - Nebraska | 647079 | 979TP 8 | 69 | 7.037 | 7.0421 | 0.0051
GEN-2020-031 | 02 - Nebraska | 647100 | ASH GRV8 | 69 | 6.9525 | 6.9562 | 0.0037
GEN-2020-031 | 02 - Nebraska | 647846 | S6846 8 | 69 | 8.0515 | 8.0553 | 0.0038
GEN-2020-031 | 02 - Nebraska | 647900 | S900 8 | 69 | 8.1041 | 8.1092 | 0.0051
GEN-2020-031 | 02 - Nebraska | 647914 | S914 8 | 69 | 7.91 | 7.9155 | 0.0055
GEN-2020-031 | 02 - Nebraska | 647921 | S921 8 | 69 | 26.5308 | 26.5599 | 0.0291
GEN-2020-031 | 02 - Nebraska | 647960 | S960 8 | 69 | 7.4836 | 7.4904 | 0.0068
GEN-2020-031 | 02 - Nebraska | 647979 | S979 8 | 69 | 6.8872 | 6.8921 | 0.0049
GEN-2020-031 | 02 - Nebraska | 647988 | S988 8 | 69 | 2.9097 | 2.9105 | 0.0008
GEN-2020-031 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17.8264 | 17.8395 | 0.0131
GEN-2020-031 | 02 - Nebraska | 650169 | 70&BLUFF 5 | 161 | 8.9332 | 8.9442 | 0.011
GEN-2020-031 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.4449 | 21.476 | 0.0311
GEN-2020-031 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21.3414 | 21.3651 | 0.0237
GEN-2020-031 | 02 - Nebraska | 650269 | 70&BLUFF 7 | 115 | 25.7221 | 25.7389 | 0.0168
GEN-2020-031 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32.4012 | 32.4229 | 0.0217
GEN-2020-031 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.3647 | 22.4309 | 0.0662
GEN-2020-031 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 24.2935 | 24.3816 | 0.0881
GEN-2020-031 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.7648 | 17.7927 | 0.0279
GEN-2020-031 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.3984 | 17.425 | 0.0266
GEN-2020-031 | 02 - Nebraska | 764570 | GEN-2020-002 | 69 | 8.0515 | 8.0553 | 0.0038
GEN-2020-031 | 02 - Nebraska | 764600 | GEN-2020-025 | 161 | 36.7484 | 37.9198 | 1.1714
GEN-2020-031 | 02 - Nebraska | 764615 | GEN-2020-027 | 161 | 36.0991 | 37.2285 | 1.1294
GEN-2020-031 | 02 - Nebraska | 764630 | GEN-2020-028 | 161 | 36.7484 | 37.9198 | 1.1714
GEN-2020-031 | 02 - Nebraska | 764660 | GEN-2020-031 | 161 | 36.7484 | 37.9198 | 1.1714
GEN-2020-031 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 24.0182 | 24.1043 | 0.0861
GEN-2020-031 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 24.2951 | 24.3832 | 0.0881
GEN-2020-033 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.5665 | 30.5745 | 0.008
GEN-2020-033 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.482 | 23.4917 | 0.0097
GEN-2020-033 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.3968 | 30.4229 | 0.0261
GEN-2020-033 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.6829 | 33.718 | 0.0351
GEN-2020-033 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.7555 | 35.7822 | 0.0267
GEN-2020-033 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30.0907 | 30.0963 | 0.0056
GEN-2020-033 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.2034 | 26.2179 | 0.0145
GEN-2020-033 | 02 - Nebraska | 645740 | S3740 3 | 345 | 24.3715 | 24.3832 | 0.0117
GEN-2020-033 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.9792 | 24.0017 | 0.0225
GEN-2020-033 | 02 - Nebraska | 646214 | S1214 5 | 161 | 12.9455 | 12.9523 | 0.0068
GEN-2020-033 | 02 - Nebraska | 646221 | S1221 5 | 161 | 36.3046 | 36.3278 | 0.0232
GEN-2020-033 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.2093 | 44.2376 | 0.0283
GEN-2020-033 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26.9863 | 26.9988 | 0.0125
GEN-2020-033 | 02 - Nebraska | 646233 | S1233 5 | 161 | 30.1073 | 30.1276 | 0.0203
GEN-2020-033 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27.4773 | 27.4924 | 0.0151
GEN-2020-033 | 02 - Nebraska | 646249 | S1249 5 | 161 | 26.1976 | 26.2201 | 0.0225
GEN-2020-033 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.2944 | 33.3039 | 0.0095
GEN-2020-033 | 02 - Nebraska | 646253 | S1253 5 | 161 | 28.287 | 28.3027 | 0.0157
GEN-2020-033 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.7388 | 34.7844 | 0.0456
GEN-2020-033 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.8078 | 50.8724 | 0.0646
GEN-2020-033 | 02 - Nebraska | 646256 | S1256 5 | 161 | 23.4433 | 23.458 | 0.0147
GEN-2020-033 | 02 - Nebraska | 646259 | S1259 5 | 161 | 40.3384 | 40.3943 | 0.0559
GEN-2020-033 | 02 - Nebraska | 646260 | S1260 5 | 161 | 42.8417 | 42.944 | 0.1023
GEN-2020-033 | 02 - Nebraska | 646278 | S1278 5 | 161 | 28.2109 | 28.2329 | 0.022
GEN-2020-033 | 02 - Nebraska | 646281 | S1281 5 | 161 | 40.759 | 40.8654 | 0.1064
GEN-2020-033 | 02 - Nebraska | 646287 | S1287 5 | 161 | 23.6474 | 23.6795 | 0.0321
GEN-2020-033 | 02 - Nebraska | 646361 | S1361 5 | 161 | 44.279 | 44.3845 | 0.1055
GEN-2020-033 | 02 - Nebraska | 646362 | S1362 5 | 161 | 41.3724 | 41.4833 | 0.1109
GEN-2020-033 | 02 - Nebraska | 646363 | S1363 5 | 161 | 37.7602 | 37.9198 | 0.1596
GEN-2020-033 | 02 - Nebraska | 647014 | S914A 8 | 69 | 11.742 | 11.7437 | 0.0017
GEN-2020-033 | 02 - Nebraska | 647079 | 979TP 8 | 69 | 7.0415 | 7.0421 | 0.0006
GEN-2020-033 | 02 - Nebraska | 647100 | ASH GRV8 | 69 | 6.9557 | 6.9562 | 0.0005
GEN-2020-033 | 02 - Nebraska | 647846 | S6846 8 | 69 | 8.0548 | 8.0553 | 0.0005
GEN-2020-033 | 02 - Nebraska | 647900 | S900 8 | 69 | 8.1085 | 8.1092 | 0.0007
GEN-2020-033 | 02 - Nebraska | 647914 | S914 8 | 69 | 7.9148 | 7.9155 | 0.0007
GEN-2020-033 | 02 - Nebraska | 647921 | S921 8 | 69 | 26.5561 | 26.5599 | 0.0038
GEN-2020-033 | 02 - Nebraska | 647960 | S960 8 | 69 | 7.4895 | 7.4904 | 0.0009
GEN-2020-033 | 02 - Nebraska | 647979 | S979 8 | 69 | 6.8915 | 6.8921 | 0.0006
GEN-2020-033 | 02 - Nebraska | 647988 | S988 8 | 69 | 2.9104 | 2.9105 | 0.0001
GEN-2020-033 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17.8377 | 17.8395 | 0.0018
GEN-2020-033 | 02 - Nebraska | 650169 | 70&BLUFF 5 | 161 | 8.9428 | 8.9442 | 0.0014
GEN-2020-033 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.4718 | 21.476 | 0.0042
GEN-2020-033 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21.3619 | 21.3651 | 0.0032
GEN-2020-033 | 02 - Nebraska | 650269 | 70&BLUFF 7 | 115 | 25.7367 | 25.7389 | 0.0022
GEN-2020-033 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32.42 | 32.4229 | 0.0029
GEN-2020-033 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.4222 | 22.4309 | 0.0087
GEN-2020-033 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 24.3699 | 24.3816 | 0.0117
GEN-2020-033 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.789 | 17.7927 | 0.0037
GEN-2020-033 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.4215 | 17.425 | 0.0035
GEN-2020-033 | 02 - Nebraska | 764570 | GEN-2020-002 | 69 | 8.0548 | 8.0553 | 0.0005
GEN-2020-033 | 02 - Nebraska | 764600 | GEN-2020-025 | 161 | 37.7602 | 37.9198 | 0.1596
GEN-2020-033 | 02 - Nebraska | 764615 | GEN-2020-027 | 161 | 37.0688 | 37.2285 | 0.1597
GEN-2020-033 | 02 - Nebraska | 764630 | GEN-2020-028 | 161 | 37.7602 | 37.9198 | 0.1596
GEN-2020-033 | 02 - Nebraska | 764660 | GEN-2020-031 | 161 | 37.7602 | 37.9198 | 0.1596
GEN-2020-033 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 24.0928 | 24.1043 | 0.0115
GEN-2020-033 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 24.3715 | 24.3832 | 0.0117
GEN-2020-036 | 02 - Nebraska | 45906 | J1590 SUB | 345 | 15.0027 | 15.0035 | 0.0008
GEN-2020-036 | 02 - Nebraska | 85831 | J583 | 345 | 6.0611 | 6.0619 | 0.0008
GEN-2020-036 | 02 - Nebraska | 87486 | J748GENTIE | 345 | 13.9565 | 13.9572 | 0.0007
GEN-2020-036 | 02 - Nebraska | 87487 | J748POI | 345 | 15.8407 | 15.8415 | 0.0008
GEN-2020-036 | 02 - Nebraska | 300039 | 7FAIRPT | 345 | 12.5845 | 12.5859 | 0.0014
GEN-2020-036 | 02 - Nebraska | 300076 | 5FAIRPTB2 | 161 | 16.5704 | 16.5712 | 0.0008
GEN-2020-036 | 02 - Nebraska | 301347 | 5WINSLOW | 161 | 8.8564 | 8.8566 | 0.0002
GEN-2020-036 | 02 - Nebraska | 301559 | 5FAIRPTXF3 | 161 | 16.5889 | 16.5897 | 0.0008
GEN-2020-036 | 02 - Nebraska | 541147 | ST JOE_CAP5 | 161 | 17.9668 | 17.9675 | 0.0007
GEN-2020-036 | 02 - Nebraska | 541197 | MULLNCR7 | 345 | 7.8117 | 7.8138 | 0.0021
GEN-2020-036 | 02 - Nebraska | 541199 | ST JOE 7 | 345 | 19.7437 | 19.7459 | 0.0022
GEN-2020-036 | 02 - Nebraska | 541201 | SIBLEY 7 | 345 | 21.0099 | 21.0107 | 0.0008
GEN-2020-036 | 02 - Nebraska | 541253 | ST JOE 5 | 161 | 20.05 | 20.0509 | 0.0009
GEN-2020-036 | 02 - Nebraska | 541257 | COOK 5 | 161 | 14.2257 | 14.2261 | 0.0004
GEN-2020-036 | 02 - Nebraska | 541258 | WOODBIN5 | 161 | 17.0285 | 17.0292 | 0.0007
GEN-2020-036 | 02 - Nebraska | 541394 | AVENUECTY 5 | 161 | 8.7874 | 8.7876 | 0.0002
GEN-2020-036 | 02 - Nebraska | 541400 | EASTOWN7 | 345 | 18.3305 | 18.3319 | 0.0014
GEN-2020-036 | 02 - Nebraska | 541401 | EASTOWN5 | 161 | 17.5492 | 17.5499 | 0.0007
GEN-2020-036 | 02 - Nebraska | 541411 | MC REAC1 | 345 | 7.4798 | 7.4817 | 0.0019
GEN-2020-036 | 02 - Nebraska | 541412 | MC REAC2 | 345 | 7.4798 | 7.4817 | 0.0019
GEN-2020-036 | 02 - Nebraska | 541413 | MC REAC3 | 345 | 7.4798 | 7.4817 | 0.0019
GEN-2020-036 | 02 - Nebraska | 541414 | SIB REA1 | 345 | 18.7713 | 18.7719 | 0.0006
GEN-2020-036 | 02 - Nebraska | 541500 | KETCHEM7 | 345 | 7.8124 | 7.8134 | 0.001
GEN-2020-036 | 02 - Nebraska | 541501 | OSBORN7 | 345 | 6.9726 | 6.9734 | 0.0008
GEN-2020-036 | 02 - Nebraska | 541510 | HOLT 7 | 345 | 8.9069 | 8.9106 | 0.0037
GEN-2020-036 | 02 - Nebraska | 541511 | ROCKCK7 | 345 | 6.9434 | 6.9454 | 0.002
GEN-2020-036 | 02 - Nebraska | 541517 | HOLT_REACT7 | 345 | 8.8618 | 8.8655 | 0.0037
GEN-2020-036 | 02 - Nebraska | 541543 | OUTLAW | 345 | 5.7476 | 5.749 | 0.0014
GEN-2020-036 | 02 - Nebraska | 542980 | NASHUA 7 | 345 | 22.7058 | 22.7067 | 0.0009
GEN-2020-036 | 02 - Nebraska | 542982 | IATAN 7 | 345 | 29.3717 | 29.3727 | 0.001
GEN-2020-036 | 02 - Nebraska | 560746 | G13-002-TAP | 115 | 43.5007 | 43.5193 | 0.0186
GEN-2020-036 | 02 - Nebraska | 583700 | GEN-2013-019 | 115 | 19.2006 | 19.204 | 0.0034
GEN-2020-036 | 02 - Nebraska | 585241 | GEN-2015-088 | 345 | 12.3602 | 12.364 | 0.0038
GEN-2020-036 | 02 - Nebraska | 635000 | CBLUFFS3 | 345 | 32.1516 | 32.2342 | 0.0826
GEN-2020-036 | 02 - Nebraska | 635001 | CBLUFFS5 | 161 | 39.7612 | 39.8181 | 0.0569
GEN-2020-036 | 02 - Nebraska | 635002 | CBLUFFS8 | 69 | 25.2421 | 25.2514 | 0.0093
GEN-2020-036 | 02 - Nebraska | 635011 | INDNCRK5 | 161 | 22.0284 | 22.0461 | 0.0177
GEN-2020-036 | 02 - Nebraska | 635013 | PNYCRK 3 | 345 | 29.2431 | 29.31 | 0.0669
GEN-2020-036 | 02 - Nebraska | 635014 | OVRLND 3 | 345 | 27.4424 | 27.5003 | 0.0579
GEN-2020-036 | 02 - Nebraska | 635015 | OVRLND 5 | 161 | 31.5331 | 31.5672 | 0.0341
GEN-2020-036 | 02 - Nebraska | 635016 | STHLND 3 | 345 | 29.2083 | 29.2751 | 0.0668
GEN-2020-036 | 02 - Nebraska | 635017 | ATCHSN 3 | 345 | 17.3976 | 17.4058 | 0.0082
GEN-2020-036 | 02 - Nebraska | 635018 | WESTBORO 3 | 345 | 16.5982 | 16.6054 | 0.0072
GEN-2020-036 | 02 - Nebraska | 635030 | RIVRBND5 | 161 | 36.2309 | 36.2778 | 0.0469
GEN-2020-036 | 02 - Nebraska | 635100 | RLHILLS3 | 345 | 13.0879 | 13.0923 | 0.0044
GEN-2020-036 | 02 - Nebraska | 635200 | RAUN 3 | 345 | 28.7088 | 28.7143 | 0.0055
GEN-2020-036 | 02 - Nebraska | 635201 | RAUN 5 | 161 | 28.5042 | 28.5069 | 0.0027
GEN-2020-036 | 02 - Nebraska | 635252 | J412 POI 3 | 345 | 10.1504 | 10.1509 | 0.0005
GEN-2020-036 | 02 - Nebraska | 635398 | REMSEN 3 | 345 | 15.2391 | 15.2399 | 0.0008
GEN-2020-036 | 02 - Nebraska | 635570 | ORIENT 3 | 345 | 17.3915 | 17.3963 | 0.0048
GEN-2020-036 | 02 - Nebraska | 635589 | ECLIPSE3 | 345 | 9.0599 | 9.0617 | 0.0018
GEN-2020-036 | 02 - Nebraska | 635590 | FALLOW 3 | 345 | 10.9953 | 10.998 | 0.0027
GEN-2020-036 | 02 - Nebraska | 637084 | J476 SHENHLL | 345 | 16.5148 | 16.522 | 0.0072
GEN-2020-036 | 02 - Nebraska | 640125 | COLMB.E3 | 345 | 10.9891 | 10.991 | 0.0019
GEN-2020-036 | 02 - Nebraska | 640127 | COLMB.E7 | 115 | 23.4844 | 23.4865 | 0.0021
GEN-2020-036 | 02 - Nebraska | 640139 | COOPER 3 | 345 | 26.9482 | 26.9714 | 0.0232
GEN-2020-036 | 02 - Nebraska | 640140 | COOPER 5 | 161 | 18.1312 | 18.1359 | 0.0047
GEN-2020-036 | 02 - Nebraska | 640141 | COOPER_ESST8 | 69 | 4.6824 | 4.6825 | 0.0001
GEN-2020-036 | 02 - Nebraska | 640143 | COOPER_602 8 | 69 | 2.0146 | 2.0146 | 0
GEN-2020-036 | 02 - Nebraska | 640171 | FIRTH 7 | 115 | 7.0172 | 7.0177 | 0.0005
GEN-2020-036 | 02 - Nebraska | 640226 | HOSKINS3 | 345 | 16.1269 | 16.1283 | 0.0014
GEN-2020-036 | 02 - Nebraska | 640234 | HUMBOLT5 | 161 | 7.8362 | 7.8368 | 0.0006
GEN-2020-036 | 02 - Nebraska | 640271 | MCCOOL 3 | 345 | 11.6162 | 11.6185 | 0.0023
GEN-2020-036 | 02 - Nebraska | 640277 | MOORE 3 | 345 | 23.8766 | 23.8992 | 0.0226
GEN-2020-036 | 02 - Nebraska | 640278 | SHELDON7 | 115 | 44.5682 | 44.587 | 0.0188
GEN-2020-036 | 02 - Nebraska | 640316 | PAWNEEL7 | 115 | 11.7976 | 11.7993 | 0.0017
GEN-2020-036 | 02 - Nebraska | 640342 | SHELCRK3 | 345 | 11.4549 | 11.4566 | 0.0017
GEN-2020-036 | 02 - Nebraska | 640446 | COOPER 8 | 69 | 4.78 | 4.7802 | 0.0002
GEN-2020-036 | 02 - Nebraska | 640525 | TOBIAS 3 | 345 | 12.3602 | 12.364 | 0.0038
GEN-2020-036 | 02 - Nebraska | 640588 | TURTLE.CRK 3 | 345 | 13.3489 | 13.3499 | 0.001
GEN-2020-036 | 02 - Nebraska | 640589 | SHOLES.W 3 | 345 | 10.4766 | 10.4772 | 0.0006
GEN-2020-036 | 02 - Nebraska | 640590 | MONOLITH 3 | 345 | 23.3485 | 23.3699 | 0.0214
GEN-2020-036 | 02 - Nebraska | 640591 | MONOLITH 7 | 115 | 43.5007 | 43.5193 | 0.0186
GEN-2020-036 | 02 - Nebraska | 640598 | HAYSTACK.WD3 | 345 | 9.9779 | 9.9783 | 0.0004
GEN-2020-036 | 02 - Nebraska | 643271 | PLUMBCR.W 3 | 345 | 13.0071 | 13.008 | 0.0009
GEN-2020-036 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.5284 | 30.5745 | 0.0461
GEN-2020-036 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.4281 | 23.4917 | 0.0636
GEN-2020-036 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.1939 | 30.4229 | 0.229
GEN-2020-036 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.4576 | 33.718 | 0.2604
GEN-2020-036 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.5977 | 35.7822 | 0.1845
GEN-2020-036 | 02 - Nebraska | 645458 | S3458 3 | 345 | 29.9973 | 30.0963 | 0.099
GEN-2020-036 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.1303 | 26.2179 | 0.0876
GEN-2020-036 | 02 - Nebraska | 645740 | S3740 3 | 345 | 23.9276 | 24.3832 | 0.4556
GEN-2020-036 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.876 | 24.0017 | 0.1257
GEN-2020-036 | 02 - Nebraska | 646201 | S1201 5 | 161 | 31.9995 | 32.0427 | 0.0432
GEN-2020-036 | 02 - Nebraska | 646206 | S1206 5 | 161 | 44.7672 | 44.8616 | 0.0944
GEN-2020-036 | 02 - Nebraska | 646209 | S1209 5 | 161 | 48.2929 | 48.4181 | 0.1252
GEN-2020-036 | 02 - Nebraska | 646214 | S1214 5 | 161 | 12.9437 | 12.9523 | 0.0086
GEN-2020-036 | 02 - Nebraska | 646216 | S1216 5 | 161 | 30.854 | 30.9002 | 0.0462
GEN-2020-036 | 02 - Nebraska | 646217 | S1217 5 | 161 | 33.6316 | 33.6872 | 0.0556
GEN-2020-036 | 02 - Nebraska | 646220 | S1220 5 | 161 | 28.8343 | 28.8688 | 0.0345
GEN-2020-036 | 02 - Nebraska | 646221 | S1221 5 | 161 | 36.2438 | 36.3278 | 0.084
GEN-2020-036 | 02 - Nebraska | 646226 | S1226 5 | 161 | 25.639 | 25.6682 | 0.0292
GEN-2020-036 | 02 - Nebraska | 646227 | S1227 5 | 161 | 33.0839 | 33.142 | 0.0581
GEN-2020-036 | 02 - Nebraska | 646229 | S1229 5 | 161 | 28.9422 | 28.9784 | 0.0362
GEN-2020-036 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.1254 | 44.2376 | 0.1122
GEN-2020-036 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26.9591 | 26.9988 | 0.0397
GEN-2020-036 | 02 - Nebraska | 646233 | S1233 5 | 161 | 30.0617 | 30.1276 | 0.0659
GEN-2020-036 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27.4418 | 27.4924 | 0.0506
GEN-2020-036 | 02 - Nebraska | 646235 | S1235 5 | 161 | 34.8522 | 34.9268 | 0.0746
GEN-2020-036 | 02 - Nebraska | 646244 | S1244 5 | 161 | 22.2409 | 22.263 | 0.0221
GEN-2020-036 | 02 - Nebraska | 646249 | S1249 5 | 161 | 26.1692 | 26.2201 | 0.0509
GEN-2020-036 | 02 - Nebraska | 646250 | S1250 5 | 161 | 35.6447 | 35.7004 | 0.0557
GEN-2020-036 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.2492 | 33.3039 | 0.0547
GEN-2020-036 | 02 - Nebraska | 646253 | S1253 5 | 161 | 28.2529 | 28.3027 | 0.0498
GEN-2020-036 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.69 | 34.7844 | 0.0944
GEN-2020-036 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.6695 | 50.8724 | 0.2029
GEN-2020-036 | 02 - Nebraska | 646256 | S1256 5 | 161 | 23.4201 | 23.458 | 0.0379
GEN-2020-036 | 02 - Nebraska | 646259 | S1259 5 | 161 | 40.2785 | 40.3943 | 0.1158
GEN-2020-036 | 02 - Nebraska | 646260 | S1260 5 | 161 | 42.8179 | 42.944 | 0.1261
GEN-2020-036 | 02 - Nebraska | 646263 | S1263 5 | 161 | 8.4615 | 8.4626 | 0.0011
GEN-2020-036 | 02 - Nebraska | 646278 | S1278 5 | 161 | 28.1811 | 28.2329 | 0.0518
GEN-2020-036 | 02 - Nebraska | 646280 | S1280 5 | 161 | 10.4488 | 10.4502 | 0.0014
GEN-2020-036 | 02 - Nebraska | 646281 | S1281 5 | 161 | 40.7548 | 40.8654 | 0.1106
GEN-2020-036 | 02 - Nebraska | 646286 | S1286 5 | 161 | 26.687 | 26.7166 | 0.0296
GEN-2020-036 | 02 - Nebraska | 646287 | S1287 5 | 161 | 23.6446 | 23.6795 | 0.0349
GEN-2020-036 | 02 - Nebraska | 646297 | S1297 5 | 161 | 19.2371 | 19.2544 | 0.0173
GEN-2020-036 | 02 - Nebraska | 646298 | S1298 5 | 161 | 30.2877 | 30.3321 | 0.0444
GEN-2020-036 | 02 - Nebraska | 646305 | S1305 5 | 161 | 28.7734 | 28.8136 | 0.0402
GEN-2020-036 | 02 - Nebraska | 646341 | S1341 5 | 161 | 27.9852 | 28.0234 | 0.0382
GEN-2020-036 | 02 - Nebraska | 646347 | S1347 5 | 161 | 33.9344 | 33.9924 | 0.058
GEN-2020-036 | 02 - Nebraska | 646361 | S1361 5 | 161 | 44.2459 | 44.3845 | 0.1386
GEN-2020-036 | 02 - Nebraska | 646362 | S1362 5 | 161 | 41.3686 | 41.4833 | 0.1147
GEN-2020-036 | 02 - Nebraska | 646363 | S1363 5 | 161 | 37.8379 | 37.9198 | 0.0819
GEN-2020-036 | 02 - Nebraska | 646366 | S1366 5 | 161 | 16.4069 | 16.4183 | 0.0114
GEN-2020-036 | 02 - Nebraska | 647006 | S906 N 8 | 69 | 32.266 | 32.2848 | 0.0188
GEN-2020-036 | 02 - Nebraska | 647015 | S6815T1&T2 8 | 69 | 12.0695 | 12.0721 | 0.0026
GEN-2020-036 | 02 - Nebraska | 647016 | 6815TP38 | 69 | 17.5449 | 17.5502 | 0.0053
GEN-2020-036 | 02 - Nebraska | 647017 | 6815TP98 | 69 | 12.6564 | 12.6593 | 0.0029
GEN-2020-036 | 02 - Nebraska | 647815 | S6815T3 8 | 69 | 11.4339 | 11.4362 | 0.0023
GEN-2020-036 | 02 - Nebraska | 647874 | S6874 8 | 69 | 8.6149 | 8.6162 | 0.0013
GEN-2020-036 | 02 - Nebraska | 647901 | S901 8 | 69 | 26.3334 | 26.3427 | 0.0093
GEN-2020-036 | 02 - Nebraska | 647904 | S904 8 | 69 | 8.7516 | 8.7528 | 0.0012
GEN-2020-036 | 02 - Nebraska | 647906 | S906 S 8 | 69 | 32.6952 | 32.7128 | 0.0176
GEN-2020-036 | 02 - Nebraska | 647909 | S909 8 | 69 | 27.1871 | 27.2018 | 0.0147
GEN-2020-036 | 02 - Nebraska | 647916 | S916 8 | 69 | 23.8484 | 23.8599 | 0.0115
GEN-2020-036 | 02 - Nebraska | 647921 | S921 8 | 69 | 26.5446 | 26.5599 | 0.0153
GEN-2020-036 | 02 - Nebraska | 647924 | S924 8 | 69 | 24.4083 | 24.4178 | 0.0095
GEN-2020-036 | 02 - Nebraska | 647928 | S928 8 | 69 | 17.2414 | 17.2471 | 0.0057
GEN-2020-036 | 02 - Nebraska | 647938 | S938 8 | 69 | 21.746 | 21.7542 | 0.0082
GEN-2020-036 | 02 - Nebraska | 647940 | S940 8 | 69 | 20.9553 | 20.9645 | 0.0092
GEN-2020-036 | 02 - Nebraska | 647942 | S942 8 | 69 | 16.206 | 16.2113 | 0.0053
GEN-2020-036 | 02 - Nebraska | 647960 | S960 8 | 69 | 7.4891 | 7.4904 | 0.0013
GEN-2020-036 | 02 - Nebraska | 647995 | S995 8 | 69 | 9.492 | 9.4935 | 0.0015
GEN-2020-036 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17.8241 | 17.8395 | 0.0154
GEN-2020-036 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.4386 | 21.476 | 0.0374
GEN-2020-036 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21.3338 | 21.3651 | 0.0313
GEN-2020-036 | 02 - Nebraska | 650210 | NW70FAIRFD7 | 115 | 21.4985 | 21.5051 | 0.0066
GEN-2020-036 | 02 - Nebraska | 650214 | NW68HOLDRG7 | 115 | 25.7581 | 25.7674 | 0.0093
GEN-2020-036 | 02 - Nebraska | 650216 | SW27&F 7 | 115 | 22.224 | 22.2312 | 0.0072
GEN-2020-036 | 02 - Nebraska | 650262 | 57&GARLAND7 | 115 | 25.5445 | 25.5547 | 0.0102
GEN-2020-036 | 02 - Nebraska | 650267 | 84LEIGHTON7 | 115 | 29.6606 | 29.6748 | 0.0142
GEN-2020-036 | 02 - Nebraska | 650270 | 70&CALVERT7 | 115 | 27.5978 | 27.6094 | 0.0116
GEN-2020-036 | 02 - Nebraska | 650271 | 81&OCHENEY7 | 115 | 25.269 | 25.2787 | 0.0097
GEN-2020-036 | 02 - Nebraska | 650272 | 91&A 7 | 115 | 21.998 | 22.0055 | 0.0075
GEN-2020-036 | 02 - Nebraska | 650273 | 93&O 7 | 115 | 22.7585 | 22.7667 | 0.0082
GEN-2020-036 | 02 - Nebraska | 650274 | 91&HWY2 7 | 115 | 21.8769 | 21.8838 | 0.0069
GEN-2020-036 | 02 - Nebraska | 650279 | 120&ALVO 7 | 115 | 21.8034 | 21.8116 | 0.0082
GEN-2020-036 | 02 - Nebraska | 650283 | WAVERLY 7 | 115 | 21.275 | 21.2824 | 0.0074
GEN-2020-036 | 02 - Nebraska | 650284 | 84FLETCHER7 | 115 | 25.0792 | 25.0889 | 0.0097
GEN-2020-036 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32.4032 | 32.4229 | 0.0197
GEN-2020-036 | 02 - Nebraska | 650290 | ROKEBY 7 | 115 | 25.7609 | 25.7696 | 0.0087
GEN-2020-036 | 02 - Nebraska | 652564 | SIOUXCY3 | 345 | 16.0923 | 16.0934 | 0.0011
GEN-2020-036 | 02 - Nebraska | 760746 | GEN-2017-115 | 345 | 7.2201 | 7.2225 | 0.0024
GEN-2020-036 | 02 - Nebraska | 760788 | GEN-2017-201 | 345 | 9.4559 | 9.4564 | 0.0005
GEN-2020-036 | 02 - Nebraska | 760872 | GEN-2017-198 | 69 | 24.9749 | 24.9832 | 0.0083
GEN-2020-036 | 02 - Nebraska | 761208 | GEN-2017-210 | 345 | 10.1542 | 10.1559 | 0.0017
GEN-2020-036 | 02 - Nebraska | 761292 | GEN-2017-181 | 345 | 7.0086 | 7.0097 | 0.0011
GEN-2020-036 | 02 - Nebraska | 761313 | GEN-2017-182 | 345 | 5.8514 | 5.8522 | 0.0008
GEN-2020-036 | 02 - Nebraska | 761376 | GEN-2017-183 | 345 | 7.5638 | 7.564 | 0.0002
GEN-2020-036 | 02 - Nebraska | 761383 | G17-183-TAP | 345 | 16.4128 | 16.4136 | 0.0008
GEN-2020-036 | 02 - Nebraska | 762581 | GEN-2018-022 | 345 | 6.5854 | 6.5869 | 0.0015
GEN-2020-036 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.373 | 22.4309 | 0.0579
GEN-2020-036 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 23.926 | 24.3816 | 0.4556
GEN-2020-036 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.7683 | 17.7927 | 0.0244
GEN-2020-036 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.4017 | 17.425 | 0.0233
GEN-2020-036 | 02 - Nebraska | 763505 | GEN-2019-009 | 161 | 8.155 | 8.156 | 0.001
GEN-2020-036 | 02 - Nebraska | 763725 | GEN-2019-041 | 115 | 43.3931 | 43.4116 | 0.0185
GEN-2020-036 | 02 - Nebraska | 764600 | GEN-2020-025 | 161 | 37.8379 | 37.9198 | 0.0819
GEN-2020-036 | 02 - Nebraska | 764615 | GEN-2020-027 | 161 | 37.1495 | 37.2285 | 0.079
GEN-2020-036 | 02 - Nebraska | 764630 | GEN-2020-028 | 161 | 37.8379 | 37.9198 | 0.0819
GEN-2020-036 | 02 - Nebraska | 764660 | GEN-2020-031 | 161 | 37.8379 | 37.9198 | 0.0819
GEN-2020-036 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 23.6486 | 24.1043 | 0.4557
GEN-2020-036 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 23.9276 | 24.3832 | 0.4556
GEN-2020-036 | 02 - Nebraska | 764720 | GEN-2020-043 | 161 | 33.9332 | 33.9911 | 0.0579
GEN-2020-036 | 02 - Nebraska | 764735 | GEN-2020-044 | 161 | 33.9332 | 33.9911 | 0.0579
GEN-2020-036 | 02 - Nebraska | 764750 | GEN-2020-045 | 161 | 33.9332 | 33.9911 | 0.0579
GEN-2020-036 | 02 - Nebraska | 764795 | GEN-2020-094 | 345 | 11.937 | 11.9489 | 0.0119
GEN-2020-036 | 02 - Nebraska | 764805 | G20-094-TAP | 345 | 16.7897 | 16.8137 | 0.024
GEN-2020-038 | 02 - Nebraska | 45906 | J1590 SUB | 345 | 15.0026 | 15.0035 | 0.0009
GEN-2020-038 | 02 - Nebraska | 85831 | J583 | 345 | 6.061 | 6.0619 | 0.0009
GEN-2020-038 | 02 - Nebraska | 87486 | J748GENTIE | 345 | 13.9564 | 13.9572 | 0.0008
GEN-2020-038 | 02 - Nebraska | 87487 | J748POI | 345 | 15.8405 | 15.8415 | 0.001
GEN-2020-038 | 02 - Nebraska | 300039 | 7FAIRPT | 345 | 12.5842 | 12.5859 | 0.0017
GEN-2020-038 | 02 - Nebraska | 300076 | 5FAIRPTB2 | 161 | 16.5703 | 16.5712 | 0.0009
GEN-2020-038 | 02 - Nebraska | 301347 | 5WINSLOW | 161 | 8.8564 | 8.8566 | 0.0002
GEN-2020-038 | 02 - Nebraska | 301559 | 5FAIRPTXF3 | 161 | 16.5888 | 16.5897 | 0.0009
GEN-2020-038 | 02 - Nebraska | 541147 | ST JOE_CAP5 | 161 | 17.9666 | 17.9675 | 0.0009
GEN-2020-038 | 02 - Nebraska | 541197 | MULLNCR7 | 345 | 7.8112 | 7.8138 | 0.0026
GEN-2020-038 | 02 - Nebraska | 541199 | ST JOE 7 | 345 | 19.7432 | 19.7459 | 0.0027
GEN-2020-038 | 02 - Nebraska | 541201 | SIBLEY 7 | 345 | 21.0097 | 21.0107 | 0.001
GEN-2020-038 | 02 - Nebraska | 541253 | ST JOE 5 | 161 | 20.0498 | 20.0509 | 0.0011
GEN-2020-038 | 02 - Nebraska | 541257 | COOK 5 | 161 | 14.2256 | 14.2261 | 0.0005
GEN-2020-038 | 02 - Nebraska | 541258 | WOODBIN5 | 161 | 17.0284 | 17.0292 | 0.0008
GEN-2020-038 | 02 - Nebraska | 541394 | AVENUECTY 5 | 161 | 8.7874 | 8.7876 | 0.0002
GEN-2020-038 | 02 - Nebraska | 541400 | EASTOWN7 | 345 | 18.3302 | 18.3319 | 0.0017
GEN-2020-038 | 02 - Nebraska | 541401 | EASTOWN5 | 161 | 17.5491 | 17.5499 | 0.0008
GEN-2020-038 | 02 - Nebraska | 541411 | MC REAC1 | 345 | 7.4794 | 7.4817 | 0.0023
GEN-2020-038 | 02 - Nebraska | 541412 | MC REAC2 | 345 | 7.4794 | 7.4817 | 0.0023
GEN-2020-038 | 02 - Nebraska | 541413 | MC REAC3 | 345 | 7.4794 | 7.4817 | 0.0023
GEN-2020-038 | 02 - Nebraska | 541414 | SIB REA1 | 345 | 18.7712 | 18.7719 | 0.0007
GEN-2020-038 | 02 - Nebraska | 541500 | KETCHEM7 | 345 | 7.8122 | 7.8134 | 0.0012
GEN-2020-038 | 02 - Nebraska | 541501 | OSBORN7 | 345 | 6.9725 | 6.9734 | 0.0009
GEN-2020-038 | 02 - Nebraska | 541510 | HOLT 7 | 345 | 8.9062 | 8.9106 | 0.0044
GEN-2020-038 | 02 - Nebraska | 541511 | ROCKCK7 | 345 | 6.9429 | 6.9454 | 0.0025
GEN-2020-038 | 02 - Nebraska | 541517 | HOLT_REACT7 | 345 | 8.8611 | 8.8655 | 0.0044
GEN-2020-038 | 02 - Nebraska | 541543 | OUTLAW | 345 | 5.7473 | 5.749 | 0.0017
GEN-2020-038 | 02 - Nebraska | 542980 | NASHUA 7 | 345 | 22.7056 | 22.7067 | 0.0011
GEN-2020-038 | 02 - Nebraska | 542982 | IATAN 7 | 345 | 29.3715 | 29.3727 | 0.0012
GEN-2020-038 | 02 - Nebraska | 560746 | G13-002-TAP | 115 | 43.4969 | 43.5193 | 0.0224
GEN-2020-038 | 02 - Nebraska | 583700 | GEN-2013-019 | 115 | 19.1999 | 19.204 | 0.0041
GEN-2020-038 | 02 - Nebraska | 585241 | GEN-2015-088 | 345 | 12.3594 | 12.364 | 0.0046
GEN-2020-038 | 02 - Nebraska | 635000 | CBLUFFS3 | 345 | 32.1347 | 32.2342 | 0.0995
GEN-2020-038 | 02 - Nebraska | 635001 | CBLUFFS5 | 161 | 39.7495 | 39.8181 | 0.0686
GEN-2020-038 | 02 - Nebraska | 635002 | CBLUFFS8 | 69 | 25.2402 | 25.2514 | 0.0112
GEN-2020-038 | 02 - Nebraska | 635011 | INDNCRK5 | 161 | 22.0247 | 22.0461 | 0.0214
GEN-2020-038 | 02 - Nebraska | 635013 | PNYCRK 3 | 345 | 29.2294 | 29.31 | 0.0806
GEN-2020-038 | 02 - Nebraska | 635014 | OVRLND 3 | 345 | 27.4306 | 27.5003 | 0.0697
GEN-2020-038 | 02 - Nebraska | 635015 | OVRLND 5 | 161 | 31.5261 | 31.5672 | 0.0411
GEN-2020-038 | 02 - Nebraska | 635016 | STHLND 3 | 345 | 29.1947 | 29.2751 | 0.0804
GEN-2020-038 | 02 - Nebraska | 635017 | ATCHSN 3 | 345 | 17.3959 | 17.4058 | 0.0099
GEN-2020-038 | 02 - Nebraska | 635018 | WESTBORO 3 | 345 | 16.5967 | 16.6054 | 0.0087
GEN-2020-038 | 02 - Nebraska | 635030 | RIVRBND5 | 161 | 36.2213 | 36.2778 | 0.0565
GEN-2020-038 | 02 - Nebraska | 635100 | RLHILLS3 | 345 | 13.087 | 13.0923 | 0.0053
GEN-2020-038 | 02 - Nebraska | 635200 | RAUN 3 | 345 | 28.7077 | 28.7143 | 0.0066
GEN-2020-038 | 02 - Nebraska | 635201 | RAUN 5 | 161 | 28.5037 | 28.5069 | 0.0032
GEN-2020-038 | 02 - Nebraska | 635252 | J412 POI 3 | 345 | 10.1504 | 10.1509 | 0.0005
GEN-2020-038 | 02 - Nebraska | 635398 | REMSEN 3 | 345 | 15.2389 | 15.2399 | 0.001
GEN-2020-038 | 02 - Nebraska | 635570 | ORIENT 3 | 345 | 17.3905 | 17.3963 | 0.0058
GEN-2020-038 | 02 - Nebraska | 635589 | ECLIPSE3 | 345 | 9.0596 | 9.0617 | 0.0021
GEN-2020-038 | 02 - Nebraska | 635590 | FALLOW 3 | 345 | 10.9947 | 10.998 | 0.0033
GEN-2020-038 | 02 - Nebraska | 637084 | J476 SHENHLL | 345 | 16.5133 | 16.522 | 0.0087
GEN-2020-038 | 02 - Nebraska | 640125 | COLMB.E3 | 345 | 10.9887 | 10.991 | 0.0023
GEN-2020-038 | 02 - Nebraska | 640127 | COLMB.E7 | 115 | 23.484 | 23.4865 | 0.0025
GEN-2020-038 | 02 - Nebraska | 640139 | COOPER 3 | 345 | 26.9435 | 26.9714 | 0.0279
GEN-2020-038 | 02 - Nebraska | 640140 | COOPER 5 | 161 | 18.1302 | 18.1359 | 0.0057
GEN-2020-038 | 02 - Nebraska | 640141 | COOPER_ESST8 | 69 | 4.6823 | 4.6825 | 0.0002
GEN-2020-038 | 02 - Nebraska | 640143 | COOPER_602 8 | 69 | 2.0146 | 2.0146 | 0
GEN-2020-038 | 02 - Nebraska | 640171 | FIRTH 7 | 115 | 7.0171 | 7.0177 | 0.0006
GEN-2020-038 | 02 - Nebraska | 640226 | HOSKINS3 | 345 | 16.1266 | 16.1283 | 0.0017
GEN-2020-038 | 02 - Nebraska | 640234 | HUMBOLT5 | 161 | 7.8361 | 7.8368 | 0.0007
GEN-2020-038 | 02 - Nebraska | 640271 | MCCOOL 3 | 345 | 11.6158 | 11.6185 | 0.0027
GEN-2020-038 | 02 - Nebraska | 640277 | MOORE 3 | 345 | 23.8719 | 23.8992 | 0.0273
GEN-2020-038 | 02 - Nebraska | 640278 | SHELDON7 | 115 | 44.5643 | 44.587 | 0.0227
GEN-2020-038 | 02 - Nebraska | 640316 | PAWNEEL7 | 115 | 11.7972 | 11.7993 | 0.0021
GEN-2020-038 | 02 - Nebraska | 640342 | SHELCRK3 | 345 | 11.4546 | 11.4566 | 0.002
GEN-2020-038 | 02 - Nebraska | 640446 | COOPER 8 | 69 | 4.78 | 4.7802 | 0.0002
GEN-2020-038 | 02 - Nebraska | 640525 | TOBIAS 3 | 345 | 12.3594 | 12.364 | 0.0046
GEN-2020-038 | 02 - Nebraska | 640588 | TURTLE.CRK 3 | 345 | 13.3488 | 13.3499 | 0.0011
GEN-2020-038 | 02 - Nebraska | 640589 | SHOLES.W 3 | 345 | 10.4765 | 10.4772 | 0.0007
GEN-2020-038 | 02 - Nebraska | 640590 | MONOLITH 3 | 345 | 23.3441 | 23.3699 | 0.0258
GEN-2020-038 | 02 - Nebraska | 640591 | MONOLITH 7 | 115 | 43.4969 | 43.5193 | 0.0224
GEN-2020-038 | 02 - Nebraska | 640598 | HAYSTACK.WD3 | 345 | 9.9778 | 9.9783 | 0.0005
GEN-2020-038 | 02 - Nebraska | 643271 | PLUMBCR.W 3 | 345 | 13.0069 | 13.008 | 0.0011
GEN-2020-038 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.519 | 30.5745 | 0.0555
GEN-2020-038 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.4151 | 23.4917 | 0.0766
GEN-2020-038 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.1473 | 30.4229 | 0.2756
GEN-2020-038 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.4048 | 33.718 | 0.3132
GEN-2020-038 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.5601 | 35.7822 | 0.2221
GEN-2020-038 | 02 - Nebraska | 645458 | S3458 3 | 345 | 29.9771 | 30.0963 | 0.1192
GEN-2020-038 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.1124 | 26.2179 | 0.1055
GEN-2020-038 | 02 - Nebraska | 645740 | S3740 3 | 345 | 23.8364 | 24.3832 | 0.5468
GEN-2020-038 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.8504 | 24.0017 | 0.1513
GEN-2020-038 | 02 - Nebraska | 646201 | S1201 5 | 161 | 31.9906 | 32.0427 | 0.0521
GEN-2020-038 | 02 - Nebraska | 646206 | S1206 5 | 161 | 44.7479 | 44.8616 | 0.1137
GEN-2020-038 | 02 - Nebraska | 646209 | S1209 5 | 161 | 48.2673 | 48.4181 | 0.1508
GEN-2020-038 | 02 - Nebraska | 646214 | S1214 5 | 161 | 12.9419 | 12.9523 | 0.0104
GEN-2020-038 | 02 - Nebraska | 646216 | S1216 5 | 161 | 30.8445 | 30.9002 | 0.0557
GEN-2020-038 | 02 - Nebraska | 646217 | S1217 5 | 161 | 33.6203 | 33.6872 | 0.0669
GEN-2020-038 | 02 - Nebraska | 646220 | S1220 5 | 161 | 28.8273 | 28.8688 | 0.0415
GEN-2020-038 | 02 - Nebraska | 646221 | S1221 5 | 161 | 36.2266 | 36.3278 | 0.1012
GEN-2020-038 | 02 - Nebraska | 646226 | S1226 5 | 161 | 25.633 | 25.6682 | 0.0352
GEN-2020-038 | 02 - Nebraska | 646227 | S1227 5 | 161 | 33.072 | 33.142 | 0.07
GEN-2020-038 | 02 - Nebraska | 646229 | S1229 5 | 161 | 28.9348 | 28.9784 | 0.0436
GEN-2020-038 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.1025 | 44.2376 | 0.1351
GEN-2020-038 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26.9509 | 26.9988 | 0.0479
GEN-2020-038 | 02 - Nebraska | 646233 | S1233 5 | 161 | 30.0482 | 30.1276 | 0.0794
GEN-2020-038 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27.4314 | 27.4924 | 0.061
GEN-2020-038 | 02 - Nebraska | 646235 | S1235 5 | 161 | 34.837 | 34.9268 | 0.0898
GEN-2020-038 | 02 - Nebraska | 646244 | S1244 5 | 161 | 22.2364 | 22.263 | 0.0266
GEN-2020-038 | 02 - Nebraska | 646249 | S1249 5 | 161 | 26.1588 | 26.2201 | 0.0613
GEN-2020-038 | 02 - Nebraska | 646250 | S1250 5 | 161 | 35.6332 | 35.7004 | 0.0672
GEN-2020-038 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.238 | 33.3039 | 0.0659
GEN-2020-038 | 02 - Nebraska | 646253 | S1253 5 | 161 | 28.2427 | 28.3027 | 0.06
GEN-2020-038 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.6707 | 34.7844 | 0.1137
GEN-2020-038 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.6281 | 50.8724 | 0.2443
GEN-2020-038 | 02 - Nebraska | 646256 | S1256 5 | 161 | 23.4123 | 23.458 | 0.0457
GEN-2020-038 | 02 - Nebraska | 646259 | S1259 5 | 161 | 40.2548 | 40.3943 | 0.1395
GEN-2020-038 | 02 - Nebraska | 646260 | S1260 5 | 161 | 42.7922 | 42.944 | 0.1518
GEN-2020-038 | 02 - Nebraska | 646263 | S1263 5 | 161 | 8.4613 | 8.4626 | 0.0013
GEN-2020-038 | 02 - Nebraska | 646278 | S1278 5 | 161 | 28.1705 | 28.2329 | 0.0624
GEN-2020-038 | 02 - Nebraska | 646280 | S1280 5 | 161 | 10.4485 | 10.4502 | 0.0017
GEN-2020-038 | 02 - Nebraska | 646281 | S1281 5 | 161 | 40.7322 | 40.8654 | 0.1332
GEN-2020-038 | 02 - Nebraska | 646286 | S1286 5 | 161 | 26.681 | 26.7166 | 0.0356
GEN-2020-038 | 02 - Nebraska | 646287 | S1287 5 | 161 | 23.6375 | 23.6795 | 0.042
GEN-2020-038 | 02 - Nebraska | 646297 | S1297 5 | 161 | 19.2335 | 19.2544 | 0.0209
GEN-2020-038 | 02 - Nebraska | 646298 | S1298 5 | 161 | 30.2786 | 30.3321 | 0.0535
GEN-2020-038 | 02 - Nebraska | 646305 | S1305 5 | 161 | 28.7651 | 28.8136 | 0.0485
GEN-2020-038 | 02 - Nebraska | 646341 | S1341 5 | 161 | 27.9774 | 28.0234 | 0.046
GEN-2020-038 | 02 - Nebraska | 646347 | S1347 5 | 161 | 33.9226 | 33.9924 | 0.0698
GEN-2020-038 | 02 - Nebraska | 646361 | S1361 5 | 161 | 44.2176 | 44.3845 | 0.1669
GEN-2020-038 | 02 - Nebraska | 646362 | S1362 5 | 161 | 41.3452 | 41.4833 | 0.1381
GEN-2020-038 | 02 - Nebraska | 646363 | S1363 5 | 161 | 37.8212 | 37.9198 | 0.0986
GEN-2020-038 | 02 - Nebraska | 646366 | S1366 5 | 161 | 16.4045 | 16.4183 | 0.0138
GEN-2020-038 | 02 - Nebraska | 647006 | S906 N 8 | 69 | 32.2622 | 32.2848 | 0.0226
GEN-2020-038 | 02 - Nebraska | 647015 | S6815T1&T2 8 | 69 | 12.069 | 12.0721 | 0.0031
GEN-2020-038 | 02 - Nebraska | 647016 | 6815TP38 | 69 | 17.5438 | 17.5502 | 0.0064
GEN-2020-038 | 02 - Nebraska | 647017 | 6815TP98 | 69 | 12.6558 | 12.6593 | 0.0035
GEN-2020-038 | 02 - Nebraska | 647815 | S6815T3 8 | 69 | 11.4335 | 11.4362 | 0.0027
GEN-2020-038 | 02 - Nebraska | 647874 | S6874 8 | 69 | 8.6146 | 8.6162 | 0.0016
GEN-2020-038 | 02 - Nebraska | 647901 | S901 8 | 69 | 26.3314 | 26.3427 | 0.0113
GEN-2020-038 | 02 - Nebraska | 647904 | S904 8 | 69 | 8.7513 | 8.7528 | 0.0015
GEN-2020-038 | 02 - Nebraska | 647906 | S906 S 8 | 69 | 32.6916 | 32.7128 | 0.0212
GEN-2020-038 | 02 - Nebraska | 647909 | S909 8 | 69 | 27.184 | 27.2018 | 0.0178
GEN-2020-038 | 02 - Nebraska | 647916 | S916 8 | 69 | 23.846 | 23.8599 | 0.0139
GEN-2020-038 | 02 - Nebraska | 647921 | S921 8 | 69 | 26.5415 | 26.5599 | 0.0184
GEN-2020-038 | 02 - Nebraska | 647924 | S924 8 | 69 | 24.4063 | 24.4178 | 0.0115
GEN-2020-038 | 02 - Nebraska | 647928 | S928 8 | 69 | 17.2403 | 17.2471 | 0.0068
GEN-2020-038 | 02 - Nebraska | 647938 | S938 8 | 69 | 21.7443 | 21.7542 | 0.0099
GEN-2020-038 | 02 - Nebraska | 647940 | S940 8 | 69 | 20.9534 | 20.9645 | 0.0111
GEN-2020-038 | 02 - Nebraska | 647942 | S942 8 | 69 | 16.2049 | 16.2113 | 0.0064
GEN-2020-038 | 02 - Nebraska | 647960 | S960 8 | 69 | 7.4888 | 7.4904 | 0.0016
GEN-2020-038 | 02 - Nebraska | 647995 | S995 8 | 69 | 9.4916 | 9.4935 | 0.0019
GEN-2020-038 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17.821 | 17.8395 | 0.0185
GEN-2020-038 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.431 | 21.476 | 0.045
GEN-2020-038 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21.3274 | 21.3651 | 0.0377
GEN-2020-038 | 02 - Nebraska | 650210 | NW70FAIRFD7 | 115 | 21.4972 | 21.5051 | 0.0079
GEN-2020-038 | 02 - Nebraska | 650214 | NW68HOLDRG7 | 115 | 25.7562 | 25.7674 | 0.0112
GEN-2020-038 | 02 - Nebraska | 650216 | SW27&F 7 | 115 | 22.2226 | 22.2312 | 0.0086
GEN-2020-038 | 02 - Nebraska | 650262 | 57&GARLAND7 | 115 | 25.5424 | 25.5547 | 0.0123
GEN-2020-038 | 02 - Nebraska | 650267 | 84LEIGHTON7 | 115 | 29.6576 | 29.6748 | 0.0172
GEN-2020-038 | 02 - Nebraska | 650270 | 70&CALVERT7 | 115 | 27.5955 | 27.6094 | 0.0139
GEN-2020-038 | 02 - Nebraska | 650271 | 81&OCHENEY7 | 115 | 25.267 | 25.2787 | 0.0117
GEN-2020-038 | 02 - Nebraska | 650272 | 91&A 7 | 115 | 21.9964 | 22.0055 | 0.0091
GEN-2020-038 | 02 - Nebraska | 650273 | 93&O 7 | 115 | 22.7568 | 22.7667 | 0.0099
GEN-2020-038 | 02 - Nebraska | 650274 | 91&HWY2 7 | 115 | 21.8755 | 21.8838 | 0.0083
GEN-2020-038 | 02 - Nebraska | 650279 | 120&ALVO 7 | 115 | 21.8017 | 21.8116 | 0.0099
GEN-2020-038 | 02 - Nebraska | 650283 | WAVERLY 7 | 115 | 21.2735 | 21.2824 | 0.0089
GEN-2020-038 | 02 - Nebraska | 650284 | 84FLETCHER7 | 115 | 25.0772 | 25.0889 | 0.0117
GEN-2020-038 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32.3992 | 32.4229 | 0.0237
GEN-2020-038 | 02 - Nebraska | 650290 | ROKEBY 7 | 115 | 25.7592 | 25.7696 | 0.0104
GEN-2020-038 | 02 - Nebraska | 652564 | SIOUXCY3 | 345 | 16.0921 | 16.0934 | 0.0013
GEN-2020-038 | 02 - Nebraska | 760746 | GEN-2017-115 | 345 | 7.2196 | 7.2225 | 0.0029
GEN-2020-038 | 02 - Nebraska | 760788 | GEN-2017-201 | 345 | 9.4559 | 9.4564 | 0.0005
GEN-2020-038 | 02 - Nebraska | 760872 | GEN-2017-198 | 69 | 24.9732 | 24.9832 | 0.01
GEN-2020-038 | 02 - Nebraska | 761208 | GEN-2017-210 | 345 | 10.1539 | 10.1559 | 0.002
GEN-2020-038 | 02 - Nebraska | 761292 | GEN-2017-181 | 345 | 7.0084 | 7.0097 | 0.0013
GEN-2020-038 | 02 - Nebraska | 761313 | GEN-2017-182 | 345 | 5.8512 | 5.8522 | 0.001
GEN-2020-038 | 02 - Nebraska | 761376 | GEN-2017-183 | 345 | 7.5638 | 7.564 | 0.0002
GEN-2020-038 | 02 - Nebraska | 761383 | G17-183-TAP | 345 | 16.4126 | 16.4136 | 0.001
GEN-2020-038 | 02 - Nebraska | 762581 | GEN-2018-022 | 345 | 6.5851 | 6.5869 | 0.0018
GEN-2020-038 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.3612 | 22.4309 | 0.0697
GEN-2020-038 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 23.8348 | 24.3816 | 0.5468
GEN-2020-038 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.7633 | 17.7927 | 0.0294
GEN-2020-038 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.397 | 17.425 | 0.028
GEN-2020-038 | 02 - Nebraska | 763505 | GEN-2019-009 | 161 | 8.1548 | 8.156 | 0.0012
GEN-2020-038 | 02 - Nebraska | 763725 | GEN-2019-041 | 115 | 43.3893 | 43.4116 | 0.0223
GEN-2020-038 | 02 - Nebraska | 764600 | GEN-2020-025 | 161 | 37.8212 | 37.9198 | 0.0986
GEN-2020-038 | 02 - Nebraska | 764615 | GEN-2020-027 | 161 | 37.1334 | 37.2285 | 0.0951
GEN-2020-038 | 02 - Nebraska | 764630 | GEN-2020-028 | 161 | 37.8212 | 37.9198 | 0.0986
GEN-2020-038 | 02 - Nebraska | 764660 | GEN-2020-031 | 161 | 37.8212 | 37.9198 | 0.0986
GEN-2020-038 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 23.57 | 24.1043 | 0.5343
GEN-2020-038 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 23.8364 | 24.3832 | 0.5468
GEN-2020-038 | 02 - Nebraska | 764720 | GEN-2020-043 | 161 | 33.9213 | 33.9911 | 0.0698
GEN-2020-038 | 02 - Nebraska | 764735 | GEN-2020-044 | 161 | 33.9213 | 33.9911 | 0.0698
GEN-2020-038 | 02 - Nebraska | 764750 | GEN-2020-045 | 161 | 33.9213 | 33.9911 | 0.0698
GEN-2020-038 | 02 - Nebraska | 764795 | GEN-2020-094 | 345 | 11.9346 | 11.9489 | 0.0143
GEN-2020-038 | 02 - Nebraska | 764805 | G20-094-TAP | 345 | 16.7848 | 16.8137 | 0.0289
GEN-2020-043 | 02 - Nebraska | 541510 | HOLT 7 | 345 | 8.9103 | 8.9106 | 0.0003
GEN-2020-043 | 02 - Nebraska | 541511 | ROCKCK7 | 345 | 6.9452 | 6.9454 | 0.0002
GEN-2020-043 | 02 - Nebraska | 541517 | HOLT_REACT7 | 345 | 8.8652 | 8.8655 | 0.0003
GEN-2020-043 | 02 - Nebraska | 541543 | OUTLAW | 345 | 5.7488 | 5.749 | 0.0002
GEN-2020-043 | 02 - Nebraska | 635000 | CBLUFFS3 | 345 | 32.2098 | 32.2342 | 0.0244
GEN-2020-043 | 02 - Nebraska | 635001 | CBLUFFS5 | 161 | 39.7959 | 39.8181 | 0.0222
GEN-2020-043 | 02 - Nebraska | 635003 | SUB701 5 | 161 | 21.5442 | 21.5548 | 0.0106
GEN-2020-043 | 02 - Nebraska | 635004 | SUB701 8 | 69 | 22.379 | 22.383 | 0.004
GEN-2020-043 | 02 - Nebraska | 635005 | SUB702 5 | 161 | 20.9024 | 20.9116 | 0.0092
GEN-2020-043 | 02 - Nebraska | 635013 | PNYCRK 3 | 345 | 29.2903 | 29.31 | 0.0197
GEN-2020-043 | 02 - Nebraska | 635014 | OVRLND 3 | 345 | 27.483 | 27.5003 | 0.0173
GEN-2020-043 | 02 - Nebraska | 635016 | STHLND 3 | 345 | 29.2554 | 29.2751 | 0.0197
GEN-2020-043 | 02 - Nebraska | 635200 | RAUN 3 | 345 | 28.7119 | 28.7143 | 0.0024
GEN-2020-043 | 02 - Nebraska | 635201 | RAUN 5 | 161 | 28.5056 | 28.5069 | 0.0013
GEN-2020-043 | 02 - Nebraska | 640139 | COOPER 3 | 345 | 26.9689 | 26.9714 | 0.0025
GEN-2020-043 | 02 - Nebraska | 640300 | OAKLAND7 | 115 | 7.9543 | 7.9546 | 0.0003
GEN-2020-043 | 02 - Nebraska | 640377 | TEKAMAH5 | 161 | 9.3775 | 9.379 | 0.0015
GEN-2020-043 | 02 - Nebraska | 640378 | TEKAMAH7 | 115 | 8.6258 | 8.6265 | 0.0007
GEN-2020-043 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.5446 | 30.5745 | 0.0299
GEN-2020-043 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.4644 | 23.4917 | 0.0273
GEN-2020-043 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.3905 | 30.4229 | 0.0324
GEN-2020-043 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.6742 | 33.718 | 0.0438
GEN-2020-043 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.733 | 35.7822 | 0.0492
GEN-2020-043 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30.0881 | 30.0963 | 0.0082
GEN-2020-043 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.1708 | 26.2179 | 0.0471
GEN-2020-043 | 02 - Nebraska | 645740 | S3740 3 | 345 | 24.3684 | 24.3832 | 0.0148
GEN-2020-043 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.9791 | 24.0017 | 0.0226
GEN-2020-043 | 02 - Nebraska | 646201 | S1201 5 | 161 | 32.0114 | 32.0427 | 0.0313
GEN-2020-043 | 02 - Nebraska | 646206 | S1206 5 | 161 | 44.8167 | 44.8616 | 0.0449
GEN-2020-043 | 02 - Nebraska | 646209 | S1209 5 | 161 | 48.2454 | 48.4181 | 0.1727
GEN-2020-043 | 02 - Nebraska | 646210 | S1210 5 | 161 | 28.2222 | 28.2486 | 0.0264
GEN-2020-043 | 02 - Nebraska | 646211 | S1211 5 | 161 | 36.2605 | 36.3041 | 0.0436
GEN-2020-043 | 02 - Nebraska | 646216 | S1216 5 | 161 | 30.87 | 30.9002 | 0.0302
GEN-2020-043 | 02 - Nebraska | 646217 | S1217 5 | 161 | 33.6464 | 33.6872 | 0.0408
GEN-2020-043 | 02 - Nebraska | 646220 | S1220 5 | 161 | 28.8429 | 28.8688 | 0.0259
GEN-2020-043 | 02 - Nebraska | 646221 | S1221 5 | 161 | 36.2703 | 36.3278 | 0.0575
GEN-2020-043 | 02 - Nebraska | 646226 | S1226 5 | 161 | 25.6391 | 25.6682 | 0.0291
GEN-2020-043 | 02 - Nebraska | 646227 | S1227 5 | 161 | 33.0931 | 33.142 | 0.0489
GEN-2020-043 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.1299 | 44.2376 | 0.1077
GEN-2020-043 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26.9822 | 26.9988 | 0.0166
GEN-2020-043 | 02 - Nebraska | 646233 | S1233 5 | 161 | 30.0945 | 30.1276 | 0.0331
GEN-2020-043 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27.4564 | 27.4924 | 0.036
GEN-2020-043 | 02 - Nebraska | 646235 | S1235 5 | 161 | 34.8526 | 34.9268 | 0.0742
GEN-2020-043 | 02 - Nebraska | 646236 | S1236 5 | 161 | 24.9867 | 25.0452 | 0.0585
GEN-2020-043 | 02 - Nebraska | 646237 | S1237 5 | 161 | 22.4002 | 22.4417 | 0.0415
GEN-2020-043 | 02 - Nebraska | 646244 | S1244 5 | 161 | 22.2526 | 22.263 | 0.0104
GEN-2020-043 | 02 - Nebraska | 646250 | S1250 5 | 161 | 35.6454 | 35.7004 | 0.055
GEN-2020-043 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.2685 | 33.3039 | 0.0354
GEN-2020-043 | 02 - Nebraska | 646252 | S1252 5 | 161 | 30.4839 | 30.6053 | 0.1214
GEN-2020-043 | 02 - Nebraska | 646253 | S1253 5 | 161 | 28.2563 | 28.3027 | 0.0464
GEN-2020-043 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.7557 | 34.7844 | 0.0287
GEN-2020-043 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.803 | 50.8724 | 0.0694
GEN-2020-043 | 02 - Nebraska | 646256 | S1256 5 | 161 | 23.4352 | 23.458 | 0.0228
GEN-2020-043 | 02 - Nebraska | 646259 | S1259 5 | 161 | 40.3557 | 40.3943 | 0.0386
GEN-2020-043 | 02 - Nebraska | 646291 | S1291 5 | 161 | 7.1322 | 7.1338 | 0.0016
GEN-2020-043 | 02 - Nebraska | 646297 | S1297 5 | 161 | 19.2407 | 19.2544 | 0.0137
GEN-2020-043 | 02 - Nebraska | 646298 | S1298 5 | 161 | 30.3007 | 30.3321 | 0.0314
GEN-2020-043 | 02 - Nebraska | 646299 | S1299 5 | 161 | 28.0718 | 28.0974 | 0.0256
GEN-2020-043 | 02 - Nebraska | 646305 | S1305 5 | 161 | 28.7855 | 28.8136 | 0.0281
GEN-2020-043 | 02 - Nebraska | 646341 | S1341 5 | 161 | 27.9971 | 28.0234 | 0.0263
GEN-2020-043 | 02 - Nebraska | 646345 | S1345 5 | 161 | 23.0608 | 23.1175 | 0.0567
GEN-2020-043 | 02 - Nebraska | 646347 | S1347 5 | 161 | 33.7635 | 33.9924 | 0.2289
GEN-2020-043 | 02 - Nebraska | 646361 | S1361 5 | 161 | 44.3445 | 44.3845 | 0.04
GEN-2020-043 | 02 - Nebraska | 646367 | S1367 5 | 161 | 22.1732 | 22.2072 | 0.034
GEN-2020-043 | 02 - Nebraska | 647006 | S906 N 8 | 69 | 32.2741 | 32.2848 | 0.0107
GEN-2020-043 | 02 - Nebraska | 647104 | MUD LNG8 | 69 | 14.6993 | 14.7031 | 0.0038
GEN-2020-043 | 02 - Nebraska | 647291 | S991 E 8 | 69 | 12.5483 | 12.5495 | 0.0012
GEN-2020-043 | 02 - Nebraska | 647422 | FREM B 8 | 69 | 14.5714 | 14.5724 | 0.001
GEN-2020-043 | 02 - Nebraska | 647902 | S902 8 | 69 | 9.1904 | 9.1911 | 0.0007
GEN-2020-043 | 02 - Nebraska | 647906 | S906 S 8 | 69 | 32.7035 | 32.7128 | 0.0093
GEN-2020-043 | 02 - Nebraska | 647907 | S907 8 | 69 | 18.0303 | 18.0351 | 0.0048
GEN-2020-043 | 02 - Nebraska | 647909 | S909 8 | 69 | 27.1883 | 27.2018 | 0.0135
GEN-2020-043 | 02 - Nebraska | 647911 | S911 8 | 69 | 21.3161 | 21.3226 | 0.0065
GEN-2020-043 | 02 - Nebraska | 647913 | S913 8 | 69 | 16.2031 | 16.2065 | 0.0034
GEN-2020-043 | 02 - Nebraska | 647916 | S916 8 | 69 | 23.8515 | 23.8599 | 0.0084
GEN-2020-043 | 02 - Nebraska | 647917 | S917 8 | 69 | 26.0286 | 26.0392 | 0.0106
GEN-2020-043 | 02 - Nebraska | 647918 | S918 8 | 69 | 23.0121 | 23.0211 | 0.009
GEN-2020-043 | 02 - Nebraska | 647919 | S919 8 | 69 | 21.5821 | 21.5899 | 0.0078
GEN-2020-043 | 02 - Nebraska | 647921 | S921 8 | 69 | 26.5487 | 26.5599 | 0.0112
GEN-2020-043 | 02 - Nebraska | 647928 | S928 8 | 69 | 17.2436 | 17.2471 | 0.0035
GEN-2020-043 | 02 - Nebraska | 647930 | S930 8 | 69 | 21.6307 | 21.6387 | 0.008
GEN-2020-043 | 02 - Nebraska | 647937 | S937 8 | 69 | 9.1415 | 9.1423 | 0.0008
GEN-2020-043 | 02 - Nebraska | 647939 | S939 8 | 69 | 20.1944 | 20.2016 | 0.0072
GEN-2020-043 | 02 - Nebraska | 647940 | S940 8 | 69 | 20.9578 | 20.9645 | 0.0067
GEN-2020-043 | 02 - Nebraska | 647942 | S942 8 | 69 | 16.2078 | 16.2113 | 0.0035
GEN-2020-043 | 02 - Nebraska | 647950 | S950 8 | 69 | 20.4025 | 20.4096 | 0.0071
GEN-2020-043 | 02 - Nebraska | 647983 | S983 8 | 69 | 7.6236 | 7.624 | 0.0004
GEN-2020-043 | 02 - Nebraska | 647984 | S984 8 | 69 | 7.9743 | 7.9748 | 0.0005
GEN-2020-043 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.471 | 21.476 | 0.005
GEN-2020-043 | 02 - Nebraska | 760746 | GEN-2017-115 | 345 | 7.2223 | 7.2225 | 0.0002
GEN-2020-043 | 02 - Nebraska | 762069 | G17-105TAP | 161 | 8.7989 | 8.8 | 0.0011
GEN-2020-043 | 02 - Nebraska | 762070 | GEN-2017-105 | 161 | 8.7989 | 8.8 | 0.0011
GEN-2020-043 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.4061 | 22.4309 | 0.0248
GEN-2020-043 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 24.3667 | 24.3816 | 0.0149
GEN-2020-043 | 02 - Nebraska | 762712 | G18-037-TAP | 161 | 35.6312 | 35.6731 | 0.0419
GEN-2020-043 | 02 - Nebraska | 762713 | GEN-2018-037 | 161 | 33.4545 | 33.4913 | 0.0368
GEN-2020-043 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.7822 | 17.7927 | 0.0105
GEN-2020-043 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.415 | 17.425 | 0.01
GEN-2020-043 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 24.0898 | 24.1043 | 0.0145
GEN-2020-043 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 24.3684 | 24.3832 | 0.0148
GEN-2020-043 | 02 - Nebraska | 764720 | GEN-2020-043 | 161 | 33.7622 | 33.9911 | 0.2289
GEN-2020-043 | 02 - Nebraska | 764735 | GEN-2020-044 | 161 | 33.7622 | 33.9911 | 0.2289
GEN-2020-043 | 02 - Nebraska | 764750 | GEN-2020-045 | 161 | 33.7622 | 33.9911 | 0.2289
GEN-2020-043 | 02 - Nebraska | 764765 | GEN-2020-078 | 161 | 16.4346 | 16.45 | 0.0154
GEN-2020-043 | 02 - Nebraska | 764775 | G20-078-TAP | 161 | 16.4697 | 16.4852 | 0.0155
GEN-2020-043 | 02 - Nebraska | 764795 | GEN-2020-094 | 345 | 11.9477 | 11.9489 | 0.0012
GEN-2020-043 | 02 - Nebraska | 764805 | G20-094-TAP | 345 | 16.8113 | 16.8137 | 0.0024
GEN-2020-044 | 02 - Nebraska | 541510 | HOLT 7 | 345 | 8.9103 | 8.9106 | 0.0003
GEN-2020-044 | 02 - Nebraska | 541511 | ROCKCK7 | 345 | 6.9452 | 6.9454 | 0.0002
GEN-2020-044 | 02 - Nebraska | 541517 | HOLT_REACT7 | 345 | 8.8652 | 8.8655 | 0.0003
GEN-2020-044 | 02 - Nebraska | 541543 | OUTLAW | 345 | 5.7488 | 5.749 | 0.0002
GEN-2020-044 | 02 - Nebraska | 635000 | CBLUFFS3 | 345 | 32.2098 | 32.2342 | 0.0244
GEN-2020-044 | 02 - Nebraska | 635001 | CBLUFFS5 | 161 | 39.7959 | 39.8181 | 0.0222
GEN-2020-044 | 02 - Nebraska | 635003 | SUB701 5 | 161 | 21.5442 | 21.5548 | 0.0106
GEN-2020-044 | 02 - Nebraska | 635004 | SUB701 8 | 69 | 22.379 | 22.383 | 0.004
GEN-2020-044 | 02 - Nebraska | 635005 | SUB702 5 | 161 | 20.9024 | 20.9116 | 0.0092
GEN-2020-044 | 02 - Nebraska | 635013 | PNYCRK 3 | 345 | 29.2903 | 29.31 | 0.0197
GEN-2020-044 | 02 - Nebraska | 635014 | OVRLND 3 | 345 | 27.483 | 27.5003 | 0.0173
GEN-2020-044 | 02 - Nebraska | 635016 | STHLND 3 | 345 | 29.2554 | 29.2751 | 0.0197
GEN-2020-044 | 02 - Nebraska | 635200 | RAUN 3 | 345 | 28.7119 | 28.7143 | 0.0024
GEN-2020-044 | 02 - Nebraska | 635201 | RAUN 5 | 161 | 28.5056 | 28.5069 | 0.0013
GEN-2020-044 | 02 - Nebraska | 640139 | COOPER 3 | 345 | 26.9689 | 26.9714 | 0.0025
GEN-2020-044 | 02 - Nebraska | 640300 | OAKLAND7 | 115 | 7.9543 | 7.9546 | 0.0003
GEN-2020-044 | 02 - Nebraska | 640377 | TEKAMAH5 | 161 | 9.3775 | 9.379 | 0.0015
GEN-2020-044 | 02 - Nebraska | 640378 | TEKAMAH7 | 115 | 8.6258 | 8.6265 | 0.0007
GEN-2020-044 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.5446 | 30.5745 | 0.0299
GEN-2020-044 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.4644 | 23.4917 | 0.0273
GEN-2020-044 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.3905 | 30.4229 | 0.0324
GEN-2020-044 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.6742 | 33.718 | 0.0438
GEN-2020-044 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.733 | 35.7822 | 0.0492
GEN-2020-044 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30.0881 | 30.0963 | 0.0082
GEN-2020-044 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.1708 | 26.2179 | 0.0471
GEN-2020-044 | 02 - Nebraska | 645740 | S3740 3 | 345 | 24.3684 | 24.3832 | 0.0148
GEN-2020-044 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.9791 | 24.0017 | 0.0226
GEN-2020-044 | 02 - Nebraska | 646201 | S1201 5 | 161 | 32.0114 | 32.0427 | 0.0313
GEN-2020-044 | 02 - Nebraska | 646206 | S1206 5 | 161 | 44.8167 | 44.8616 | 0.0449
GEN-2020-044 | 02 - Nebraska | 646209 | S1209 5 | 161 | 48.2454 | 48.4181 | 0.1727
GEN-2020-044 | 02 - Nebraska | 646210 | S1210 5 | 161 | 28.2222 | 28.2486 | 0.0264
GEN-2020-044 | 02 - Nebraska | 646211 | S1211 5 | 161 | 36.2605 | 36.3041 | 0.0436
GEN-2020-044 | 02 - Nebraska | 646216 | S1216 5 | 161 | 30.87 | 30.9002 | 0.0302
GEN-2020-044 | 02 - Nebraska | 646217 | S1217 5 | 161 | 33.6464 | 33.6872 | 0.0408
GEN-2020-044 | 02 - Nebraska | 646220 | S1220 5 | 161 | 28.8429 | 28.8688 | 0.0259
GEN-2020-044 | 02 - Nebraska | 646221 | S1221 5 | 161 | 36.2703 | 36.3278 | 0.0575
GEN-2020-044 | 02 - Nebraska | 646226 | S1226 5 | 161 | 25.6391 | 25.6682 | 0.0291
GEN-2020-044 | 02 - Nebraska | 646227 | S1227 5 | 161 | 33.0931 | 33.142 | 0.0489
GEN-2020-044 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.1299 | 44.2376 | 0.1077
GEN-2020-044 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26.9822 | 26.9988 | 0.0166
GEN-2020-044 | 02 - Nebraska | 646233 | S1233 5 | 161 | 30.0945 | 30.1276 | 0.0331
GEN-2020-044 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27.4564 | 27.4924 | 0.036
GEN-2020-044 | 02 - Nebraska | 646235 | S1235 5 | 161 | 34.8526 | 34.9268 | 0.0742
GEN-2020-044 | 02 - Nebraska | 646236 | S1236 5 | 161 | 24.9867 | 25.0452 | 0.0585
GEN-2020-044 | 02 - Nebraska | 646237 | S1237 5 | 161 | 22.4002 | 22.4417 | 0.0415
GEN-2020-044 | 02 - Nebraska | 646244 | S1244 5 | 161 | 22.2526 | 22.263 | 0.0104
GEN-2020-044 | 02 - Nebraska | 646250 | S1250 5 | 161 | 35.6454 | 35.7004 | 0.055
GEN-2020-044 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.2685 | 33.3039 | 0.0354
GEN-2020-044 | 02 - Nebraska | 646252 | S1252 5 | 161 | 30.4839 | 30.6053 | 0.1214
GEN-2020-044 | 02 - Nebraska | 646253 | S1253 5 | 161 | 28.2563 | 28.3027 | 0.0464
GEN-2020-044 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.7557 | 34.7844 | 0.0287
GEN-2020-044 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.803 | 50.8724 | 0.0694
GEN-2020-044 | 02 - Nebraska | 646256 | S1256 5 | 161 | 23.4352 | 23.458 | 0.0228
GEN-2020-044 | 02 - Nebraska | 646259 | S1259 5 | 161 | 40.3557 | 40.3943 | 0.0386
GEN-2020-044 | 02 - Nebraska | 646291 | S1291 5 | 161 | 7.1322 | 7.1338 | 0.0016
GEN-2020-044 | 02 - Nebraska | 646297 | S1297 5 | 161 | 19.2407 | 19.2544 | 0.0137
GEN-2020-044 | 02 - Nebraska | 646298 | S1298 5 | 161 | 30.3007 | 30.3321 | 0.0314
GEN-2020-044 | 02 - Nebraska | 646299 | S1299 5 | 161 | 28.0718 | 28.0974 | 0.0256
GEN-2020-044 | 02 - Nebraska | 646305 | S1305 5 | 161 | 28.7855 | 28.8136 | 0.0281
GEN-2020-044 | 02 - Nebraska | 646341 | S1341 5 | 161 | 27.9971 | 28.0234 | 0.0263
GEN-2020-044 | 02 - Nebraska | 646345 | S1345 5 | 161 | 23.0608 | 23.1175 | 0.0567
GEN-2020-044 | 02 - Nebraska | 646347 | S1347 5 | 161 | 33.7635 | 33.9924 | 0.2289
GEN-2020-044 | 02 - Nebraska | 646361 | S1361 5 | 161 | 44.3445 | 44.3845 | 0.04
GEN-2020-044 | 02 - Nebraska | 646367 | S1367 5 | 161 | 22.1732 | 22.2072 | 0.034
GEN-2020-044 | 02 - Nebraska | 647006 | S906 N 8 | 69 | 32.2741 | 32.2848 | 0.0107
GEN-2020-044 | 02 - Nebraska | 647104 | MUD LNG8 | 69 | 14.6993 | 14.7031 | 0.0038
GEN-2020-044 | 02 - Nebraska | 647291 | S991 E 8 | 69 | 12.5483 | 12.5495 | 0.0012
GEN-2020-044 | 02 - Nebraska | 647422 | FREM B 8 | 69 | 14.5714 | 14.5724 | 0.001
GEN-2020-044 | 02 - Nebraska | 647902 | S902 8 | 69 | 9.1904 | 9.1911 | 0.0007
GEN-2020-044 | 02 - Nebraska | 647906 | S906 S 8 | 69 | 32.7035 | 32.7128 | 0.0093
GEN-2020-044 | 02 - Nebraska | 647907 | S907 8 | 69 | 18.0303 | 18.0351 | 0.0048
GEN-2020-044 | 02 - Nebraska | 647909 | S909 8 | 69 | 27.1883 | 27.2018 | 0.0135
GEN-2020-044 | 02 - Nebraska | 647911 | S911 8 | 69 | 21.3161 | 21.3226 | 0.0065
GEN-2020-044 | 02 - Nebraska | 647913 | S913 8 | 69 | 16.2031 | 16.2065 | 0.0034
GEN-2020-044 | 02 - Nebraska | 647916 | S916 8 | 69 | 23.8515 | 23.8599 | 0.0084
GEN-2020-044 | 02 - Nebraska | 647917 | S917 8 | 69 | 26.0286 | 26.0392 | 0.0106
GEN-2020-044 | 02 - Nebraska | 647918 | S918 8 | 69 | 23.0121 | 23.0211 | 0.009
GEN-2020-044 | 02 - Nebraska | 647919 | S919 8 | 69 | 21.5821 | 21.5899 | 0.0078
GEN-2020-044 | 02 - Nebraska | 647921 | S921 8 | 69 | 26.5487 | 26.5599 | 0.0112
GEN-2020-044 | 02 - Nebraska | 647928 | S928 8 | 69 | 17.2436 | 17.2471 | 0.0035
GEN-2020-044 | 02 - Nebraska | 647930 | S930 8 | 69 | 21.6307 | 21.6387 | 0.008
GEN-2020-044 | 02 - Nebraska | 647937 | S937 8 | 69 | 9.1415 | 9.1423 | 0.0008
GEN-2020-044 | 02 - Nebraska | 647939 | S939 8 | 69 | 20.1944 | 20.2016 | 0.0072
GEN-2020-044 | 02 - Nebraska | 647940 | S940 8 | 69 | 20.9578 | 20.9645 | 0.0067
GEN-2020-044 | 02 - Nebraska | 647942 | S942 8 | 69 | 16.2078 | 16.2113 | 0.0035
GEN-2020-044 | 02 - Nebraska | 647950 | S950 8 | 69 | 20.4025 | 20.4096 | 0.0071
GEN-2020-044 | 02 - Nebraska | 647983 | S983 8 | 69 | 7.6236 | 7.624 | 0.0004
GEN-2020-044 | 02 - Nebraska | 647984 | S984 8 | 69 | 7.9743 | 7.9748 | 0.0005
GEN-2020-044 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.471 | 21.476 | 0.005
GEN-2020-044 | 02 - Nebraska | 760746 | GEN-2017-115 | 345 | 7.2223 | 7.2225 | 0.0002
GEN-2020-044 | 02 - Nebraska | 762069 | G17-105TAP | 161 | 8.7989 | 8.8 | 0.0011
GEN-2020-044 | 02 - Nebraska | 762070 | GEN-2017-105 | 161 | 8.7989 | 8.8 | 0.0011
GEN-2020-044 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.4061 | 22.4309 | 0.0248
GEN-2020-044 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 24.3667 | 24.3816 | 0.0149
GEN-2020-044 | 02 - Nebraska | 762712 | G18-037-TAP | 161 | 35.6312 | 35.6731 | 0.0419
GEN-2020-044 | 02 - Nebraska | 762713 | GEN-2018-037 | 161 | 33.4545 | 33.4913 | 0.0368
GEN-2020-044 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.7822 | 17.7927 | 0.0105
GEN-2020-044 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.415 | 17.425 | 0.01
GEN-2020-044 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 24.0898 | 24.1043 | 0.0145
GEN-2020-044 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 24.3684 | 24.3832 | 0.0148
GEN-2020-044 | 02 - Nebraska | 764720 | GEN-2020-043 | 161 | 33.7622 | 33.9911 | 0.2289
GEN-2020-044 | 02 - Nebraska | 764735 | GEN-2020-044 | 161 | 33.7622 | 33.9911 | 0.2289
GEN-2020-044 | 02 - Nebraska | 764750 | GEN-2020-045 | 161 | 33.7622 | 33.9911 | 0.2289
GEN-2020-044 | 02 - Nebraska | 764765 | GEN-2020-078 | 161 | 16.4346 | 16.45 | 0.0154
GEN-2020-044 | 02 - Nebraska | 764775 | G20-078-TAP | 161 | 16.4697 | 16.4852 | 0.0155
GEN-2020-044 | 02 - Nebraska | 764795 | GEN-2020-094 | 345 | 11.9477 | 11.9489 | 0.0012
GEN-2020-044 | 02 - Nebraska | 764805 | G20-094-TAP | 345 | 16.8113 | 16.8137 | 0.0024
GEN-2020-045 | 02 - Nebraska | 541510 | HOLT 7 | 345 | 8.9103 | 8.9106 | 0.0003
GEN-2020-045 | 02 - Nebraska | 541511 | ROCKCK7 | 345 | 6.9452 | 6.9454 | 0.0002
GEN-2020-045 | 02 - Nebraska | 541517 | HOLT_REACT7 | 345 | 8.8652 | 8.8655 | 0.0003
GEN-2020-045 | 02 - Nebraska | 541543 | OUTLAW | 345 | 5.7488 | 5.749 | 0.0002
GEN-2020-045 | 02 - Nebraska | 635000 | CBLUFFS3 | 345 | 32.2098 | 32.2342 | 0.0244
GEN-2020-045 | 02 - Nebraska | 635001 | CBLUFFS5 | 161 | 39.7959 | 39.8181 | 0.0222
GEN-2020-045 | 02 - Nebraska | 635003 | SUB701 5 | 161 | 21.5442 | 21.5548 | 0.0106
GEN-2020-045 | 02 - Nebraska | 635004 | SUB701 8 | 69 | 22.379 | 22.383 | 0.004
GEN-2020-045 | 02 - Nebraska | 635005 | SUB702 5 | 161 | 20.9024 | 20.9116 | 0.0092
GEN-2020-045 | 02 - Nebraska | 635013 | PNYCRK 3 | 345 | 29.2903 | 29.31 | 0.0197
GEN-2020-045 | 02 - Nebraska | 635014 | OVRLND 3 | 345 | 27.483 | 27.5003 | 0.0173
GEN-2020-045 | 02 - Nebraska | 635016 | STHLND 3 | 345 | 29.2554 | 29.2751 | 0.0197
GEN-2020-045 | 02 - Nebraska | 635200 | RAUN 3 | 345 | 28.7119 | 28.7143 | 0.0024
GEN-2020-045 | 02 - Nebraska | 635201 | RAUN 5 | 161 | 28.5056 | 28.5069 | 0.0013
GEN-2020-045 | 02 - Nebraska | 640139 | COOPER 3 | 345 | 26.9689 | 26.9714 | 0.0025
GEN-2020-045 | 02 - Nebraska | 640300 | OAKLAND7 | 115 | 7.9543 | 7.9546 | 0.0003
GEN-2020-045 | 02 - Nebraska | 640377 | TEKAMAH5 | 161 | 9.3775 | 9.379 | 0.0015
GEN-2020-045 | 02 - Nebraska | 640378 | TEKAMAH7 | 115 | 8.6258 | 8.6265 | 0.0007
GEN-2020-045 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.5446 | 30.5745 | 0.0299
GEN-2020-045 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.4644 | 23.4917 | 0.0273
GEN-2020-045 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.3905 | 30.4229 | 0.0324
GEN-2020-045 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.6742 | 33.718 | 0.0438
GEN-2020-045 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.733 | 35.7822 | 0.0492
GEN-2020-045 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30.0881 | 30.0963 | 0.0082
GEN-2020-045 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.1708 | 26.2179 | 0.0471
GEN-2020-045 | 02 - Nebraska | 645740 | S3740 3 | 345 | 24.3684 | 24.3832 | 0.0148
GEN-2020-045 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.9791 | 24.0017 | 0.0226
GEN-2020-045 | 02 - Nebraska | 646201 | S1201 5 | 161 | 32.0114 | 32.0427 | 0.0313
GEN-2020-045 | 02 - Nebraska | 646206 | S1206 5 | 161 | 44.8167 | 44.8616 | 0.0449
GEN-2020-045 | 02 - Nebraska | 646209 | S1209 5 | 161 | 48.2454 | 48.4181 | 0.1727
GEN-2020-045 | 02 - Nebraska | 646210 | S1210 5 | 161 | 28.2222 | 28.2486 | 0.0264
GEN-2020-045 | 02 - Nebraska | 646211 | S1211 5 | 161 | 36.2605 | 36.3041 | 0.0436
GEN-2020-045 | 02 - Nebraska | 646216 | S1216 5 | 161 | 30.87 | 30.9002 | 0.0302
GEN-2020-045 | 02 - Nebraska | 646217 | S1217 5 | 161 | 33.6464 | 33.6872 | 0.0408
GEN-2020-045 | 02 - Nebraska | 646220 | S1220 5 | 161 | 28.8429 | 28.8688 | 0.0259
GEN-2020-045 | 02 - Nebraska | 646221 | S1221 5 | 161 | 36.2703 | 36.3278 | 0.0575
GEN-2020-045 | 02 - Nebraska | 646226 | S1226 5 | 161 | 25.6391 | 25.6682 | 0.0291
GEN-2020-045 | 02 - Nebraska | 646227 | S1227 5 | 161 | 33.0931 | 33.142 | 0.0489
GEN-2020-045 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.1299 | 44.2376 | 0.1077
GEN-2020-045 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26.9822 | 26.9988 | 0.0166
GEN-2020-045 | 02 - Nebraska | 646233 | S1233 5 | 161 | 30.0945 | 30.1276 | 0.0331
GEN-2020-045 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27.4564 | 27.4924 | 0.036
GEN-2020-045 | 02 - Nebraska | 646235 | S1235 5 | 161 | 34.8526 | 34.9268 | 0.0742
GEN-2020-045 | 02 - Nebraska | 646236 | S1236 5 | 161 | 24.9867 | 25.0452 | 0.0585
GEN-2020-045 | 02 - Nebraska | 646237 | S1237 5 | 161 | 22.4002 | 22.4417 | 0.0415
GEN-2020-045 | 02 - Nebraska | 646244 | S1244 5 | 161 | 22.2526 | 22.263 | 0.0104
GEN-2020-045 | 02 - Nebraska | 646250 | S1250 5 | 161 | 35.6454 | 35.7004 | 0.055
GEN-2020-045 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.2685 | 33.3039 | 0.0354
GEN-2020-045 | 02 - Nebraska | 646252 | S1252 5 | 161 | 30.4839 | 30.6053 | 0.1214
GEN-2020-045 | 02 - Nebraska | 646253 | S1253 5 | 161 | 28.2563 | 28.3027 | 0.0464
GEN-2020-045 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.7557 | 34.7844 | 0.0287
GEN-2020-045 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.803 | 50.8724 | 0.0694
GEN-2020-045 | 02 - Nebraska | 646256 | S1256 5 | 161 | 23.4352 | 23.458 | 0.0228
GEN-2020-045 | 02 - Nebraska | 646259 | S1259 5 | 161 | 40.3557 | 40.3943 | 0.0386
GEN-2020-045 | 02 - Nebraska | 646291 | S1291 5 | 161 | 7.1322 | 7.1338 | 0.0016
GEN-2020-045 | 02 - Nebraska | 646297 | S1297 5 | 161 | 19.2407 | 19.2544 | 0.0137
GEN-2020-045 | 02 - Nebraska | 646298 | S1298 5 | 161 | 30.3007 | 30.3321 | 0.0314
GEN-2020-045 | 02 - Nebraska | 646299 | S1299 5 | 161 | 28.0718 | 28.0974 | 0.0256
GEN-2020-045 | 02 - Nebraska | 646305 | S1305 5 | 161 | 28.7855 | 28.8136 | 0.0281
GEN-2020-045 | 02 - Nebraska | 646341 | S1341 5 | 161 | 27.9971 | 28.0234 | 0.0263
GEN-2020-045 | 02 - Nebraska | 646345 | S1345 5 | 161 | 23.0608 | 23.1175 | 0.0567
GEN-2020-045 | 02 - Nebraska | 646347 | S1347 5 | 161 | 33.7635 | 33.9924 | 0.2289
GEN-2020-045 | 02 - Nebraska | 646361 | S1361 5 | 161 | 44.3445 | 44.3845 | 0.04
GEN-2020-045 | 02 - Nebraska | 646367 | S1367 5 | 161 | 22.1732 | 22.2072 | 0.034
GEN-2020-045 | 02 - Nebraska | 647006 | S906 N 8 | 69 | 32.2741 | 32.2848 | 0.0107
GEN-2020-045 | 02 - Nebraska | 647104 | MUD LNG8 | 69 | 14.6993 | 14.7031 | 0.0038
GEN-2020-045 | 02 - Nebraska | 647291 | S991 E 8 | 69 | 12.5483 | 12.5495 | 0.0012
GEN-2020-045 | 02 - Nebraska | 647422 | FREM B 8 | 69 | 14.5714 | 14.5724 | 0.001
GEN-2020-045 | 02 - Nebraska | 647902 | S902 8 | 69 | 9.1904 | 9.1911 | 0.0007
GEN-2020-045 | 02 - Nebraska | 647906 | S906 S 8 | 69 | 32.7035 | 32.7128 | 0.0093
GEN-2020-045 | 02 - Nebraska | 647907 | S907 8 | 69 | 18.0303 | 18.0351 | 0.0048
GEN-2020-045 | 02 - Nebraska | 647909 | S909 8 | 69 | 27.1883 | 27.2018 | 0.0135
GEN-2020-045 | 02 - Nebraska | 647911 | S911 8 | 69 | 21.3161 | 21.3226 | 0.0065
GEN-2020-045 | 02 - Nebraska | 647913 | S913 8 | 69 | 16.2031 | 16.2065 | 0.0034
GEN-2020-045 | 02 - Nebraska | 647916 | S916 8 | 69 | 23.8515 | 23.8599 | 0.0084
GEN-2020-045 | 02 - Nebraska | 647917 | S917 8 | 69 | 26.0286 | 26.0392 | 0.0106
GEN-2020-045 | 02 - Nebraska | 647918 | S918 8 | 69 | 23.0121 | 23.0211 | 0.009
GEN-2020-045 | 02 - Nebraska | 647919 | S919 8 | 69 | 21.5821 | 21.5899 | 0.0078
GEN-2020-045 | 02 - Nebraska | 647921 | S921 8 | 69 | 26.5487 | 26.5599 | 0.0112
GEN-2020-045 | 02 - Nebraska | 647928 | S928 8 | 69 | 17.2436 | 17.2471 | 0.0035
GEN-2020-045 | 02 - Nebraska | 647930 | S930 8 | 69 | 21.6307 | 21.6387 | 0.008
GEN-2020-045 | 02 - Nebraska | 647937 | S937 8 | 69 | 9.1415 | 9.1423 | 0.0008
GEN-2020-045 | 02 - Nebraska | 647939 | S939 8 | 69 | 20.1944 | 20.2016 | 0.0072
GEN-2020-045 | 02 - Nebraska | 647940 | S940 8 | 69 | 20.9578 | 20.9645 | 0.0067
GEN-2020-045 | 02 - Nebraska | 647942 | S942 8 | 69 | 16.2078 | 16.2113 | 0.0035
GEN-2020-045 | 02 - Nebraska | 647950 | S950 8 | 69 | 20.4025 | 20.4096 | 0.0071
GEN-2020-045 | 02 - Nebraska | 647983 | S983 8 | 69 | 7.6236 | 7.624 | 0.0004
GEN-2020-045 | 02 - Nebraska | 647984 | S984 8 | 69 | 7.9743 | 7.9748 | 0.0005
GEN-2020-045 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.471 | 21.476 | 0.005
GEN-2020-045 | 02 - Nebraska | 760746 | GEN-2017-115 | 345 | 7.2223 | 7.2225 | 0.0002
GEN-2020-045 | 02 - Nebraska | 762069 | G17-105TAP | 161 | 8.7989 | 8.8 | 0.0011
GEN-2020-045 | 02 - Nebraska | 762070 | GEN-2017-105 | 161 | 8.7989 | 8.8 | 0.0011
GEN-2020-045 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.4061 | 22.4309 | 0.0248
GEN-2020-045 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 24.3667 | 24.3816 | 0.0149
GEN-2020-045 | 02 - Nebraska | 762712 | G18-037-TAP | 161 | 35.6312 | 35.6731 | 0.0419
GEN-2020-045 | 02 - Nebraska | 762713 | GEN-2018-037 | 161 | 33.4545 | 33.4913 | 0.0368
GEN-2020-045 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.7822 | 17.7927 | 0.0105
GEN-2020-045 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.415 | 17.425 | 0.01
GEN-2020-045 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 24.0898 | 24.1043 | 0.0145
GEN-2020-045 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 24.3684 | 24.3832 | 0.0148
GEN-2020-045 | 02 - Nebraska | 764720 | GEN-2020-043 | 161 | 33.7622 | 33.9911 | 0.2289
GEN-2020-045 | 02 - Nebraska | 764735 | GEN-2020-044 | 161 | 33.7622 | 33.9911 | 0.2289
GEN-2020-045 | 02 - Nebraska | 764750 | GEN-2020-045 | 161 | 33.7622 | 33.9911 | 0.2289
GEN-2020-045 | 02 - Nebraska | 764765 | GEN-2020-078 | 161 | 16.4346 | 16.45 | 0.0154
GEN-2020-045 | 02 - Nebraska | 764775 | G20-078-TAP | 161 | 16.4697 | 16.4852 | 0.0155
GEN-2020-045 | 02 - Nebraska | 764795 | GEN-2020-094 | 345 | 11.9477 | 11.9489 | 0.0012
GEN-2020-045 | 02 - Nebraska | 764805 | G20-094-TAP | 345 | 16.8113 | 16.8137 | 0.0024
GEN-2020-069 | 02 - Nebraska | 640050 | AINSWND7 | 115 | 3.7614 | 3.8501 | 0.0887
GEN-2020-069 | 02 - Nebraska | 640051 | AINSWRT7 | 115 | 3.461 | 3.5729 | 0.1119
GEN-2020-069 | 02 - Nebraska | 640052 | AINSWRT8 | 69 | 1.9842 | 2.0052 | 0.021
GEN-2020-069 | 02 - Nebraska | 640096 | CALAMS 7 | 115 | 3.5208 | 3.5607 | 0.0399
GEN-2020-069 | 02 - Nebraska | 640117 | CODY 7 | 115 | 0.94 | 1.1049 | 0.1649
GEN-2020-069 | 02 - Nebraska | 640210 | HARMONY7 | 115 | 1.8519 | 2.0536 | 0.2017
GEN-2020-069 | 02 - Nebraska | 640351 | ST.FRANC | 115 | 1.8983 | 2.0096 | 0.1113
GEN-2020-069 | 02 - Nebraska | 640367 | STUART 7 | 115 | 2.646 | 2.6688 | 0.0228
GEN-2020-069 | 02 - Nebraska | 640394 | VALTN.W7 | 115 | 1.7247 | 1.9687 | 0.244
GEN-2020-069 | 02 - Nebraska | 640580 | BASSETT 7 | 115 | 2.72 | 2.7659 | 0.0459
GEN-2020-069 | 02 - Nebraska | 640581 | BASSETT 8 | 69 | 2.7581 | 2.7858 | 0.0277
GEN-2020-069 | 02 - Nebraska | 652482 | MISSION7 | 115 | 2.1916 | 2.2702 | 0.0786
GEN-2020-069 | 02 - Nebraska | 764465 | GEN-2020-069 | 115 | 1.1323 | 1.3952 | 0.2629
GEN-2020-069 | 02 - Nebraska | 764475 | G20-069-TAP | 115 | 1.1595 | 1.4207 | 0.2612
GEN-2020-070 | 02 - Nebraska | 523118 | BUFF_DUNES 7 | 345 | 5.5676 | 5.5737 | 0.0061
GEN-2020-070 | 02 - Nebraska | 523853 | FINNEY 7 | 345 | 9.0786 | 9.0947 | 0.0161
GEN-2020-070 | 02 - Nebraska | 530551 | SALINE 3 | 115 | 4.9605 | 4.9761 | 0.0156
GEN-2020-070 | 02 - Nebraska | 530552 | GORHAM 3 | 115 | 3.2023 | 3.2101 | 0.0078
GEN-2020-070 | 02 - Nebraska | 530553 | S HAYS 3 | 115 | 8.5943 | 8.6501 | 0.0558
GEN-2020-070 | 02 - Nebraska | 530558 | KNOLL N 6 | 230 | 10.475 | 10.7064 | 0.2314
GEN-2020-070 | 02 - Nebraska | 530560 | WKNNY 3 | 115 | 2.2368 | 2.2405 | 0.0037
GEN-2020-070 | 02 - Nebraska | 530561 | KNOLL 3 | 115 | 10.5399 | 10.6228 | 0.0829
GEN-2020-070 | 02 - Nebraska | 530562 | HAYS 3 | 115 | 7.8344 | 7.8807 | 0.0463
GEN-2020-070 | 02 - Nebraska | 530581 | N HAYS3 | 115 | 9.4677 | 9.535 | 0.0673
GEN-2020-070 | 02 - Nebraska | 530582 | S HAYS6 | 230 | 8.6357 | 8.7501 | 0.1144
GEN-2020-070 | 02 - Nebraska | 530583 | POSTROCK7 | 345 | 7.6187 | 7.9233 | 0.3046
GEN-2020-070 | 02 - Nebraska | 530584 | POSTROCK6 | 230 | 10.5581 | 10.7949 | 0.2368
GEN-2020-070 | 02 - Nebraska | 530590 | BEMIS 3 | 115 | 3.9893 | 3.9994 | 0.0101
GEN-2020-070 | 02 - Nebraska | 530592 | SMOKYHL6 | 230 | 6.1914 | 6.2077 | 0.0163
GEN-2020-070 | 02 - Nebraska | 530593 | SMKYP1 6 | 230 | 5.4563 | 5.4685 | 0.0122
GEN-2020-070 | 02 - Nebraska | 530599 | SMKYP2 6 | 230 | 5.718 | 5.7318 | 0.0138
GEN-2020-070 | 02 - Nebraska | 530605 | REDLIN 3 | 115 | 3.8643 | 3.8712 | 0.0069
GEN-2020-070 | 02 - Nebraska | 530610 | SHAYS_230 | 230 | 3.5109 | 3.5257 | 0.0148
GEN-2020-070 | 02 - Nebraska | 530676 | GMEC 3 | 115 | 9.9787 | 10.0525 | 0.0738
GEN-2020-070 | 02 - Nebraska | 530677 | OGALATP3 | 115 | 2.6473 | 2.6525 | 0.0052
GEN-2020-070 | 02 - Nebraska | 530680 | HEIZER 6 | 230 | 7.9208 | 7.9655 | 0.0447
GEN-2020-070 | 02 - Nebraska | 530684 | RUSLPMP3 | 115 | 2.0989 | 2.1022 | 0.0033
GEN-2020-070 | 02 - Nebraska | 530694 | VINE2 3 | 115 | 7.922 | 7.9694 | 0.0474
GEN-2020-070 | 02 - Nebraska | 530695 | CHETOLAH3 | 115 | 8.5476 | 8.6028 | 0.0552
GEN-2020-070 | 02 - Nebraska | 530702 | BUCKEYE_230 | 230 | 7.8553 | 7.9803 | 0.125
GEN-2020-070 | 02 - Nebraska | 530714 | ANGUS 3 | 115 | 5.3552 | 5.3769 | 0.0217
GEN-2020-070 | 02 - Nebraska | 530720 | KNOLL S 6 | 230 | 10.475 | 10.7064 | 0.2314
GEN-2020-070 | 02 - Nebraska | 530721 | VINEDE_N | 115 | 7.922 | 7.9694 | 0.0474
GEN-2020-070 | 02 - Nebraska | 530722 | VINEDE_S | 115 | 7.922 | 7.9694 | 0.0474
GEN-2020-070 | 02 - Nebraska | 530725 | PFEIFER 3 | 115 | 3.5301 | 3.5395 | 0.0094
GEN-2020-070 | 02 - Nebraska | 531448 | HOLCOMB3 | 115 | 20.8354 | 20.8468 | 0.0114
GEN-2020-070 | 02 - Nebraska | 531449 | HOLCOMB7 | 345 | 9.132 | 9.1483 | 0.0163
GEN-2020-070 | 02 - Nebraska | 531465 | SETAB 7 | 345 | 6.7899 | 6.7971 | 0.0072
GEN-2020-070 | 02 - Nebraska | 531469 | SPERVIL7 | 345 | 11.1235 | 11.211 | 0.0875
GEN-2020-070 | 02 - Nebraska | 531492 | OG ONEOK | 115 | 2.1584 | 2.1619 | 0.0035
GEN-2020-070 | 02 - Nebraska | 531497 | TURKEYR3 | 115 | 1.8074 | 1.8098 | 0.0024
GEN-2020-070 | 02 - Nebraska | 531501 | BUCKNER7 | 345 | 8.532 | 8.5609 | 0.0289
GEN-2020-070 | 02 - Nebraska | 531502 | CIMRRN 7 | 345 | 6.9148 | 6.9338 | 0.019
GEN-2020-070 | 02 - Nebraska | 531504 | CIMWD2 7 | 345 | 7.0306 | 7.0499 | 0.0193
GEN-2020-070 | 02 - Nebraska | 532873 | SUMMIT 6 | 230 | 12.5146 | 12.5284 | 0.0138
GEN-2020-070 | 02 - Nebraska | 539117 | SPRVILL-EHVB | 230 | 11.2414 | 11.2959 | 0.0545
GEN-2020-070 | 02 - Nebraska | 539628 | NW-DGTP3 | 115 | 3.5546 | 3.5561 | 0.0015
GEN-2020-070 | 02 - Nebraska | 539641 | NW-DODG3 | 115 | 3.6205 | 3.6222 | 0.0017
GEN-2020-070 | 02 - Nebraska | 539645 | DCBEEF3 | 115 | 6.7827 | 6.7889 | 0.0062
GEN-2020-070 | 02 - Nebraska | 539667 | HAGGARD3 | 115 | 2.5263 | 2.5269 | 0.0006
GEN-2020-070 | 02 - Nebraska | 539671 | FTDODGE3 | 115 | 9.2173 | 9.2287 | 0.0114
GEN-2020-070 | 02 - Nebraska | 539678 | GRTBEND3 | 115 | 11.131 | 11.1669 | 0.0359
GEN-2020-070 | 02 - Nebraska | 539679 | GRTBEND6 | 230 | 7.9669 | 8.0122 | 0.0453
GEN-2020-070 | 02 - Nebraska | 539680 | N-DODGE3 | 115 | 4.6281 | 4.631 | 0.0029
GEN-2020-070 | 02 - Nebraska | 539684 | OTISSUB3 | 115 | 2.9585 | 2.9611 | 0.0026
GEN-2020-070 | 02 - Nebraska | 539688 | S-DODGE3 | 115 | 6.6535 | 6.6592 | 0.0057
GEN-2020-070 | 02 - Nebraska | 539694 | SPEARVL3 | 115 | 9.7485 | 9.7661 | 0.0176
GEN-2020-070 | 02 - Nebraska | 539695 | SPEARVL6 | 230 | 11.475 | 11.5321 | 0.0571
GEN-2020-070 | 02 - Nebraska | 539699 | W-DODGE3 | 115 | 4.3528 | 4.355 | 0.0022
GEN-2020-070 | 02 - Nebraska | 539740 | EDODGE 3 | 115 | 6.2185 | 6.2236 | 0.0051
GEN-2020-070 | 02 - Nebraska | 539758 | FORD 3 | 115 | 5.2431 | 5.246 | 0.0029
GEN-2020-070 | 02 - Nebraska | 539759 | SPRVL 3 | 115 | 12.36 | 12.3912 | 0.0312
GEN-2020-070 | 02 - Nebraska | 539771 | NFTDODG3 | 115 | 9.2687 | 9.2803 | 0.0116
GEN-2020-070 | 02 - Nebraska | 539778 | GYCOTAP3 | 115 | 2.5263 | 2.5269 | 0.0006
GEN-2020-070 | 02 - Nebraska | 539779 | GRAY CO3 | 115 | 2.5263 | 2.5269 | 0.0006
GEN-2020-070 | 02 - Nebraska | 539800 | CLARKCOUNTY7 | 345 | 10.2777 | 10.3267 | 0.049
GEN-2020-070 | 02 - Nebraska | 539801 | THISTLE7 | 345 | 15.065 | 15.0887 | 0.0237
GEN-2020-070 | 02 - Nebraska | 539803 | IRONWOOD7 | 345 | 10.7132 | 10.7921 | 0.0789
GEN-2020-070 | 02 - Nebraska | 539813 | TRANSFORMER | 345 | 8.9511 | 8.9879 | 0.0368
GEN-2020-070 | 02 - Nebraska | 539815 | IRONWOOD WF7 | 345 | 9.88 | 9.9467 | 0.0667
GEN-2020-070 | 02 - Nebraska | 539840 | GEN-2011-008 | 345 | 8.5919 | 8.6261 | 0.0342
GEN-2020-070 | 02 - Nebraska | 539841 | G-2011-008-1 | 345 | 8.5919 | 8.6261 | 0.0342
GEN-2020-070 | 02 - Nebraska | 539855 | G-2011-008-2 | 345 | 7.3952 | 7.4205 | 0.0253
GEN-2020-070 | 02 - Nebraska | 539857 | G-2011-008-3 | 345 | 6.9602 | 6.9826 | 0.0224
GEN-2020-070 | 02 - Nebraska | 539944 | LOCHS | 115 | 3.2854 | 3.2867 | 0.0013
GEN-2020-070 | 02 - Nebraska | 560080 | G16-046-TAP | 345 | 9.2927 | 9.3396 | 0.0469
GEN-2020-070 | 02 - Nebraska | 560082 | G16-050-TAP | 345 | 7.4178 | 7.5497 | 0.1319
GEN-2020-070 | 02 - Nebraska | 579480 | GEN-2008-124 | 345 | 10.4076 | 10.482 | 0.0744
GEN-2020-070 | 02 - Nebraska | 585241 | GEN-2015-088 | 345 | 12.3567 | 12.364 | 0.0073
GEN-2020-070 | 02 - Nebraska | 587310 | GEN-2016-046 | 345 | 8.2587 | 8.2957 | 0.037
GEN-2020-070 | 02 - Nebraska | 587311 | G16-046XFMR1 | 115 | 12.3477 | 12.3752 | 0.0275
GEN-2020-070 | 02 - Nebraska | 587350 | GEN-2016-050 | 345 | 6.2289 | 6.3186 | 0.0897
GEN-2020-070 | 02 - Nebraska | 587680 | GEN-2016-074 | 345 | 6.39 | 6.3985 | 0.0085
GEN-2020-070 | 02 - Nebraska | 588630 | GEN-2017-018 | 345 | 15.065 | 15.0887 | 0.0237
GEN-2020-070 | 02 - Nebraska | 599950 | LAMAR7 | 345 | 2.4288 | 2.4299 | 0.0011
GEN-2020-070 | 02 - Nebraska | 640065 | AXTELL 3 | 345 | 10.1745 | 10.2613 | 0.0868
GEN-2020-070 | 02 - Nebraska | 640066 | AXTELL 7 | 115 | 15.3161 | 15.3509 | 0.0348
GEN-2020-070 | 02 - Nebraska | 640161 | ELMCRK_7 | 115 | 6.2078 | 6.2095 | 0.0017
GEN-2020-070 | 02 - Nebraska | 640162 | ELMCRK 8 | 69 | 3.871 | 3.8714 | 0.0004
GEN-2020-070 | 02 - Nebraska | 640183 | GENTLMN3 | 345 | 16.2348 | 16.2446 | 0.0098
GEN-2020-070 | 02 - Nebraska | 640215 | HASTING7 | 115 | 19.671 | 19.6814 | 0.0104
GEN-2020-070 | 02 - Nebraska | 640222 | HILDRTH7 | 115 | 4.6062 | 4.6076 | 0.0014
GEN-2020-070 | 02 - Nebraska | 640223 | HILDRTH8 | 69 | 3.6321 | 3.6326 | 0.0005
GEN-2020-070 | 02 - Nebraska | 640224 | HOLDREG7 | 115 | 7.3696 | 7.3731 | 0.0035
GEN-2020-070 | 02 - Nebraska | 640242 | JOHN.2 7 | 115 | 12.8373 | 12.8408 | 0.0035
GEN-2020-070 | 02 - Nebraska | 640248 | KEAR.NE7 | 115 | 9.8527 | 9.8583 | 0.0056
GEN-2020-070 | 02 - Nebraska | 640250 | KEARNEY7 | 115 | 12.563 | 12.5742 | 0.0112
GEN-2020-070 | 02 - Nebraska | 640261 | LOWELL 7 | 115 | 8.5193 | 8.5249 | 0.0056
GEN-2020-070 | 02 - Nebraska | 640262 | LOWELL 8 | 69 | 4.2268 | 4.2276 | 0.0008
GEN-2020-070 | 02 - Nebraska | 640275 | MINDEN 7 | 115 | 7.5434 | 7.5496 | 0.0062
GEN-2020-070 | 02 - Nebraska | 640277 | MOORE 3 | 345 | 23.8912 | 23.8992 | 0.008
GEN-2020-070 | 02 - Nebraska | 640310 | ORLEANS7 | 115 | 2.6247 | 2.6251 | 0.0004
GEN-2020-070 | 02 - Nebraska | 640311 | ORLEANS8 | 69 | 2.561 | 2.5613 | 0.0003
GEN-2020-070 | 02 - Nebraska | 640312 | PAULINE3 | 345 | 8.4532 | 8.4754 | 0.0222
GEN-2020-070 | 02 - Nebraska | 640313 | PAULINE7 | 115 | 17.0015 | 17.0184 | 0.0169
GEN-2020-070 | 02 - Nebraska | 640314 | PAULINE8 | 69 | 4.9462 | 4.9471 | 0.0009
GEN-2020-070 | 02 - Nebraska | 640374 | SWEET W3 | 345 | 11.2903 | 11.3183 | 0.028
GEN-2020-070 | 02 - Nebraska | 640383 | TOWER 7 | 115 | 9.47 | 9.4753 | 0.0053
GEN-2020-070 | 02 - Nebraska | 640448 | HOLDREGE 8 | 69 | 4.0412 | 4.0418 | 0.0006
GEN-2020-070 | 02 - Nebraska | 640525 | TOBIAS 3 | 345 | 12.3567 | 12.364 | 0.0073
GEN-2020-070 | 02 - Nebraska | 640583 | ROSEMONT 7 | 115 | 6.8004 | 6.8024 | 0.002
GEN-2020-070 | 02 - Nebraska | 640584 | COTTONWD 7 | 115 | 5.4896 | 5.4908 | 0.0012
GEN-2020-070 | 02 - Nebraska | 653571 | GR ISLD3 | 345 | 13.5564 | 13.5665 | 0.0101
GEN-2020-070 | 02 - Nebraska | 761292 | GEN-2017-181 | 345 | 7.0076 | 7.0097 | 0.0021
GEN-2020-070 | 02 - Nebraska | 761313 | GEN-2017-182 | 345 | 5.8507 | 5.8522 | 0.0015
GEN-2020-070 | 02 - Nebraska | 762658 | GEN-2018-030 | 345 | 2.7534 | 2.7549 | 0.0015
GEN-2020-070 | 02 - Nebraska | 762662 | G18-030-TAP | 345 | 2.9419 | 2.9435 | 0.0016
GEN-2020-070 | 02 - Nebraska | 762834 | GEN-2018-049 | 345 | 6.669 | 6.6737 | 0.0047
GEN-2020-070 | 02 - Nebraska | 763406 | GEN-2018-125 | 345 | 7.216 | 7.2211 | 0.0051
GEN-2020-070 | 02 - Nebraska | 763410 | G18-125-TAP | 345 | 7.5454 | 7.5511 | 0.0057
GEN-2020-070 | 02 - Nebraska | 763670 | GEN-2019-030 | 345 | 7.8458 | 7.882 | 0.0362
GEN-2020-070 | 02 - Nebraska | 763677 | G19-030-TAP | 345 | 9.322 | 9.3732 | 0.0512
GEN-2020-070 | 02 - Nebraska | 763758 | GEN-2019-044 | 115 | 6.0249 | 6.0298 | 0.0049
GEN-2020-070 | 02 - Nebraska | 763846 | G19-053/055 | 230 | 6.4378 | 6.4599 | 0.0221
GEN-2020-070 | 02 - Nebraska | 763850 | G19-055-TAP | 230 | 6.5169 | 6.5396 | 0.0227
GEN-2020-070 | 02 - Nebraska | 763857 | G19-054/068 | 230 | 6.2388 | 6.2611 | 0.0223
GEN-2020-070 | 02 - Nebraska | 763862 | G19-054-TAP | 230 | 6.313 | 6.3359 | 0.0229
GEN-2020-070 | 02 - Nebraska | 763890 | GEN-2019-058 | 345 | 10.1083 | 10.1557 | 0.0474
GEN-2020-070 | 02 - Nebraska | 764420 | GEN-2020-011 | 345 | 9.7525 | 9.8084 | 0.0559
GEN-2020-070 | 02 - Nebraska | 764430 | G20-011-TAP | 345 | 9.7525 | 9.8084 | 0.0559
GEN-2020-070 | 02 - Nebraska | 764431 | G20-011-SS1 | 345 | 9.7423 | 9.798 | 0.0557
GEN-2020-070 | 02 - Nebraska | 764432 | G20-011-SS2 | 345 | 9.6312 | 9.6857 | 0.0545
GEN-2020-070 | 02 - Nebraska | 764433 | G20-011-SS3 | 345 | 9.6669 | 9.7217 | 0.0548
GEN-2020-070 | 02 - Nebraska | 764434 | G20-011-SS4 | 345 | 9.4744 | 9.5271 | 0.0527
GEN-2020-070 | 02 - Nebraska | 764435 | GEN-2020-013 | 115 | 7.1744 | 7.1777 | 0.0033
GEN-2020-070 | 02 - Nebraska | 764445 | G20-013-TAP | 115 | 7.1847 | 7.188 | 0.0033
GEN-2020-070 | 02 - Nebraska | 764446 | G20-013-SS1 | 115 | 7.1559 | 7.1592 | 0.0033
GEN-2020-070 | 02 - Nebraska | 764447 | G20-013-SS2 | 115 | 6.8612 | 6.8641 | 0.0029
GEN-2020-070 | 02 - Nebraska | 764448 | G20-013-SS3 | 115 | 6.7944 | 6.7973 | 0.0029
GEN-2020-070 | 02 - Nebraska | 765025 | GEN-2020-070 | 345 | 6.4494 | 6.8887 | 0.4393
GEN-2020-070 | 02 - Nebraska | 765035 | G20-070-TAP | 345 | 6.4494 | 6.8887 | 0.4393
GEN-2020-077 | 02 - Nebraska | 533303 | MARSHAL3 | 115 | 4.6698 | 4.6761 | 0.0063
GEN-2020-077 | 02 - Nebraska | 533332 | KNOB HL3 | 115 | 4.8668 | 4.8806 | 0.0138
GEN-2020-077 | 02 - Nebraska | 539665 | GRNLEAF3 | 115 | 4.1577 | 4.1618 | 0.0041
GEN-2020-077 | 02 - Nebraska | 575061 | GEN-2009-040 | 115 | 3.6097 | 3.6133 | 0.0036
GEN-2020-077 | 02 - Nebraska | 640074 | BEAT. S7 | 115 | 5.3782 | 5.394 | 0.0158
GEN-2020-077 | 02 - Nebraska | 640076 | BEATRCE7 | 115 | 13.1546 | 13.2502 | 0.0956
GEN-2020-077 | 02 - Nebraska | 640088 | BPS SUB7 | 115 | 15.929 | 16.015 | 0.086
GEN-2020-077 | 02 - Nebraska | 640105 | CARLJCT7 | 115 | 5.6429 | 5.8188 | 0.1759
GEN-2020-077 | 02 - Nebraska | 640111 | CLATONA7 | 115 | 10.9076 | 10.9271 | 0.0195
GEN-2020-077 | 02 - Nebraska | 640153 | CRETE__7 | 115 | 8.4355 | 8.4441 | 0.0086
GEN-2020-077 | 02 - Nebraska | 640169 | FAIRBRY7 | 115 | 5.1229 | 5.4435 | 0.3206
GEN-2020-077 | 02 - Nebraska | 640174 | FRIEND 7 | 115 | 5.7113 | 5.724 | 0.0127
GEN-2020-077 | 02 - Nebraska | 640178 | GENEVA 7 | 115 | 9.9411 | 10.0249 | 0.0838
GEN-2020-077 | 02 - Nebraska | 640179 | GENEVA 8 | 69 | 4.3121 | 4.3212 | 0.0091
GEN-2020-077 | 02 - Nebraska | 640206 | GUIDE R7 | 115 | 4.3686 | 4.3912 | 0.0226
GEN-2020-077 | 02 - Nebraska | 640207 | GUIDE R8 | 69 | 2.2444 | 2.248 | 0.0036
GEN-2020-077 | 02 - Nebraska | 640208 | HARBINE7 | 115 | 6.889 | 7.0963 | 0.2073
GEN-2020-077 | 02 - Nebraska | 640218 | HEBRN N7 | 115 | 5.8229 | 6.164 | 0.3411
GEN-2020-077 | 02 - Nebraska | 640220 | HEBRON 7 | 115 | 5.5405 | 5.8398 | 0.2993
GEN-2020-077 | 02 - Nebraska | 640235 | HUMBOLT7 | 115 | 6.7026 | 6.705 | 0.0024
GEN-2020-077 | 02 - Nebraska | 640271 | MCCOOL 3 | 345 | 11.6051 | 11.6185 | 0.0134
GEN-2020-077 | 02 - Nebraska | 640272 | MCCOOL 7 | 115 | 14.7833 | 14.8207 | 0.0374
GEN-2020-077 | 02 - Nebraska | 640273 | MCCOOL 8 | 69 | 5.7364 | 5.7398 | 0.0034
GEN-2020-077 | 02 - Nebraska | 640278 | SHELDON7 | 115 | 44.5238 | 44.587 | 0.0632
GEN-2020-077 | 02 - Nebraska | 640361 | STEINER7 | 115 | 4.5766 | 4.5802 | 0.0036
GEN-2020-077 | 02 - Nebraska | 640368 | SUPEROR7 | 115 | 3.4658 | 3.5064 | 0.0406
GEN-2020-077 | 02 - Nebraska | 640372 | SUTTON 7 | 115 | 6.5266 | 6.5435 | 0.0169
GEN-2020-077 | 02 - Nebraska | 640373 | SUTTON 8 | 69 | 3.9261 | 3.9297 | 0.0036
GEN-2020-077 | 02 - Nebraska | 640413 | YORK SW7 | 115 | 8.4227 | 8.4306 | 0.0079
GEN-2020-077 | 02 - Nebraska | 640415 | CARLJCT8 | 69 | 3.7224 | 3.7666 | 0.0442
GEN-2020-077 | 02 - Nebraska | 640426 | STEELEC7 | 115 | 5.1073 | 5.1785 | 0.0712
GEN-2020-077 | 02 - Nebraska | 640447 | YORK.SW T2 8 | 69 | 2.5296 | 2.5301 | 0.0005
GEN-2020-077 | 02 - Nebraska | 640558 | S.FLATS.PLT7 | 115 | 4.5111 | 4.5649 | 0.0538
GEN-2020-077 | 02 - Nebraska | 640583 | ROSEMONT 7 | 115 | 6.7834 | 6.8024 | 0.019
GEN-2020-077 | 02 - Nebraska | 640584 | COTTONWD 7 | 115 | 5.479 | 5.4908 | 0.0118
GEN-2020-077 | 02 - Nebraska | 641087 | EGYCNTR7 | 115 | 18.2492 | 18.2671 | 0.0179
GEN-2020-077 | 02 - Nebraska | 647966 | S966 8 | 69 | 0.4925 | 0.4925 | 0
GEN-2020-077 | 02 - Nebraska | 761208 | GEN-2017-210 | 345 | 10.1458 | 10.1559 | 0.0101
GEN-2020-077 | 02 - Nebraska | 764480 | GEN-2020-077 | 115 | 3.6515 | 4.3021 | 0.6506
GEN-2020-077 | 02 - Nebraska | 764490 | G20-077-TAP | 115 | 4.8215 | 5.4375 | 0.616
GEN-2020-078 | 02 - Nebraska | 635200 | RAUN 3 | 345 | 28.7074 | 28.7143 | 0.0069
GEN-2020-078 | 02 - Nebraska | 635201 | RAUN 5 | 161 | 28.5019 | 28.5069 | 0.005
GEN-2020-078 | 02 - Nebraska | 635202 | NEAL S 5 | 161 | 23.4912 | 23.4944 | 0.0032
GEN-2020-078 | 02 - Nebraska | 635203 | NEAL N 5 | 161 | 26.9345 | 26.939 | 0.0045
GEN-2020-078 | 02 - Nebraska | 635220 | INTCHG 5 | 161 | 15.2492 | 15.2504 | 0.0012
GEN-2020-078 | 02 - Nebraska | 635230 | LIBERTY5 | 161 | 26.2153 | 26.2195 | 0.0042
GEN-2020-078 | 02 - Nebraska | 640070 | BANCRFT7 | 115 | 5.3087 | 5.3094 | 0.0007
GEN-2020-078 | 02 - Nebraska | 640300 | OAKLAND7 | 115 | 7.9524 | 7.9546 | 0.0022
GEN-2020-078 | 02 - Nebraska | 640377 | TEKAMAH5 | 161 | 9.3683 | 9.379 | 0.0107
GEN-2020-078 | 02 - Nebraska | 640378 | TEKAMAH7 | 115 | 8.6218 | 8.6265 | 0.0047
GEN-2020-078 | 02 - Nebraska | 640400 | W.POINT7 | 115 | 5.2458 | 5.2465 | 0.0007
GEN-2020-078 | 02 - Nebraska | 640409 | WINSLOW7 | 115 | 5.5967 | 5.5977 | 0.001
GEN-2020-078 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.4476 | 30.5745 | 0.1269
GEN-2020-078 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.4251 | 23.4917 | 0.0666
GEN-2020-078 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.3702 | 30.4229 | 0.0527
GEN-2020-078 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.1569 | 26.2179 | 0.061
GEN-2020-078 | 02 - Nebraska | 646209 | S1209 5 | 161 | 48.2782 | 48.4181 | 0.1399
GEN-2020-078 | 02 - Nebraska | 646226 | S1226 5 | 161 | 25.4385 | 25.6682 | 0.2297
GEN-2020-078 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.1246 | 44.2376 | 0.113
GEN-2020-078 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27.441 | 27.4924 | 0.0514
GEN-2020-078 | 02 - Nebraska | 646235 | S1235 5 | 161 | 34.8191 | 34.9268 | 0.1077
GEN-2020-078 | 02 - Nebraska | 646236 | S1236 5 | 161 | 24.9728 | 25.0452 | 0.0724
GEN-2020-078 | 02 - Nebraska | 646237 | S1237 5 | 161 | 22.2852 | 22.4417 | 0.1565
GEN-2020-078 | 02 - Nebraska | 646249 | S1249 5 | 161 | 26.1816 | 26.2201 | 0.0385
GEN-2020-078 | 02 - Nebraska | 646250 | S1250 5 | 161 | 35.6381 | 35.7004 | 0.0623
GEN-2020-078 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.1534 | 33.3039 | 0.1505
GEN-2020-078 | 02 - Nebraska | 646252 | S1252 5 | 161 | 30.4707 | 30.6053 | 0.1346
GEN-2020-078 | 02 - Nebraska | 646253 | S1253 5 | 161 | 28.2075 | 28.3027 | 0.0952
GEN-2020-078 | 02 - Nebraska | 646256 | S1256 5 | 161 | 23.414 | 23.458 | 0.044
GEN-2020-078 | 02 - Nebraska | 646291 | S1291 5 | 161 | 7.1218 | 7.1338 | 0.012
GEN-2020-078 | 02 - Nebraska | 646297 | S1297 5 | 161 | 19.2211 | 19.2544 | 0.0333
GEN-2020-078 | 02 - Nebraska | 646298 | S1298 5 | 161 | 30.176 | 30.3321 | 0.1561
GEN-2020-078 | 02 - Nebraska | 646305 | S1305 5 | 161 | 28.6773 | 28.8136 | 0.1363
GEN-2020-078 | 02 - Nebraska | 646341 | S1341 5 | 161 | 27.8992 | 28.0234 | 0.1242
GEN-2020-078 | 02 - Nebraska | 646345 | S1345 5 | 161 | 23.0028 | 23.1175 | 0.1147
GEN-2020-078 | 02 - Nebraska | 646347 | S1347 5 | 161 | 33.8859 | 33.9924 | 0.1065
GEN-2020-078 | 02 - Nebraska | 646367 | S1367 5 | 161 | 22.109 | 22.2072 | 0.0982
GEN-2020-078 | 02 - Nebraska | 647291 | S991 E 8 | 69 | 12.5415 | 12.5495 | 0.008
GEN-2020-078 | 02 - Nebraska | 647421 | FREM A 8 | 69 | 14.3267 | 14.3313 | 0.0046
GEN-2020-078 | 02 - Nebraska | 647422 | FREM B 8 | 69 | 14.5667 | 14.5724 | 0.0057
GEN-2020-078 | 02 - Nebraska | 647423 | FREM C 8 | 69 | 12.4003 | 12.4042 | 0.0039
GEN-2020-078 | 02 - Nebraska | 647424 | FREM D 8 | 69 | 12.6994 | 12.7033 | 0.0039
GEN-2020-078 | 02 - Nebraska | 647427 | FREM G 8 | 69 | 14.088 | 14.0925 | 0.0045
GEN-2020-078 | 02 - Nebraska | 647909 | S909 8 | 69 | 27.1877 | 27.2018 | 0.0141
GEN-2020-078 | 02 - Nebraska | 762069 | G17-105TAP | 161 | 8.7918 | 8.8 | 0.0082
GEN-2020-078 | 02 - Nebraska | 762070 | GEN-2017-105 | 161 | 8.7918 | 8.8 | 0.0082
GEN-2020-078 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.3702 | 22.4309 | 0.0607
GEN-2020-078 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.7669 | 17.7927 | 0.0258
GEN-2020-078 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.4004 | 17.425 | 0.0246
GEN-2020-078 | 02 - Nebraska | 764720 | GEN-2020-043 | 161 | 33.8847 | 33.9911 | 0.1064
GEN-2020-078 | 02 - Nebraska | 764735 | GEN-2020-044 | 161 | 33.8847 | 33.9911 | 0.1064
GEN-2020-078 | 02 - Nebraska | 764750 | GEN-2020-045 | 161 | 33.8847 | 33.9911 | 0.1064
GEN-2020-078 | 02 - Nebraska | 764765 | GEN-2020-078 | 161 | 16.0829 | 16.45 | 0.3671
GEN-2020-078 | 02 - Nebraska | 764775 | G20-078-TAP | 161 | 16.1181 | 16.4852 | 0.3671
GEN-2020-084 | 02 - Nebraska | 45906 | J1590 SUB | 345 | 14.9917 | 15.0035 | 0.0118
GEN-2020-084 | 02 - Nebraska | 87486 | J748GENTIE | 345 | 13.9477 | 13.9572 | 0.0095
GEN-2020-084 | 02 - Nebraska | 87487 | J748POI | 345 | 15.8292 | 15.8415 | 0.0123
GEN-2020-084 | 02 - Nebraska | 584650 | GEN-2015-023 | 345 | 12.9256 | 12.9266 | 0.001
GEN-2020-084 | 02 - Nebraska | 601006 | SPLT RK3 | 345 | 15.5521 | 15.5538 | 0.0017
GEN-2020-084 | 02 - Nebraska | 635000 | CBLUFFS3 | 345 | 32.1566 | 32.2342 | 0.0776
GEN-2020-084 | 02 - Nebraska | 635200 | RAUN 3 | 345 | 28.6286 | 28.7143 | 0.0857
GEN-2020-084 | 02 - Nebraska | 635201 | RAUN 5 | 161 | 28.4743 | 28.5069 | 0.0326
GEN-2020-084 | 02 - Nebraska | 635202 | NEAL S 5 | 161 | 23.4733 | 23.4944 | 0.0211
GEN-2020-084 | 02 - Nebraska | 635203 | NEAL N 5 | 161 | 26.91 | 26.939 | 0.029
GEN-2020-084 | 02 - Nebraska | 635204 | NEAL N 8 | 69 | 10.2572 | 10.2589 | 0.0017
GEN-2020-084 | 02 - Nebraska | 635206 | IDA CO 3 | 345 | 9.7706 | 9.7747 | 0.0041
GEN-2020-084 | 02 - Nebraska | 635219 | GARD AVE 3 | 345 | 9.4058 | 9.4091 | 0.0033
GEN-2020-084 | 02 - Nebraska | 635220 | INTCHG 5 | 161 | 15.2422 | 15.2504 | 0.0082
GEN-2020-084 | 02 - Nebraska | 635221 | KELLOGG5 | 161 | 17.9522 | 17.9628 | 0.0106
GEN-2020-084 | 02 - Nebraska | 635229 | AIRPORT 5 | 161 | 17.8265 | 17.8382 | 0.0117
GEN-2020-084 | 02 - Nebraska | 635230 | LIBERTY5 | 161 | 26.1922 | 26.2195 | 0.0273
GEN-2020-084 | 02 - Nebraska | 635235 | SALIX 5 | 161 | 15.3323 | 15.3405 | 0.0082
GEN-2020-084 | 02 - Nebraska | 635252 | J412 POI 3 | 345 | 10.1458 | 10.1509 | 0.0051
GEN-2020-084 | 02 - Nebraska | 635300 | MONONA 5 | 161 | 5.7321 | 5.7327 | 0.0006
GEN-2020-084 | 02 - Nebraska | 635398 | REMSEN 3 | 345 | 15.2277 | 15.2399 | 0.0122
GEN-2020-084 | 02 - Nebraska | 635399 | CHEROKEE 3 | 345 | 16.7263 | 16.7393 | 0.013
GEN-2020-084 | 02 - Nebraska | 635400 | HIGHLND 3 | 345 | 15.209 | 15.2152 | 0.0062
GEN-2020-084 | 02 - Nebraska | 637009 | GLACIAL EDGE | 345 | 16.4379 | 16.4504 | 0.0125
GEN-2020-084 | 02 - Nebraska | 637024 | RICHLAND W | 345 | 9.3367 | 9.34 | 0.0033
GEN-2020-084 | 02 - Nebraska | 640080 | BELDEN 7 | 115 | 6.3342 | 6.3345 | 0.0003
GEN-2020-084 | 02 - Nebraska | 640081 | BELDEN 8 | 69 | 3.899 | 3.8991 | 0.0001
GEN-2020-084 | 02 - Nebraska | 640226 | HOSKINS3 | 345 | 16.1225 | 16.1283 | 0.0058
GEN-2020-084 | 02 - Nebraska | 640227 | HOSKINS4 | 230 | 14.2773 | 14.2803 | 0.003
GEN-2020-084 | 02 - Nebraska | 640228 | HOSKINS7 | 115 | 20.5225 | 20.5257 | 0.0032
GEN-2020-084 | 02 - Nebraska | 640296 | NORFK.N7 | 115 | 14.8427 | 14.8443 | 0.0016
GEN-2020-084 | 02 - Nebraska | 640298 | NORFOLK7 | 115 | 13.7345 | 13.7359 | 0.0014
GEN-2020-084 | 02 - Nebraska | 640342 | SHELCRK3 | 345 | 11.454 | 11.4566 | 0.0026
GEN-2020-084 | 02 - Nebraska | 640363 | STNTN.N7 | 115 | 7.4951 | 7.4957 | 0.0006
GEN-2020-084 | 02 - Nebraska | 640377 | TEKAMAH5 | 161 | 9.3718 | 9.379 | 0.0072
GEN-2020-084 | 02 - Nebraska | 640510 | HOLT.CO3 | 345 | 13.1015 | 13.1026 | 0.0011
GEN-2020-084 | 02 - Nebraska | 640520 | ANTELOPE 3 | 345 | 12.6302 | 12.6319 | 0.0017
GEN-2020-084 | 02 - Nebraska | 640521 | ANTELOPE 7 | 115 | 22.8034 | 22.8051 | 0.0017
GEN-2020-084 | 02 - Nebraska | 640522 | ANTELOPE 8 | 69 | 5.8163 | 5.8164 | 0.0001
GEN-2020-084 | 02 - Nebraska | 640560 | WAKEFIELD 4 | 230 | 8.7789 | 8.7801 | 0.0012
GEN-2020-084 | 02 - Nebraska | 640561 | RTLSNAKE.W 4 | 230 | 7.7641 | 7.7649 | 0.0008
GEN-2020-084 | 02 - Nebraska | 640588 | TURTLE.CRK 3 | 345 | 13.3461 | 13.3499 | 0.0038
GEN-2020-084 | 02 - Nebraska | 640589 | SHOLES.W 3 | 345 | 10.4749 | 10.4772 | 0.0023
GEN-2020-084 | 02 - Nebraska | 640598 | HAYSTACK.WD3 | 345 | 9.9764 | 9.9783 | 0.0019
GEN-2020-084 | 02 - Nebraska | 643254 | UPSTREAM.W 7 | 115 | 20.9151 | 20.9165 | 0.0014
GEN-2020-084 | 02 - Nebraska | 643271 | PLUMBCR.W 3 | 345 | 13.0044 | 13.008 | 0.0036
GEN-2020-084 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.3613 | 30.5745 | 0.2132
GEN-2020-084 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.1126 | 23.4917 | 0.3791
GEN-2020-084 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.2787 | 30.4229 | 0.1442
GEN-2020-084 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.5662 | 33.718 | 0.1518
GEN-2020-084 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.6158 | 35.7822 | 0.1664
GEN-2020-084 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30.0654 | 30.0963 | 0.0309
GEN-2020-084 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.0428 | 26.2179 | 0.1751
GEN-2020-084 | 02 - Nebraska | 645740 | S3740 3 | 345 | 24.3255 | 24.3832 | 0.0577
GEN-2020-084 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.9264 | 24.0017 | 0.0753
GEN-2020-084 | 02 - Nebraska | 646206 | S1206 5 | 161 | 44.7615 | 44.8616 | 0.1001
GEN-2020-084 | 02 - Nebraska | 646209 | S1209 5 | 161 | 48.2146 | 48.4181 | 0.2035
GEN-2020-084 | 02 - Nebraska | 646226 | S1226 5 | 161 | 25.5643 | 25.6682 | 0.1039
GEN-2020-084 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.0904 | 44.2376 | 0.1472
GEN-2020-084 | 02 - Nebraska | 646249 | S1249 5 | 161 | 26.1757 | 26.2201 | 0.0444
GEN-2020-084 | 02 - Nebraska | 646250 | S1250 5 | 161 | 35.6029 | 35.7004 | 0.0975
GEN-2020-084 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.0512 | 33.3039 | 0.2527
GEN-2020-084 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.7112 | 34.7844 | 0.0732
GEN-2020-084 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.7141 | 50.8724 | 0.1583
GEN-2020-084 | 02 - Nebraska | 646281 | S1281 5 | 161 | 40.7819 | 40.8654 | 0.0835
GEN-2020-084 | 02 - Nebraska | 646297 | S1297 5 | 161 | 19.1997 | 19.2544 | 0.0547
GEN-2020-084 | 02 - Nebraska | 646298 | S1298 5 | 161 | 30.136 | 30.3321 | 0.1961
GEN-2020-084 | 02 - Nebraska | 646305 | S1305 5 | 161 | 28.6346 | 28.8136 | 0.179
GEN-2020-084 | 02 - Nebraska | 646341 | S1341 5 | 161 | 27.852 | 28.0234 | 0.1714
GEN-2020-084 | 02 - Nebraska | 646347 | S1347 5 | 161 | 33.8958 | 33.9924 | 0.0966
GEN-2020-084 | 02 - Nebraska | 647909 | S909 8 | 69 | 27.1812 | 27.2018 | 0.0206
GEN-2020-084 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17.8299 | 17.8395 | 0.0096
GEN-2020-084 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.4544 | 21.476 | 0.0216
GEN-2020-084 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21.3484 | 21.3651 | 0.0167
GEN-2020-084 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32.411 | 32.4229 | 0.0119
GEN-2020-084 | 02 - Nebraska | 652552 | SIOUXCY2 | 230 | 21.0221 | 21.0344 | 0.0123
GEN-2020-084 | 02 - Nebraska | 652564 | SIOUXCY3 | 345 | 16.0783 | 16.0934 | 0.0151
GEN-2020-084 | 02 - Nebraska | 652565 | SIOUXCY4 | 230 | 21.0221 | 21.0344 | 0.0123
GEN-2020-084 | 02 - Nebraska | 652864 | SIOUXCY-LNX3 | 345 | 15.8858 | 15.9004 | 0.0146
GEN-2020-084 | 02 - Nebraska | 659900 | EAGLE___-NI4 | 230 | 7.5349 | 7.5358 | 0.0009
GEN-2020-084 | 02 - Nebraska | 760767 | GEN-2017-144 | 345 | 12.2255 | 12.2264 | 0.0009
GEN-2020-084 | 02 - Nebraska | 760788 | GEN-2017-201 | 345 | 9.4546 | 9.4564 | 0.0018
GEN-2020-084 | 02 - Nebraska | 762069 | G17-105TAP | 161 | 8.794 | 8.8 | 0.006
GEN-2020-084 | 02 - Nebraska | 762070 | GEN-2017-105 | 161 | 8.794 | 8.8 | 0.006
GEN-2020-084 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.0853 | 22.4309 | 0.3456
GEN-2020-084 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 24.3238 | 24.3816 | 0.0578
GEN-2020-084 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.2243 | 17.7927 | 0.5684
GEN-2020-084 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 16.8547 | 17.425 | 0.5703
GEN-2020-084 | 02 - Nebraska | 763032 | GEN-2018-068 | 345 | 9.4557 | 9.4566 | 0.0009
GEN-2020-084 | 02 - Nebraska | 763142 | GEN-2018-083 | 345 | 2.2976 | 2.2977 | 0.0001
GEN-2020-084 | 02 - Nebraska | 763439 | GEN-2018-131 | 345 | 12.6111 | 12.6127 | 0.0016
GEN-2020-084 | 02 - Nebraska | 763450 | GEN-2018-132 | 345 | 11.6688 | 11.6702 | 0.0014
GEN-2020-084 | 02 - Nebraska | 763978 | GEN-2019-069 | 345 | 12.9374 | 12.9409 | 0.0035
GEN-2020-084 | 02 - Nebraska | 763982 | G19-069-TAP | 345 | 12.9821 | 12.9856 | 0.0035
GEN-2020-084 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 24.0479 | 24.1043 | 0.0564
GEN-2020-084 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 24.3255 | 24.3832 | 0.0577
GEN-2020-084 | 02 - Nebraska | 764720 | GEN-2020-043 | 161 | 33.8946 | 33.9911 | 0.0965
GEN-2020-084 | 02 - Nebraska | 764735 | GEN-2020-044 | 161 | 33.8946 | 33.9911 | 0.0965
GEN-2020-084 | 02 - Nebraska | 764750 | GEN-2020-045 | 161 | 33.8946 | 33.9911 | 0.0965
GEN-2020-094 | 02 - Nebraska | 85831 | J583 | 345 | 6.0616 | 6.0619 | 0.0003
GEN-2020-094 | 02 - Nebraska | 300039 | 7FAIRPT | 345 | 12.583 | 12.5859 | 0.0029
GEN-2020-094 | 02 - Nebraska | 300076 | 5FAIRPTB2 | 161 | 16.5698 | 16.5712 | 0.0014
GEN-2020-094 | 02 - Nebraska | 301347 | 5WINSLOW | 161 | 8.8562 | 8.8566 | 0.0004
GEN-2020-094 | 02 - Nebraska | 301559 | 5FAIRPTXF3 | 161 | 16.5883 | 16.5897 | 0.0014
GEN-2020-094 | 02 - Nebraska | 541147 | ST JOE_CAP5 | 161 | 17.966 | 17.9675 | 0.0015
GEN-2020-094 | 02 - Nebraska | 541197 | MULLNCR7 | 345 | 7.8094 | 7.8138 | 0.0044
GEN-2020-094 | 02 - Nebraska | 541199 | ST JOE 7 | 345 | 19.7412 | 19.7459 | 0.0047
GEN-2020-094 | 02 - Nebraska | 541201 | SIBLEY 7 | 345 | 21.009 | 21.0107 | 0.0017
GEN-2020-094 | 02 - Nebraska | 541253 | ST JOE 5 | 161 | 20.0489 | 20.0509 | 0.002
GEN-2020-094 | 02 - Nebraska | 541257 | COOK 5 | 161 | 14.2252 | 14.2261 | 0.0009
GEN-2020-094 | 02 - Nebraska | 541258 | WOODBIN5 | 161 | 17.0278 | 17.0292 | 0.0014
GEN-2020-094 | 02 - Nebraska | 541394 | AVENUECTY 5 | 161 | 8.7872 | 8.7876 | 0.0004
GEN-2020-094 | 02 - Nebraska | 541400 | EASTOWN7 | 345 | 18.3289 | 18.3319 | 0.003
GEN-2020-094 | 02 - Nebraska | 541401 | EASTOWN5 | 161 | 17.5485 | 17.5499 | 0.0014
GEN-2020-094 | 02 - Nebraska | 541411 | MC REAC1 | 345 | 7.4777 | 7.4817 | 0.004
GEN-2020-094 | 02 - Nebraska | 541412 | MC REAC2 | 345 | 7.4777 | 7.4817 | 0.004
GEN-2020-094 | 02 - Nebraska | 541413 | MC REAC3 | 345 | 7.4777 | 7.4817 | 0.004
GEN-2020-094 | 02 - Nebraska | 541414 | SIB REA1 | 345 | 18.7706 | 18.7719 | 0.0013
GEN-2020-094 | 02 - Nebraska | 541500 | KETCHEM7 | 345 | 7.8112 | 7.8134 | 0.0022
GEN-2020-094 | 02 - Nebraska | 541501 | OSBORN7 | 345 | 6.9717 | 6.9734 | 0.0017
GEN-2020-094 | 02 - Nebraska | 541510 | HOLT 7 | 345 | 8.903 | 8.9106 | 0.0076
GEN-2020-094 | 02 - Nebraska | 541511 | ROCKCK7 | 345 | 6.9411 | 6.9454 | 0.0043
GEN-2020-094 | 02 - Nebraska | 541517 | HOLT_REACT7 | 345 | 8.8579 | 8.8655 | 0.0076
GEN-2020-094 | 02 - Nebraska | 541543 | OUTLAW | 345 | 5.7461 | 5.749 | 0.0029
GEN-2020-094 | 02 - Nebraska | 542980 | NASHUA 7 | 345 | 22.7048 | 22.7067 | 0.0019
GEN-2020-094 | 02 - Nebraska | 542982 | IATAN 7 | 345 | 29.3706 | 29.3727 | 0.0021
GEN-2020-094 | 02 - Nebraska | 560746 | G13-002-TAP | 115 | 43.4455 | 43.5193 | 0.0738
GEN-2020-094 | 02 - Nebraska | 583700 | GEN-2013-019 | 115 | 19.1902 | 19.204 | 0.0138
GEN-2020-094 | 02 - Nebraska | 585241 | GEN-2015-088 | 345 | 12.3471 | 12.364 | 0.0169
GEN-2020-094 | 02 - Nebraska | 587680 | GEN-2016-074 | 345 | 6.398 | 6.3985 | 0.0005
GEN-2020-094 | 02 - Nebraska | 635000 | CBLUFFS3 | 345 | 32.2055 | 32.2342 | 0.0287
GEN-2020-094 | 02 - Nebraska | 635001 | CBLUFFS5 | 161 | 39.7986 | 39.8181 | 0.0195
GEN-2020-094 | 02 - Nebraska | 635002 | CBLUFFS8 | 69 | 25.2482 | 25.2514 | 0.0032
GEN-2020-094 | 02 - Nebraska | 635011 | INDNCRK5 | 161 | 22.0402 | 22.0461 | 0.0059
GEN-2020-094 | 02 - Nebraska | 635013 | PNYCRK 3 | 345 | 29.2866 | 29.31 | 0.0234
GEN-2020-094 | 02 - Nebraska | 635014 | OVRLND 3 | 345 | 27.4801 | 27.5003 | 0.0202
GEN-2020-094 | 02 - Nebraska | 635015 | OVRLND 5 | 161 | 31.5555 | 31.5672 | 0.0117
GEN-2020-094 | 02 - Nebraska | 635016 | STHLND 3 | 345 | 29.2517 | 29.2751 | 0.0234
GEN-2020-094 | 02 - Nebraska | 635017 | ATCHSN 3 | 345 | 17.3893 | 17.4058 | 0.0165
GEN-2020-094 | 02 - Nebraska | 635018 | WESTBORO 3 | 345 | 16.591 | 16.6054 | 0.0144
GEN-2020-094 | 02 - Nebraska | 635030 | RIVRBND5 | 161 | 36.2617 | 36.2778 | 0.0161
GEN-2020-094 | 02 - Nebraska | 635100 | RLHILLS3 | 345 | 13.0899 | 13.0923 | 0.0024
GEN-2020-094 | 02 - Nebraska | 635570 | ORIENT 3 | 345 | 17.3927 | 17.3963 | 0.0036
GEN-2020-094 | 02 - Nebraska | 635589 | ECLIPSE3 | 345 | 9.061 | 9.0617 | 0.0007
GEN-2020-094 | 02 - Nebraska | 635590 | FALLOW 3 | 345 | 10.9969 | 10.998 | 0.0011
GEN-2020-094 | 02 - Nebraska | 637084 | J476 SHENHLL | 345 | 16.5078 | 16.522 | 0.0142
GEN-2020-094 | 02 - Nebraska | 640065 | AXTELL 3 | 345 | 10.2596 | 10.2613 | 0.0017
GEN-2020-094 | 02 - Nebraska | 640074 | BEAT. S7 | 115 | 5.3936 | 5.394 | 0.0004
GEN-2020-094 | 02 - Nebraska | 640076 | BEATRCE7 | 115 | 13.2481 | 13.2502 | 0.0021
GEN-2020-094 | 02 - Nebraska | 640088 | BPS SUB7 | 115 | 16.0118 | 16.015 | 0.0032
GEN-2020-094 | 02 - Nebraska | 640111 | CLATONA7 | 115 | 10.9245 | 10.9271 | 0.0026
GEN-2020-094 | 02 - Nebraska | 640125 | COLMB.E3 | 345 | 10.9854 | 10.991 | 0.0056
GEN-2020-094 | 02 - Nebraska | 640127 | COLMB.E7 | 115 | 23.4807 | 23.4865 | 0.0058
GEN-2020-094 | 02 - Nebraska | 640139 | COOPER 3 | 345 | 26.9202 | 26.9714 | 0.0512
GEN-2020-094 | 02 - Nebraska | 640140 | COOPER 5 | 161 | 18.1266 | 18.1359 | 0.0093
GEN-2020-094 | 02 - Nebraska | 640141 | COOPER_ESST8 | 69 | 4.6822 | 4.6825 | 0.0003
GEN-2020-094 | 02 - Nebraska | 640143 | COOPER_602 8 | 69 | 2.0146 | 2.0146 | 0
GEN-2020-094 | 02 - Nebraska | 640153 | CRETE__7 | 115 | 8.4419 | 8.4441 | 0.0022
GEN-2020-094 | 02 - Nebraska | 640171 | FIRTH 7 | 115 | 7.016 | 7.0177 | 0.0017
GEN-2020-094 | 02 - Nebraska | 640174 | FRIEND 7 | 115 | 5.7232 | 5.724 | 0.0008
GEN-2020-094 | 02 - Nebraska | 640178 | GENEVA 7 | 115 | 10.0233 | 10.0249 | 0.0016
GEN-2020-094 | 02 - Nebraska | 640179 | GENEVA 8 | 69 | 4.321 | 4.3212 | 0.0002
GEN-2020-094 | 02 - Nebraska | 640200 | GR ISLD4 | 230 | 17.7439 | 17.749 | 0.0051
GEN-2020-094 | 02 - Nebraska | 640234 | HUMBOLT5 | 161 | 7.8359 | 7.8368 | 0.0009
GEN-2020-094 | 02 - Nebraska | 640271 | MCCOOL 3 | 345 | 11.6091 | 11.6185 | 0.0094
GEN-2020-094 | 02 - Nebraska | 640272 | MCCOOL 7 | 115 | 14.8163 | 14.8207 | 0.0044
GEN-2020-094 | 02 - Nebraska | 640273 | MCCOOL 8 | 69 | 5.7394 | 5.7398 | 0.0004
GEN-2020-094 | 02 - Nebraska | 640277 | MOORE 3 | 345 | 23.7993 | 23.8992 | 0.0999
GEN-2020-094 | 02 - Nebraska | 640278 | SHELDON7 | 115 | 44.513 | 44.587 | 0.074
GEN-2020-094 | 02 - Nebraska | 640312 | PAULINE3 | 345 | 8.4725 | 8.4754 | 0.0029
GEN-2020-094 | 02 - Nebraska | 640313 | PAULINE7 | 115 | 17.0158 | 17.0184 | 0.0026
GEN-2020-094 | 02 - Nebraska | 640314 | PAULINE8 | 69 | 4.9469 | 4.9471 | 0.0002
GEN-2020-094 | 02 - Nebraska | 640316 | PAWNEEL7 | 115 | 11.7938 | 11.7993 | 0.0055
GEN-2020-094 | 02 - Nebraska | 640342 | SHELCRK3 | 345 | 11.452 | 11.4566 | 0.0046
GEN-2020-094 | 02 - Nebraska | 640374 | SWEET W3 | 345 | 11.3168 | 11.3183 | 0.0015
GEN-2020-094 | 02 - Nebraska | 640413 | YORK SW7 | 115 | 8.4293 | 8.4306 | 0.0013
GEN-2020-094 | 02 - Nebraska | 640446 | COOPER 8 | 69 | 4.7799 | 4.7802 | 0.0003
GEN-2020-094 | 02 - Nebraska | 640447 | YORK.SW T2 8 | 69 | 2.53 | 2.5301 | 0.0001
GEN-2020-094 | 02 - Nebraska | 640525 | TOBIAS 3 | 345 | 12.3471 | 12.364 | 0.0169
GEN-2020-094 | 02 - Nebraska | 640590 | MONOLITH 3 | 345 | 23.276 | 23.3699 | 0.0939
GEN-2020-094 | 02 - Nebraska | 640591 | MONOLITH 7 | 115 | 43.4455 | 43.5193 | 0.0738
GEN-2020-094 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30.56 | 30.5745 | 0.0145
GEN-2020-094 | 02 - Nebraska | 645451 | S3451 3 | 345 | 23.4719 | 23.4917 | 0.0198
GEN-2020-094 | 02 - Nebraska | 645454 | S3454 3 | 345 | 30.3582 | 30.4229 | 0.0647
GEN-2020-094 | 02 - Nebraska | 645455 | S3455 3 | 345 | 33.6527 | 33.718 | 0.0653
GEN-2020-094 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35.7203 | 35.7822 | 0.0619
GEN-2020-094 | 02 - Nebraska | 645458 | S3458 3 | 345 | 29.8903 | 30.0963 | 0.206
GEN-2020-094 | 02 - Nebraska | 645459 | S3459 3 | 345 | 26.1897 | 26.2179 | 0.0282
GEN-2020-094 | 02 - Nebraska | 645740 | S3740 3 | 345 | 24.3377 | 24.3832 | 0.0455
GEN-2020-094 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23.9698 | 24.0017 | 0.0319
GEN-2020-094 | 02 - Nebraska | 646201 | S1201 5 | 161 | 32.0288 | 32.0427 | 0.0139
GEN-2020-094 | 02 - Nebraska | 646206 | S1206 5 | 161 | 44.8306 | 44.8616 | 0.031
GEN-2020-094 | 02 - Nebraska | 646209 | S1209 5 | 161 | 48.3791 | 48.4181 | 0.039
GEN-2020-094 | 02 - Nebraska | 646216 | S1216 5 | 161 | 30.8854 | 30.9002 | 0.0148
GEN-2020-094 | 02 - Nebraska | 646217 | S1217 5 | 161 | 33.6696 | 33.6872 | 0.0176
GEN-2020-094 | 02 - Nebraska | 646220 | S1220 5 | 161 | 28.8578 | 28.8688 | 0.011
GEN-2020-094 | 02 - Nebraska | 646221 | S1221 5 | 161 | 36.3033 | 36.3278 | 0.0245
GEN-2020-094 | 02 - Nebraska | 646229 | S1229 5 | 161 | 28.9669 | 28.9784 | 0.0115
GEN-2020-094 | 02 - Nebraska | 646231 | S1231 5 | 161 | 44.2037 | 44.2376 | 0.0339
GEN-2020-094 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26.9865 | 26.9988 | 0.0123
GEN-2020-094 | 02 - Nebraska | 646233 | S1233 5 | 161 | 30.1091 | 30.1276 | 0.0185
GEN-2020-094 | 02 - Nebraska | 646244 | S1244 5 | 161 | 22.2554 | 22.263 | 0.0076
GEN-2020-094 | 02 - Nebraska | 646249 | S1249 5 | 161 | 26.2051 | 26.2201 | 0.015
GEN-2020-094 | 02 - Nebraska | 646250 | S1250 5 | 161 | 35.6828 | 35.7004 | 0.0176
GEN-2020-094 | 02 - Nebraska | 646251 | S1251 5 | 161 | 33.2867 | 33.3039 | 0.0172
GEN-2020-094 | 02 - Nebraska | 646254 | S1254 5 | 161 | 34.7567 | 34.7844 | 0.0277
GEN-2020-094 | 02 - Nebraska | 646255 | S1255 5 | 161 | 50.8166 | 50.8724 | 0.0558
GEN-2020-094 | 02 - Nebraska | 646259 | S1259 5 | 161 | 40.3614 | 40.3943 | 0.0329
GEN-2020-094 | 02 - Nebraska | 646263 | S1263 5 | 161 | 8.4613 | 8.4626 | 0.0013
GEN-2020-094 | 02 - Nebraska | 646278 | S1278 5 | 161 | 28.2177 | 28.2329 | 0.0152
GEN-2020-094 | 02 - Nebraska | 646280 | S1280 5 | 161 | 10.4481 | 10.4502 | 0.0021
GEN-2020-094 | 02 - Nebraska | 646281 | S1281 5 | 161 | 40.8322 | 40.8654 | 0.0332
GEN-2020-094 | 02 - Nebraska | 646286 | S1286 5 | 161 | 26.7071 | 26.7166 | 0.0095
GEN-2020-094 | 02 - Nebraska | 646347 | S1347 5 | 161 | 33.9745 | 33.9924 | 0.0179
GEN-2020-094 | 02 - Nebraska | 646361 | S1361 5 | 161 | 44.3449 | 44.3845 | 0.0396
GEN-2020-094 | 02 - Nebraska | 646366 | S1366 5 | 161 | 16.4142 | 16.4183 | 0.0041
GEN-2020-094 | 02 - Nebraska | 647006 | S906 N 8 | 69 | 32.2786 | 32.2848 | 0.0062
GEN-2020-094 | 02 - Nebraska | 647015 | S6815T1&T2 8 | 69 | 12.0712 | 12.0721 | 0.0009
GEN-2020-094 | 02 - Nebraska | 647016 | 6815TP38 | 69 | 17.5484 | 17.5502 | 0.0018
GEN-2020-094 | 02 - Nebraska | 647017 | 6815TP98 | 69 | 12.6583 | 12.6593 | 0.001
GEN-2020-094 | 02 - Nebraska | 647815 | S6815T3 8 | 69 | 11.4354 | 11.4362 | 0.0008
GEN-2020-094 | 02 - Nebraska | 647874 | S6874 8 | 69 | 8.6158 | 8.6162 | 0.0004
GEN-2020-094 | 02 - Nebraska | 647901 | S901 8 | 69 | 26.3396 | 26.3427 | 0.0031
GEN-2020-094 | 02 - Nebraska | 647904 | S904 8 | 69 | 8.7523 | 8.7528 | 0.0005
GEN-2020-094 | 02 - Nebraska | 647906 | S906 S 8 | 69 | 32.7068 | 32.7128 | 0.006
GEN-2020-094 | 02 - Nebraska | 647909 | S909 8 | 69 | 27.1971 | 27.2018 | 0.0047
GEN-2020-094 | 02 - Nebraska | 647916 | S916 8 | 69 | 23.8563 | 23.8599 | 0.0036
GEN-2020-094 | 02 - Nebraska | 647924 | S924 8 | 69 | 24.4146 | 24.4178 | 0.0032
GEN-2020-094 | 02 - Nebraska | 647928 | S928 8 | 69 | 17.2453 | 17.2471 | 0.0018
GEN-2020-094 | 02 - Nebraska | 647938 | S938 8 | 69 | 21.7515 | 21.7542 | 0.0027
GEN-2020-094 | 02 - Nebraska | 647995 | S995 8 | 69 | 9.493 | 9.4935 | 0.0005
GEN-2020-094 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17.7841 | 17.8395 | 0.0554
GEN-2020-094 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21.3575 | 21.476 | 0.1185
GEN-2020-094 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21.1832 | 21.3651 | 0.1819
GEN-2020-094 | 02 - Nebraska | 650210 | NW70FAIRFD7 | 115 | 21.4846 | 21.5051 | 0.0205
GEN-2020-094 | 02 - Nebraska | 650214 | NW68HOLDRG7 | 115 | 25.7378 | 25.7674 | 0.0296
GEN-2020-094 | 02 - Nebraska | 650216 | SW27&F 7 | 115 | 22.2094 | 22.2312 | 0.0218
GEN-2020-094 | 02 - Nebraska | 650238 | 20PIONEERS7 | 115 | 27.4599 | 27.4929 | 0.033
GEN-2020-094 | 02 - Nebraska | 650242 | FOLSM&PHIL7 | 115 | 27.8743 | 27.907 | 0.0327
GEN-2020-094 | 02 - Nebraska | 650246 | SW7&BENNET7 | 115 | 23.4565 | 23.4793 | 0.0228
GEN-2020-094 | 02 - Nebraska | 650247 | 40&BENNET 7 | 115 | 21.522 | 21.5419 | 0.0199
GEN-2020-094 | 02 - Nebraska | 650262 | 57&GARLAND7 | 115 | 25.5249 | 25.5547 | 0.0298
GEN-2020-094 | 02 - Nebraska | 650267 | 84LEIGHTON7 | 115 | 29.6337 | 29.6748 | 0.0411
GEN-2020-094 | 02 - Nebraska | 650270 | 70&CALVERT7 | 115 | 27.5746 | 27.6094 | 0.0348
GEN-2020-094 | 02 - Nebraska | 650271 | 81&OCHENEY7 | 115 | 25.2491 | 25.2787 | 0.0296
GEN-2020-094 | 02 - Nebraska | 650272 | 91&A 7 | 115 | 21.9832 | 22.0055 | 0.0223
GEN-2020-094 | 02 - Nebraska | 650273 | 93&O 7 | 115 | 22.7427 | 22.7667 | 0.024
GEN-2020-094 | 02 - Nebraska | 650274 | 91&HWY2 7 | 115 | 21.8623 | 21.8838 | 0.0215
GEN-2020-094 | 02 - Nebraska | 650279 | 120&ALVO 7 | 115 | 21.7885 | 21.8116 | 0.0231
GEN-2020-094 | 02 - Nebraska | 650283 | WAVERLY 7 | 115 | 21.2622 | 21.2824 | 0.0202
GEN-2020-094 | 02 - Nebraska | 650284 | 84FLETCHER7 | 115 | 25.0623 | 25.0889 | 0.0266
GEN-2020-094 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32.3646 | 32.4229 | 0.0583
GEN-2020-094 | 02 - Nebraska | 650290 | ROKEBY 7 | 115 | 25.7419 | 25.7696 | 0.0277
GEN-2020-094 | 02 - Nebraska | 653571 | GR ISLD3 | 345 | 13.5614 | 13.5665 | 0.0051
GEN-2020-094 | 02 - Nebraska | 653871 | GR ISLD-LNX3 | 345 | 13.4365 | 13.4415 | 0.005
GEN-2020-094 | 02 - Nebraska | 760746 | GEN-2017-115 | 345 | 7.2174 | 7.2225 | 0.0051
GEN-2020-094 | 02 - Nebraska | 760872 | GEN-2017-198 | 69 | 24.9805 | 24.9832 | 0.0027
GEN-2020-094 | 02 - Nebraska | 761208 | GEN-2017-210 | 345 | 10.1488 | 10.1559 | 0.0071
GEN-2020-094 | 02 - Nebraska | 761292 | GEN-2017-181 | 345 | 7.0048 | 7.0097 | 0.0049
GEN-2020-094 | 02 - Nebraska | 761313 | GEN-2017-182 | 345 | 5.8488 | 5.8522 | 0.0034
GEN-2020-094 | 02 - Nebraska | 761376 | GEN-2017-183 | 345 | 7.5636 | 7.564 | 0.0004
GEN-2020-094 | 02 - Nebraska | 761383 | G17-183-TAP | 345 | 16.4119 | 16.4136 | 0.0017
GEN-2020-094 | 02 - Nebraska | 762581 | GEN-2018-022 | 345 | 6.5838 | 6.5869 | 0.0031
GEN-2020-094 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 22.413 | 22.4309 | 0.0179
GEN-2020-094 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 24.336 | 24.3816 | 0.0456
GEN-2020-094 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 17.7849 | 17.7927 | 0.0078
GEN-2020-094 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 17.4176 | 17.425 | 0.0074
GEN-2020-094 | 02 - Nebraska | 763505 | GEN-2019-009 | 161 | 8.1548 | 8.156 | 0.0012
GEN-2020-094 | 02 - Nebraska | 763725 | GEN-2019-041 | 115 | 43.3382 | 43.4116 | 0.0734
GEN-2020-094 | 02 - Nebraska | 764690 | GEN-2020-036 | 345 | 24.0598 | 24.1043 | 0.0445
GEN-2020-094 | 02 - Nebraska | 764705 | GEN-2020-038 | 345 | 24.3377 | 24.3832 | 0.0455
GEN-2020-094 | 02 - Nebraska | 764720 | GEN-2020-043 | 161 | 33.9733 | 33.9911 | 0.0178
GEN-2020-094 | 02 - Nebraska | 764735 | GEN-2020-044 | 161 | 33.9733 | 33.9911 | 0.0178
GEN-2020-094 | 02 - Nebraska | 764750 | GEN-2020-045 | 161 | 33.9733 | 33.9911 | 0.0178
GEN-2020-094 | 02 - Nebraska | 764795 | GEN-2020-094 | 345 | 11.536 | 11.9489 | 0.4129
GEN-2020-094 | 02 - Nebraska | 764805 | G20-094-TAP | 345 | 16.4046 | 16.8137 | 0.4091
ASGI-2020-001 | 03 - Central | 300105 | 5NORTON | 161 | 6.7832 | 6.8371 | 0.0539
ASGI-2020-001 | 03 - Central | 300540 | 2NORTON | 69 | 6.1597 | 6.1718 | 0.0121
ASGI-2020-001 | 03 - Central | 301567 | 5NORTONTP | 161 | 6.3031 | 6.3423 | 0.0392
ASGI-2020-001 | 03 - Central | 345221 | 5MOBERLY | 161 | 15.8922 | 15.901 | 0.0088
ASGI-2020-001 | 03 - Central | 543012 | SWAVCAP2 | 69 | 3.8974 | 4.251 | 0.3536
ASGI-2020-001 | 03 - Central | 543013 | SWAVCAP5 | 161 | 3.4498 | 3.5073 | 0.0575
ASGI-2020-001 | 03 - Central | 543059 | MALTABN5 | 161 | 4.1471 | 4.2046 | 0.0575
ASGI-2020-001 | 03 - Central | 543061 | BRUNSWK5 | 161 | 5.9383 | 5.9426 | 0.0043
ASGI-2020-001 | 03 - Central | 543062 | SALSBRY5 | 161 | 12.0666 | 12.0907 | 0.0241
ASGI-2020-001 | 03 - Central | 543063 | SWAVRLY5 | 161 | 3.5199 | 3.5799 | 0.06
ASGI-2020-001 | 03 - Central | 543064 | NORTON 5 | 161 | 6.805 | 6.8601 | 0.0551
ASGI-2020-001 | 03 - Central | 543070 | WEST---5 | 161 | 4.7408 | 4.7674 | 0.0266
ASGI-2020-001 | 03 - Central | 543071 | S EAST 5 | 161 | 4.9318 | 4.9606 | 0.0288
ASGI-2020-001 | 03 - Central | 543072 | MRSHLJT5 | 161 | 5.936 | 5.9779 | 0.0419
ASGI-2020-001 | 03 - Central | 543073 | MIAMI_ 5 | 161 | 4.8108 | 4.8383 | 0.0275
ASGI-2020-001 | 03 - Central | 543094 | SWAVRLY2 | 69 | 3.8991 | 4.2531 | 0.354
ASGI-2020-001 | 03 - Central | 543097 | CORDER 2 | 69 | 3.6994 | 3.9183 | 0.2189
ASGI-2020-001 | 03 - Central | 543098 | CTY HIG2 | 69 | 3.9928 | 4.1978 | 0.205
ASGI-2020-001 | 03 - Central | 543099 | HIGNSVL2 | 69 | 4.0054 | 4.2067 | 0.2013
ASGI-2020-001 | 03 - Central | 543101 | DOVER2 | 69 | 3.6923 | 3.9169 | 0.2246
ASGI-2020-001 | 03 - Central | 543102 | WHGNSVL2 | 69 | 4.1507 | 4.3242 | 0.1735
ASGI-2020-001 | 03 - Central | 543144 | HGNSCTYW2 | 69 | 3.6415 | 3.8108 | 0.1693
ASGI-2020-001 | 03 - Central | 543146 | HGNSCTYPLNT2 | 69 | 3.9485 | 4.149 | 0.2005
ASGI-2020-001 | 03 - Central | 543657 | CORDERTP2 | 69 | 3.8954 | 4.1384 | 0.243
ASGI-2020-001 | 03 - Central | 543658 | DOVER_TAP2 | 69 | 3.8873 | 4.1365 | 0.2492
ASGI-2020-001 | 03 - Central | 762383 | ASG-2018-007 | 161 | 12.0554 | 12.0795 | 0.0241
ASGI-2020-001 | 03 - Central | 765235 | AGI-2020-001 | 69 | 3.8991 | 4.2531 | 0.354
ASGI-2020-003 | 03 - Central | 300049 | 7THOMHL | 345 | 14.9155 | 14.9246 | 0.0091
ASGI-2020-003 | 03 - Central | 300066 | 5HIGBEEB1 | 161 | 12.8518 | 12.8601 | 0.0083
ASGI-2020-003 | 03 - Central | 300091 | 5LATHRP | 161 | 7.3075 | 7.3097 | 0.0022
ASGI-2020-003 | 03 - Central | 300098 | 5MOCITYB2 | 161 | 19.4663 | 19.4986 | 0.0323
ASGI-2020-003 | 03 - Central | 300105 | 5NORTON | 161 | 6.8282 | 6.8371 | 0.0089
ASGI-2020-003 | 03 - Central | 300120 | 5THMHILB1 | 161 | 31.5745 | 31.609 | 0.0345
ASGI-2020-003 | 03 - Central | 300126 | 5MOBTAP | 161 | 15.8916 | 15.9112 | 0.0196
ASGI-2020-003 | 03 - Central | 300132 | 5THMHLB2 | 161 | 31.7112 | 31.746 | 0.0348
ASGI-2020-003 | 03 - Central | 300133 | 5THMHLB3 | 161 | 31.613 | 31.6474 | 0.0344
ASGI-2020-003 | 03 - Central | 300304 | 2MOCITY | 69 | 9.5379 | 9.54 | 0.0021
ASGI-2020-003 | 03 - Central | 300381 | 5BEVIER | 161 | 7.9203 | 7.9222 | 0.0019
ASGI-2020-003 | 03 - Central | 300500 | 5HUNTSDL | 161 | 10.8092 | 10.8104 | 0.0012
ASGI-2020-003 | 03 - Central | 300540 | 2NORTON | 69 | 6.1697 | 6.1718 | 0.0021
ASGI-2020-003 | 03 - Central | 300953 | 5HARRSBRG | 161 | 9.3247 | 9.3275 | 0.0028
ASGI-2020-003 | 03 - Central | 301443 | 5THMHLB4 | 161 | 31.3265 | 31.3614 | 0.0349
ASGI-2020-003 | 03 - Central | 301494 | 5HIGBEEB2 | 161 | 12.852 | 12.8603 | 0.0083
ASGI-2020-003 | 03 - Central | 301503 | 7THOMHLGSU3 | 345 | 14.8067 | 14.8155 | 0.0088
ASGI-2020-003 | 03 - Central | 301504 | 5THOMHLGSU1 | 161 | 30.5794 | 30.6113 | 0.0319
ASGI-2020-003 | 03 - Central | 301505 | 5THOMHLGSU2 | 161 | 30.5493 | 30.5813 | 0.032
ASGI-2020-003 | 03 - Central | 301507 | 5THOMHLU3SU | 161 | 30.0542 | 30.0853 | 0.0311
ASGI-2020-003 | 03 - Central | 301508 | 5THOMHLXF1 | 161 | 30.2901 | 30.3217 | 0.0316
ASGI-2020-003 | 03 - Central | 301510 | 5THOMHLXF4 | 161 | 31.0156 | 31.0495 | 0.0339
ASGI-2020-003 | 03 - Central | 301511 | 5THMHILTFERB | 161 | 31.3107 | 31.3446 | 0.0339
ASGI-2020-003 | 03 - Central | 301563 | 5MOCITYB1 | 161 | 19.4904 | 19.5225 | 0.0321
ASGI-2020-003 | 03 - Central | 301567 | 5NORTONTP | 161 | 6.3359 | 6.3423 | 0.0064
ASGI-2020-003 | 03 - Central | 344557 | 5MAURER 1 | 161 | 8.2537 | 8.2909 | 0.0372
ASGI-2020-003 | 03 - Central | 344558 | 5MAURER 2 | 161 | 8.2537 | 8.2909 | 0.0372
ASGI-2020-003 | 03 - Central | 345221 | 5MOBERLY | 161 | 15.8813 | 15.901 | 0.0197
ASGI-2020-003 | 03 - Central | 345222 | 2MOBERLY | 69 | 8.0319 | 8.0336 | 0.0017
ASGI-2020-003 | 03 - Central | 345408 | 7OVERTON | 345 | 12.9859 | 12.9884 | 0.0025
ASGI-2020-003 | 03 - Central | 345409 | 5OVERTON | 161 | 21.3419 | 21.347 | 0.0051
ASGI-2020-003 | 03 - Central | 345411 | 5OVERTON 2 | 161 | 21.3419 | 21.347 | 0.0051
ASGI-2020-003 | 03 - Central | 346048 | 2MAURER | 69 | 3.3002 | 3.3027 | 0.0025
ASGI-2020-003 | 03 - Central | 346096 | 2MACON_AM | 69 | 1.6181 | 1.6181 | 0
ASGI-2020-003 | 03 - Central | 346117 | 2OVERTON | 69 | 3.687 | 3.6871 | 0.0001
ASGI-2020-003 | 03 - Central | 346169 | 2DUPONT | 69 | 6.966 | 6.9672 | 0.0012
ASGI-2020-003 | 03 - Central | 346170 | 2ROTH TAP | 69 | 1.8421 | 1.8421 | 0
ASGI-2020-003 | 03 - Central | 346171 | 2SPRK TAP | 69 | 7.1818 | 7.1831 | 0.0013
ASGI-2020-003 | 03 - Central | 541248 | LBRTYST5 | 161 | 19.4516 | 19.4622 | 0.0106
ASGI-2020-003 | 03 - Central | 543013 | SWAVCAP5 | 161 | 3.5052 | 3.5073 | 0.0021
ASGI-2020-003 | 03 - Central | 543020 | BRMGHAM5 | 161 | 27.0143 | 27.0235 | 0.0092
ASGI-2020-003 | 03 - Central | 543023 | CLAYCM25 | 161 | 13.9275 | 13.93 | 0.0025
ASGI-2020-003 | 03 - Central | 543059 | MALTABN5 | 161 | 4.2014 | 4.2046 | 0.0032
ASGI-2020-003 | 03 - Central | 543060 | CAROLTN5 | 161 | 4.5652 | 4.7157 | 0.1505
ASGI-2020-003 | 03 - Central | 543061 | BRUNSWK5 | 161 | 5.851 | 5.9426 | 0.0916
ASGI-2020-003 | 03 - Central | 543062 | SALSBRY5 | 161 | 12.0261 | 12.0907 | 0.0646
ASGI-2020-003 | 03 - Central | 543063 | SWAVRLY5 | 161 | 3.5777 | 3.5799 | 0.0022
ASGI-2020-003 | 03 - Central | 543064 | NORTON 5 | 161 | 6.8509 | 6.8601 | 0.0092
ASGI-2020-003 | 03 - Central | 543070 | WEST---5 | 161 | 4.763 | 4.7674 | 0.0044
ASGI-2020-003 | 03 - Central | 543071 | S EAST 5 | 161 | 4.9558 | 4.9606 | 0.0048
ASGI-2020-003 | 03 - Central | 543072 | MRSHLJT5 | 161 | 5.9709 | 5.9779 | 0.007
ASGI-2020-003 | 03 - Central | 543073 | MIAMI_ 5 | 161 | 4.8338 | 4.8383 | 0.0045
ASGI-2020-003 | 03 - Central | 543095 | LIBRTYS2 | 69 | 12.4511 | 12.4518 | 0.0007
ASGI-2020-003 | 03 - Central | 548808 | ECKLES-161 | 161 | 25.689 | 25.7073 | 0.0183
ASGI-2020-003 | 03 - Central | 762383 | ASG-2018-007 | 161 | 12.0151 | 12.0795 | 0.0644
ASGI-2020-003 | 03 - Central | 765265 | AGI-2020-003 | 161 | 4.5652 | 4.7157 | 0.1505
GEN-2020-003 | 03 - Central | 532981 | CRESWLN4 | 138 | 9.2611 | 9.3227 | 0.0616
GEN-2020-003 | 03 - Central | 532982 | OXFORD 4 | 138 | 11.1035 | 11.1413 | 0.0378
GEN-2020-003 | 03 - Central | 532984 | SUMNER 4 | 138 | 12.5757 | 12.6174 | 0.0417
GEN-2020-003 | 03 - Central | 532985 | TCROCK 4 | 138 | 6.2397 | 6.2609 | 0.0212
GEN-2020-003 | 03 - Central | 532992 | TIMBJCT4 | 138 | 6.7265 | 6.7512 | 0.0247
GEN-2020-003 | 03 - Central | 533063 | SC10BEL4 | 138 | 12.409 | 12.4465 | 0.0375
GEN-2020-003 | 03 - Central | 533070 | SLATECRK4 | 138 | 6.1798 | 6.205 | 0.0252
GEN-2020-003 | 03 - Central | 533075 | VIOLA 4 | 138 | 24.9244 | 24.9343 | 0.0099
GEN-2020-003 | 03 - Central | 533541 | AKRON 2 | 69 | 7.5407 | 7.5823 | 0.0416
GEN-2020-003 | 03 - Central | 533543 | CRESWLN2 | 69 | 14.369 | 14.5118 | 0.1428
GEN-2020-003 | 03 - Central | 533545 | FLORAL 2 | 69 | 2.5857 | 2.59 | 0.0043
GEN-2020-003 | 03 - Central | 533546 | FLORALJ2 | 69 | 2.9383 | 2.9439 | 0.0056
GEN-2020-003 | 03 - Central | 533547 | OAK 2 | 69 | 10.0248 | 10.2224 | 0.1976
GEN-2020-003 | 03 - Central | 533549 | RAINBOW2 | 69 | 7.8255 | 8.0218 | 0.1963
GEN-2020-003 | 03 - Central | 533550 | RICHLAN2 | 69 | 6.317 | 6.3296 | 0.0126
GEN-2020-003 | 03 - Central | 533551 | SC1KING2 | 69 | 3.5564 | 3.5649 | 0.0085
GEN-2020-003 | 03 - Central | 533553 | SC4ROME2 | 69 | 6.5788 | 6.5949 | 0.0161
GEN-2020-003 | 03 - Central | 533554 | SC5SILV2 | 69 | 7.5503 | 7.6336 | 0.0833
GEN-2020-003 | 03 - Central | 533555 | SC7CRES2 | 69 | 14.3454 | 14.4878 | 0.1424
GEN-2020-003 | 03 - Central | 533556 | STROTHR2 | 69 | 8.0262 | 8.2618 | 0.2356
GEN-2020-003 | 03 - Central | 533557 | TIMBER 2 | 69 | 2.5989 | 2.6032 | 0.0043
GEN-2020-003 | 03 - Central | 533558 | TIMBJCT2 | 69 | 9.2702 | 9.3332 | 0.063
GEN-2020-003 | 03 - Central | 533559 | UDALL 2 | 69 | 7.8242 | 7.8626 | 0.0384
GEN-2020-003 | 03 - Central | 533561 | WINFLD 2 | 69 | 9.1169 | 9.4861 | 0.3692
GEN-2020-003 | 03 - Central | 533562 | PRAIRIE2 | 69 | 7.7159 | 7.8206 | 0.1047
GEN-2020-003 | 03 - Central | 533563 | PRAIRIJ2 | 69 | 8.5208 | 8.6486 | 0.1278
GEN-2020-003 | 03 - Central | 533573 | CRESWLS2 | 69 | 14.3641 | 14.5068 | 0.1427
GEN-2020-003 | 03 - Central | 533836 | ROSEHIL2 | 69 | 5.7254 | 5.7309 | 0.0055
GEN-2020-003 | 03 - Central | 533837 | RH JCT 2 | 69 | 7.0217 | 7.0301 | 0.0084
GEN-2020-003 | 03 - Central | 533990 | EAST SUB 2 | 69 | 7.5035 | 8.0264 | 0.5229
GEN-2020-003 | 03 - Central | 533991 | WEST SUB 2 | 69 | 7.03 | 7.327 | 0.297
GEN-2020-003 | 03 - Central | 533992 | VIKING SUB 2 | 69 | 6.8521 | 7.2224 | 0.3703
GEN-2020-003 | 03 - Central | 761838 | GEN-2017-121 | 138 | 9.4894 | 9.5118 | 0.0224
GEN-2020-003 | 03 - Central | 765085 | GEN-2020-003 | 69 | 7.5035 | 8.0264 | 0.5229
GEN-2020-007 | 03 - Central | 300071 | 5CLINTN | 161 | 14.2348 | 14.2379 | 0.0031
GEN-2020-007 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 16.1072 | 16.1277 | 0.0205
GEN-2020-007 | 03 - Central | 300740 | 7SPORTSMAN | 345 | 24.6184 | 24.6206 | 0.0022
GEN-2020-007 | 03 - Central | 300949 | 7JASPER | 345 | 13.0315 | 13.0411 | 0.0096
GEN-2020-007 | 03 - Central | 510380 | DELWARE7 | 345 | 12.2151 | 12.2209 | 0.0058
GEN-2020-007 | 03 - Central | 514825 | KAYWIND7 | 345 | 12.6269 | 12.6287 | 0.0018
GEN-2020-007 | 03 - Central | 515621 | OPENSKY7 | 345 | 12.6602 | 12.662 | 0.0018
GEN-2020-007 | 03 - Central | 532768 | EMPEC 7 | 345 | 16.8215 | 16.8308 | 0.0093
GEN-2020-007 | 03 - Central | 532769 | LANG 7 | 345 | 16.636 | 16.6452 | 0.0092
GEN-2020-007 | 03 - Central | 532770 | MORRIS 7 | 345 | 12.9055 | 12.9096 | 0.0041
GEN-2020-007 | 03 - Central | 532774 | SWISVAL7 | 345 | 17.6022 | 17.6348 | 0.0326
GEN-2020-007 | 03 - Central | 532775 | 87TH 7 | 345 | 21.4978 | 21.5435 | 0.0457
GEN-2020-007 | 03 - Central | 532776 | READWF 7 | 345 | 14.0613 | 14.0678 | 0.0065
GEN-2020-007 | 03 - Central | 532777 | G17-009-TAP | 345 | 12.0521 | 12.069 | 0.0169
GEN-2020-007 | 03 - Central | 532778 | GEN-2017-009 | 345 | 11.1384 | 11.1528 | 0.0144
GEN-2020-007 | 03 - Central | 532780 | CANEYRV7 | 345 | 9.9343 | 9.9404 | 0.0061
GEN-2020-007 | 03 - Central | 532781 | CANEYWF7 | 345 | 9.6536 | 9.6594 | 0.0058
GEN-2020-007 | 03 - Central | 532791 | BENTON 7 | 345 | 20.2482 | 20.2629 | 0.0147
GEN-2020-007 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18.4835 | 18.5326 | 0.0491
GEN-2020-007 | 03 - Central | 532794 | ROSEHIL7 | 345 | 19.6631 | 19.6793 | 0.0162
GEN-2020-007 | 03 - Central | 532796 | WICHITA7 | 345 | 24.4976 | 24.5073 | 0.0097
GEN-2020-007 | 03 - Central | 532797 | WOLFCRK7 | 345 | 22.0053 | 22.1344 | 0.1291
GEN-2020-007 | 03 - Central | 532799 | WAVERLY7 | 345 | 18.4883 | 18.6143 | 0.126
GEN-2020-007 | 03 - Central | 532800 | LATHAMS7 | 345 | 10.5954 | 10.6019 | 0.0065
GEN-2020-007 | 03 - Central | 532801 | ELKRVR17 | 345 | 9.3878 | 9.3928 | 0.005
GEN-2020-007 | 03 - Central | 532802 | WAVERTX7 | 345 | 15.1052 | 15.1886 | 0.0834
GEN-2020-007 | 03 - Central | 532851 | AUBURN 6 | 230 | 13.7355 | 13.7402 | 0.0047
GEN-2020-007 | 03 - Central | 532853 | LAWHILL6 | 230 | 14.134 | 14.1387 | 0.0047
GEN-2020-007 | 03 - Central | 532854 | LEC U5 6 | 230 | 14.001 | 14.0056 | 0.0046
GEN-2020-007 | 03 - Central | 532856 | SWISVAL6 | 230 | 22.5772 | 22.5998 | 0.0226
GEN-2020-007 | 03 - Central | 532857 | TECHILL6 | 230 | 11.1746 | 11.179 | 0.0044
GEN-2020-007 | 03 - Central | 532914 | SPRGHL 5 | 161 | 11.216 | 11.2279 | 0.0119
GEN-2020-007 | 03 - Central | 532935 | MARMTNW5 | 161 | 8.4057 | 8.4072 | 0.0015
GEN-2020-007 | 03 - Central | 532937 | NEOSHO 5 | 161 | 23.9221 | 23.946 | 0.0239
GEN-2020-007 | 03 - Central | 532986 | BENTON 4 | 138 | 29.1485 | 29.159 | 0.0105
GEN-2020-007 | 03 - Central | 532991 | WEAVER 4 | 138 | 22.9615 | 22.9679 | 0.0064
GEN-2020-007 | 03 - Central | 533020 | NEOSHOS4 | 138 | 25.4936 | 25.5172 | 0.0236
GEN-2020-007 | 03 - Central | 533021 | NEOSHO 4 | 138 | 25.537 | 25.5606 | 0.0236
GEN-2020-007 | 03 - Central | 533022 | NEOSHON4 | 138 | 25.4168 | 25.4402 | 0.0234
GEN-2020-007 | 03 - Central | 533039 | ELPASO 4 | 138 | 25.8025 | 25.8094 | 0.0069
GEN-2020-007 | 03 - Central | 533062 | ROSEHIL4 | 138 | 32.2655 | 32.2797 | 0.0142
GEN-2020-007 | 03 - Central | 533068 | STEARMN4 | 138 | 20.1937 | 20.1982 | 0.0045
GEN-2020-007 | 03 - Central | 533624 | BURLING2 | 69 | 3.5602 | 3.5606 | 0.0004
GEN-2020-007 | 03 - Central | 533625 | BURLIND2 | 69 | 3.1726 | 3.173 | 0.0004
GEN-2020-007 | 03 - Central | 533626 | BURLJCT2 | 69 | 5.1825 | 5.1833 | 0.0008
GEN-2020-007 | 03 - Central | 533628 | CC1BURL2 | 69 | 3.5587 | 3.5591 | 0.0004
GEN-2020-007 | 03 - Central | 533629 | CC2SHAR2 | 69 | 4.8469 | 4.8477 | 0.0008
GEN-2020-007 | 03 - Central | 533630 | CC3WEST2 | 69 | 4.7829 | 4.7836 | 0.0007
GEN-2020-007 | 03 - Central | 533653 | WOLFCRK2 | 69 | 6.2766 | 6.2781 | 0.0015
GEN-2020-007 | 03 - Central | 533778 | NEOSHOS2 | 69 | 24.0606 | 24.0702 | 0.0096
GEN-2020-007 | 03 - Central | 541198 | PECULR 7 | 345 | 21.0997 | 21.2331 | 0.1334
GEN-2020-007 | 03 - Central | 541200 | PHILL 7 | 345 | 19.0766 | 19.1445 | 0.0679
GEN-2020-007 | 03 - Central | 541201 | SIBLEY 7 | 345 | 21.4579 | 21.4854 | 0.0275
GEN-2020-007 | 03 - Central | 541207 | ARCHIE 5 | 161 | 16.7365 | 16.7507 | 0.0142
GEN-2020-007 | 03 - Central | 541225 | PHILL 5 | 161 | 34.0929 | 34.1347 | 0.0418
GEN-2020-007 | 03 - Central | 541340 | BELTONS5 | 161 | 19.7176 | 19.7506 | 0.033
GEN-2020-007 | 03 - Central | 541341 | S.HARP 5 | 161 | 21.2407 | 21.2789 | 0.0382
GEN-2020-007 | 03 - Central | 541342 | PECULR 5 | 161 | 23.371 | 23.4216 | 0.0506
GEN-2020-007 | 03 - Central | 541343 | S.HARP 2 | 69 | 4.5829 | 4.5835 | 0.0006
GEN-2020-007 | 03 - Central | 541344 | PECULRS5 | 161 | 21.8472 | 21.89 | 0.0428
GEN-2020-007 | 03 - Central | 541414 | SIB REA1 | 345 | 19.1281 | 19.15 | 0.0219
GEN-2020-007 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2.6756 | 2.6785 | 0.0029
GEN-2020-007 | 03 - Central | 542940 | ATLNTIC7 | 345 | 22.0744 | 22.188 | 0.1136
GEN-2020-007 | 03 - Central | 542945 | CRAIG_CAP 5 | 161 | 35.2568 | 35.3191 | 0.0623
GEN-2020-007 | 03 - Central | 542950 | STHTOWN_CAP5 | 161 | 30.7919 | 30.8321 | 0.0402
GEN-2020-007 | 03 - Central | 542965 | W.GRDNR7 | 345 | 30.8433 | 31.1725 | 0.3292
GEN-2020-007 | 03 - Central | 542966 | WGARDNR5 | 161 | 30.7474 | 30.8153 | 0.0679
GEN-2020-007 | 03 - Central | 542968 | STILWEL7 | 345 | 26.4669 | 26.7794 | 0.3125
GEN-2020-007 | 03 - Central | 542969 | STILWEL5 | 161 | 41.4946 | 41.684 | 0.1894
GEN-2020-007 | 03 - Central | 542977 | CRAIG 7 | 345 | 22.7235 | 22.7852 | 0.0617
GEN-2020-007 | 03 - Central | 542978 | CRAIG 5 | 161 | 44.2924 | 44.3908 | 0.0984
GEN-2020-007 | 03 - Central | 542981 | LACYGNE7 | 345 | 27.0353 | 28.609 | 1.5737
GEN-2020-007 | 03 - Central | 542993 | STHTOWN5 | 161 | 37.4707 | 37.5302 | 0.0595
GEN-2020-007 | 03 - Central | 542994 | HICKMAN5 | 161 | 20.0997 | 20.1235 | 0.0238
GEN-2020-007 | 03 - Central | 543002 | MARTCIT5 | 161 | 25.3832 | 25.4296 | 0.0464
GEN-2020-007 | 03 - Central | 543031 | SHWNMSN5 | 161 | 37.1869 | 37.2389 | 0.052
GEN-2020-007 | 03 - Central | 543044 | MOONLT 5 | 161 | 18.0609 | 18.0827 | 0.0218
GEN-2020-007 | 03 - Central | 543046 | OXFORD 5 | 161 | 21.4964 | 21.5315 | 0.0351
GEN-2020-007 | 03 - Central | 543049 | CEDRCRK5 | 161 | 31.3033 | 31.3524 | 0.0491
GEN-2020-007 | 03 - Central | 543050 | ANTIOCH5 | 161 | 23.4604 | 23.5112 | 0.0508
GEN-2020-007 | 03 - Central | 543053 | REDEL 5 | 161 | 25.283 | 25.3399 | 0.0569
GEN-2020-007 | 03 - Central | 543054 | CEDARNL5 | 161 | 10.9326 | 10.9412 | 0.0086
GEN-2020-007 | 03 - Central | 543056 | GARDNER5 | 161 | 16.8005 | 16.8192 | 0.0187
GEN-2020-007 | 03 - Central | 543057 | BUCYRUS5 | 161 | 21.1792 | 21.2232 | 0.044
GEN-2020-007 | 03 - Central | 543058 | NLOUISB5 | 161 | 9.3608 | 9.3694 | 0.0086
GEN-2020-007 | 03 - Central | 543068 | WAGSTAF5 | 161 | 14.5765 | 14.5945 | 0.018
GEN-2020-007 | 03 - Central | 543077 | PLSTVAL5 | 161 | 10.6902 | 10.6971 | 0.0069
GEN-2020-007 | 03 - Central | 543105 | BULLCRK5 | 161 | 29.7256 | 29.7878 | 0.0622
GEN-2020-007 | 03 - Central | 543126 | LACKMAN5 | 161 | 13.9238 | 13.9429 | 0.0191
GEN-2020-007 | 03 - Central | 543132 | BNSF 5 | 161 | 22.5175 | 22.5528 | 0.0353
GEN-2020-007 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 26.3389 | 27.8304 | 1.4915
GEN-2020-007 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 26.3389 | 27.8304 | 1.4915
GEN-2020-007 | 03 - Central | 543659 | LACYGNE2 | 69 | 2.8145 | 2.8177 | 0.0032
GEN-2020-007 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 0.673 | 0.6739 | 0.0009
GEN-2020-007 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 0.6446 | 0.6454 | 0.0008
GEN-2020-007 | 03 - Central | 560053 | G15-052T | 345 | 13.4599 | 13.4639 | 0.004
GEN-2020-007 | 03 - Central | 562476 | G14-001-TAP | 345 | 10.8392 | 10.8417 | 0.0025
GEN-2020-007 | 03 - Central | 583850 | GEN-2014-001 | 345 | 7.3062 | 7.3073 | 0.0011
GEN-2020-007 | 03 - Central | 584900 | GEN-2015-052 | 345 | 13.4099 | 13.4138 | 0.0039
GEN-2020-007 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.0283 | 19.6744 | 0.6461
GEN-2020-007 | 03 - Central | 760921 | G17-209-TAP | 345 | 19.5176 | 20.1994 | 0.6818
GEN-2020-007 | 03 - Central | 761271 | GEN-2017-108 | 161 | 7.5428 | 7.5441 | 0.0013
GEN-2020-007 | 03 - Central | 761278 | G17-108-TAP | 161 | 12.4163 | 12.4206 | 0.0043
GEN-2020-007 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5.3904 | 5.3931 | 0.0027
GEN-2020-007 | 03 - Central | 762279 | GEN-2017-195 | 345 | 30.7528 | 31.08 | 0.3272
GEN-2020-007 | 03 - Central | 762300 | GEN-2017-196 | 345 | 30.6572 | 30.9823 | 0.3251
GEN-2020-007 | 03 - Central | 762405 | ASG-2018-010 | 161 | 3.362 | 3.3626 | 0.0006
GEN-2020-007 | 03 - Central | 762680 | GEN-2018-032 | 345 | 12.1214 | 12.1425 | 0.0211
GEN-2020-007 | 03 - Central | 764300 | GEN-2020-079 | 161 | 15.4095 | 15.4113 | 0.0018
GEN-2020-007 | 03 - Central | 764310 | G20-079-TAP | 161 | 18.6044 | 18.6071 | 0.0027
GEN-2020-007 | 03 - Central | 764375 | GEN-2020-058 | 345 | 22.0296 | 22.1428 | 0.1132
GEN-2020-007 | 03 - Central | 764390 | GEN-2020-073 | 161 | 8.3895 | 8.3928 | 0.0033
GEN-2020-007 | 03 - Central | 764400 | G20-073-TAP | 161 | 8.4704 | 8.4738 | 0.0034
GEN-2020-007 | 03 - Central | 765100 | GEN-2020-052 | 345 | 9.9187 | 9.928 | 0.0093
GEN-2020-007 | 03 - Central | 765110 | G20-052-TAP | 345 | 13.1021 | 13.1185 | 0.0164
GEN-2020-007 | 03 - Central | 765115 | GEN-2020-057 | 345 | 22.0298 | 22.1429 | 0.1131
GEN-2020-007 | 03 - Central | 765130 | GEN-2020-071 | 230 | 11.3748 | 11.3791 | 0.0043
GEN-2020-007 | 03 - Central | 765140 | G20-071-TAP | 230 | 11.3748 | 11.3791 | 0.0043
GEN-2020-007 | 03 - Central | 765145 | GEN-2020-076 | 345 | 12.5422 | 12.5518 | 0.0096
GEN-2020-007 | 03 - Central | 765155 | G20-076-TAP | 345 | 12.5499 | 12.5595 | 0.0096
GEN-2020-007 | 03 - Central | 765160 | GEN-2020-086 | 345 | 12.5428 | 12.5524 | 0.0096
GEN-2020-007 | 03 - Central | 765190 | GEN-2020-090 | 345 | 8.7164 | 8.7262 | 0.0098
GEN-2020-007 | 03 - Central | 765200 | G20-090-TAP | 345 | 9.9402 | 9.9531 | 0.0129
GEN-2020-007 | 03 - Central | 766260 | GEN-2020-007 | 345 | 23.5461 | 25.1555 | 1.6094
GEN-2020-007 | 03 - Central | 766261 | G20-007-TAP | 345 | 26.1711 | 27.7699 | 1.5988
GEN-2020-008 | 03 - Central | 511490 | ELKCITY6 | 230 | 7.6804 | 7.6816 | 0.0012
GEN-2020-008 | 03 - Central | 511541 | SWEETWT6 | 230 | 9.997 | 9.9995 | 0.0025
GEN-2020-008 | 03 - Central | 511542 | BUFFCK6 | 230 | 7.0988 | 7.1 | 0.0012
GEN-2020-008 | 03 - Central | 511544 | DEMPSEY6 | 230 | 5.6188 | 5.6196 | 0.0008
GEN-2020-008 | 03 - Central | 511547 | ROARK6 | 230 | 5.2149 | 5.2155 | 0.0006
GEN-2020-008 | 03 - Central | 511553 | CHISHOLM7 | 345 | 13.1655 | 13.1753 | 0.0098
GEN-2020-008 | 03 - Central | 511557 | CHISHOLM6 | 230 | 12.7678 | 12.7724 | 0.0046
GEN-2020-008 | 03 - Central | 514785 | WOODWRD4 | 138 | 13.4359 | 13.4408 | 0.0049
GEN-2020-008 | 03 - Central | 514796 | IODINE-4 | 138 | 7.6259 | 7.6278 | 0.0019
GEN-2020-008 | 03 - Central | 515363 | CENT 4 | 138 | 3.2281 | 3.2283 | 0.0002
GEN-2020-008 | 03 - Central | 515375 | WWRDEHV7 | 345 | 19.5297 | 19.6012 | 0.0715
GEN-2020-008 | 03 - Central | 515376 | WWRDEHV4 | 138 | 24.5103 | 24.5419 | 0.0316
GEN-2020-008 | 03 - Central | 515394 | KEENAN 4 | 138 | 9.1963 | 9.2003 | 0.004
GEN-2020-008 | 03 - Central | 515398 | OUSPRT 4 | 138 | 9.7752 | 9.7799 | 0.0047
GEN-2020-008 | 03 - Central | 515407 | TATONGA7 | 345 | 17.1547 | 17.176 | 0.0213
GEN-2020-008 | 03 - Central | 515425 | WWDPST 4 | 138 | 17.9338 | 17.9481 | 0.0143
GEN-2020-008 | 03 - Central | 515448 | CRSRDSW7 | 345 | 12.1451 | 12.1555 | 0.0104
GEN-2020-008 | 03 - Central | 515458 | BORDER 7 | 345 | 8.705 | 8.7088 | 0.0038
GEN-2020-008 | 03 - Central | 515497 | MATHWSN7 | 345 | 31.5757 | 31.5866 | 0.0109
GEN-2020-008 | 03 - Central | 515554 | BVRCNTY7 | 345 | 13.174 | 13.3009 | 0.1269
GEN-2020-008 | 03 - Central | 515582 | SLNGWND7 | 345 | 8.6096 | 8.6146 | 0.005
GEN-2020-008 | 03 - Central | 515585 | MAMTHPW7 | 345 | 13.4735 | 13.4865 | 0.013
GEN-2020-008 | 03 - Central | 515590 | PALDR2W7 | 345 | 11.4149 | 11.5088 | 0.0939
GEN-2020-008 | 03 - Central | 515599 | G07621119-20 | 345 | 12.0884 | 12.1157 | 0.0273
GEN-2020-008 | 03 - Central | 515618 | BALKOW 7 | 345 | 11.2121 | 11.3024 | 0.0903
GEN-2020-008 | 03 - Central | 515634 | PALDR1W7 | 345 | 9.9566 | 10.027 | 0.0704
GEN-2020-008 | 03 - Central | 515677 | BADGER 7 | 345 | 11.9285 | 12.0116 | 0.0831
GEN-2020-008 | 03 - Central | 515686 | BLUWND 7 | 345 | 10.8481 | 10.9168 | 0.0687
GEN-2020-008 | 03 - Central | 515800 | GRACMNT7 | 345 | 18.5674 | 18.57 | 0.0026
GEN-2020-008 | 03 - Central | 515825 | GRTWSRN7 | 345 | 8.8012 | 8.8157 | 0.0145
GEN-2020-008 | 03 - Central | 515852 | DGRASSE7 | 345 | 14.5842 | 14.6079 | 0.0237
GEN-2020-008 | 03 - Central | 515853 | DGRASSE4 | 138 | 14.8172 | 14.8241 | 0.0069
GEN-2020-008 | 03 - Central | 515951 | PERSIMN7 | 345 | 10.5732 | 10.5942 | 0.021
GEN-2020-008 | 03 - Central | 515961 | GUTHRIE7 | 345 | 12.1133 | 12.1408 | 0.0275
GEN-2020-008 | 03 - Central | 516059 | BECKHAM7 | 345 | 13.0616 | 13.0714 | 0.0098
GEN-2020-008 | 03 - Central | 516106 | BOBCAT 7 | 345 | 13.6351 | 13.6905 | 0.0554
GEN-2020-008 | 03 - Central | 516146 | 25MILE 7 | 345 | 9.5631 | 9.5903 | 0.0272
GEN-2020-008 | 03 - Central | 516159 | 25MILZ 7 | 345 | 9.5524 | 9.5795 | 0.0271
GEN-2020-008 | 03 - Central | 522899 | ANTHONY 3 | 115 | 2.308 | 2.3093 | 0.0013
GEN-2020-008 | 03 - Central | 522912 | Y ROAD 3 | 115 | 4.5569 | 4.5625 | 0.0056
GEN-2020-008 | 03 - Central | 522914 | BOYD 3 | 115 | 4.2679 | 4.2724 | 0.0045
GEN-2020-008 | 03 - Central | 522926 | BOURK 2 | 69 | 8.237 | 8.248 | 0.011
GEN-2020-008 | 03 - Central | 522930 | RED DEVIL 3 | 115 | 2.4029 | 2.4045 | 0.0016
GEN-2020-008 | 03 - Central | 522931 | REED 2 | 69 | 8.237 | 8.248 | 0.011
GEN-2020-008 | 03 - Central | 522935 | GOODWELL 3 | 115 | 3.4855 | 3.4888 | 0.0033
GEN-2020-008 | 03 - Central | 522942 | LITTAU 3 | 115 | 2.8859 | 2.888 | 0.0021
GEN-2020-008 | 03 - Central | 522952 | ROSE 3 | 115 | 1.5142 | 1.5147 | 0.0005
GEN-2020-008 | 03 - Central | 523012 | TC-ANTHY_TP3 | 115 | 2.4527 | 2.4541 | 0.0014
GEN-2020-008 | 03 - Central | 523024 | TC-BEAVER 3 | 115 | 1.5142 | 1.5147 | 0.0005
GEN-2020-008 | 03 - Central | 523089 | TC-TXCOUNTY2 | 69 | 8.237 | 8.248 | 0.011
GEN-2020-008 | 03 - Central | 523090 | TEXAS_CNTY 3 | 115 | 8.0048 | 8.0222 | 0.0174
GEN-2020-008 | 03 - Central | 523093 | HITCHLAND 3 | 115 | 16.4281 | 16.494 | 0.0659
GEN-2020-008 | 03 - Central | 523095 | HITCHLAND 6 | 230 | 13.2742 | 13.3883 | 0.1141
GEN-2020-008 | 03 - Central | 523097 | HITCHLAND 7 | 345 | 12.4664 | 12.658 | 0.1916
GEN-2020-008 | 03 - Central | 523101 | NOBLE_WND 7 | 345 | 12.424 | 12.6142 | 0.1902
GEN-2020-008 | 03 - Central | 523103 | NOBLE_WND 3 | 115 | 9.3865 | 9.4221 | 0.0356
GEN-2020-008 | 03 - Central | 523106 | TXPHSF 3 | 115 | 4.2892 | 4.2954 | 0.0062
GEN-2020-008 | 03 - Central | 523111 | NOVUS1 3 | 115 | 6.6451 | 6.6629 | 0.0178
GEN-2020-008 | 03 - Central | 523112 | NOVUS1 7 | 345 | 12.2482 | 12.4331 | 0.1849
GEN-2020-008 | 03 - Central | 523113 | TC-MCMURRY 3 | 115 | 6.274 | 6.2845 | 0.0105
GEN-2020-008 | 03 - Central | 523118 | BUFF_DUNES 7 | 345 | 6.2805 | 6.3257 | 0.0452
GEN-2020-008 | 03 - Central | 523120 | COLE 3 | 115 | 4.2679 | 4.2724 | 0.0045
GEN-2020-008 | 03 - Central | 523130 | GRPLNS-HV4-3 | 115 | 6.3933 | 6.4099 | 0.0166
GEN-2020-008 | 03 - Central | 523131 | GRPLNS-HV2-3 | 115 | 8.5979 | 8.6278 | 0.0299
GEN-2020-008 | 03 - Central | 523135 | LIPSCOMB 3 | 115 | 2.7855 | 2.7873 | 0.0018
GEN-2020-008 | 03 - Central | 523140 | TXFARMS 3 | 115 | 5.28 | 5.2855 | 0.0055
GEN-2020-008 | 03 - Central | 523145 | WADE_TP 3 | 115 | 3.5448 | 3.5477 | 0.0029
GEN-2020-008 | 03 - Central | 523147 | WADE 3 | 115 | 3.3502 | 3.3528 | 0.0026
GEN-2020-008 | 03 - Central | 523154 | OCHILTREE 3 | 115 | 6.1412 | 6.1499 | 0.0087
GEN-2020-008 | 03 - Central | 523155 | OCHILTREE 6 | 230 | 4.2195 | 4.2296 | 0.0101
GEN-2020-008 | 03 - Central | 523157 | PERRYTON 2 | 69 | 2.4636 | 2.4644 | 0.0008
GEN-2020-008 | 03 - Central | 523158 | PERRYTON 3 | 115 | 5.8553 | 5.8632 | 0.0079
GEN-2020-008 | 03 - Central | 523160 | FRISCO_WND 3 | 115 | 6.6584 | 6.6666 | 0.0082
GEN-2020-008 | 03 - Central | 523174 | GOODWELLWND3 | 115 | 6.8012 | 6.8086 | 0.0074
GEN-2020-008 | 03 - Central | 523175 | LASLEY 3 | 115 | 5.5893 | 5.5929 | 0.0036
GEN-2020-008 | 03 - Central | 523177 | RB-SPURLCK+3 | 115 | 5.7069 | 5.7096 | 0.0027
GEN-2020-008 | 03 - Central | 523185 | SPEARMAN 2 | 69 | 4.3166 | 4.3178 | 0.0012
GEN-2020-008 | 03 - Central | 523186 | SPEARMAN 3 | 115 | 8.7714 | 8.7795 | 0.0081
GEN-2020-008 | 03 - Central | 523195 | HANSFORD 3 | 115 | 9.4657 | 9.4832 | 0.0175
GEN-2020-008 | 03 - Central | 523215 | GEN-2011-022 | 345 | 8.6946 | 8.7873 | 0.0927
GEN-2020-008 | 03 - Central | 523217 | RB-KEMP 3 | 115 | 3.9961 | 3.997 | 0.0009
GEN-2020-008 | 03 - Central | 523221 | XIT_INTG 6 | 230 | 3.287 | 3.2878 | 0.0008
GEN-2020-008 | 03 - Central | 523256 | ETTER 3 | 115 | 5.6326 | 5.6345 | 0.0019
GEN-2020-008 | 03 - Central | 523267 | PRINGLE 6 | 230 | 4.4462 | 4.4473 | 0.0011
GEN-2020-008 | 03 - Central | 523277 | VALERO 3 | 115 | 9.7169 | 9.723 | 0.0061
GEN-2020-008 | 03 - Central | 523304 | MOORE_W 3 | 115 | 10.7078 | 10.7152 | 0.0074
GEN-2020-008 | 03 - Central | 523308 | MOORE_E 3 | 115 | 10.7078 | 10.7152 | 0.0074
GEN-2020-008 | 03 - Central | 523309 | MOORE_CNTY 6 | 230 | 6.8794 | 6.8872 | 0.0078
GEN-2020-008 | 03 - Central | 523322 | MCDWL_CREEK3 | 115 | 10.2548 | 10.2582 | 0.0034
GEN-2020-008 | 03 - Central | 523323 | MCDWL_CREEK6 | 230 | 9.3207 | 9.327 | 0.0063
GEN-2020-008 | 03 - Central | 523823 | CARPENTER 7 | 345 | 6.5918 | 7.1111 | 0.5193
GEN-2020-008 | 03 - Central | 523853 | FINNEY 7 | 345 | 10.1924 | 10.3199 | 0.1275
GEN-2020-008 | 03 - Central | 523869 | CHAN+TASCOS6 | 230 | 4.4418 | 4.4429 | 0.0011
GEN-2020-008 | 03 - Central | 523959 | POTTER_CO 6 | 230 | 23.3509 | 23.369 | 0.0181
GEN-2020-008 | 03 - Central | 523961 | POTTER_CO 7 | 345 | 14.0737 | 14.0942 | 0.0205
GEN-2020-008 | 03 - Central | 523977 | HARRNG_WST 6 | 230 | 27.6961 | 27.7105 | 0.0144
GEN-2020-008 | 03 - Central | 523978 | HARRNG_MID 6 | 230 | 27.6961 | 27.7105 | 0.0144
GEN-2020-008 | 03 - Central | 523979 | HARRNG_EST 6 | 230 | 27.6961 | 27.7105 | 0.0144
GEN-2020-008 | 03 - Central | 524007 | ROLLHILLS 3 | 115 | 20.3481 | 20.3521 | 0.004
GEN-2020-008 | 03 - Central | 524009 | CHERRY 3 | 115 | 19.4603 | 19.464 | 0.0037
GEN-2020-008 | 03 - Central | 524010 | ROLLHILLS 6 | 230 | 20.9377 | 20.9484 | 0.0107
GEN-2020-008 | 03 - Central | 524266 | BUSHLAND 3 | 115 | 9.8694 | 9.8704 | 0.001
GEN-2020-008 | 03 - Central | 524267 | BUSHLAND 6 | 230 | 10.3777 | 10.38 | 0.0023
GEN-2020-008 | 03 - Central | 524276 | WILDOR_WND 6 | 230 | 5.4132 | 5.4137 | 0.0005
GEN-2020-008 | 03 - Central | 524290 | WILDOR2_JUS6 | 230 | 7.1931 | 7.1942 | 0.0011
GEN-2020-008 | 03 - Central | 524296 | SPNSPUR_WND7 | 345 | 5.8873 | 5.8903 | 0.003
GEN-2020-008 | 03 - Central | 524299 | SPNSPUR_COL7 | 345 | 5.8873 | 5.8903 | 0.003
GEN-2020-008 | 03 - Central | 524623 | DEAFSMITH 6 | 230 | 7.9417 | 7.9425 | 0.0008
GEN-2020-008 | 03 - Central | 524909 | ROOSEVELT 6 | 230 | 9.7895 | 9.7899 | 0.0004
GEN-2020-008 | 03 - Central | 525213 | SWISHER 6 | 230 | 10.5013 | 10.5022 | 0.0009
GEN-2020-008 | 03 - Central | 525460 | NEWHART 3 | 115 | 14.7957 | 14.7967 | 0.001
GEN-2020-008 | 03 - Central | 525461 | NEWHART 6 | 230 | 10.7434 | 10.7445 | 0.0011
GEN-2020-008 | 03 - Central | 525481 | PLANT_X 6 | 230 | 23.1863 | 23.1894 | 0.0031
GEN-2020-008 | 03 - Central | 525531 | TOLK 6 | 230 | 29.9399 | 29.945 | 0.0051
GEN-2020-008 | 03 - Central | 525549 | TOLK 7 | 345 | 15.7164 | 15.7204 | 0.004
GEN-2020-008 | 03 - Central | 525584 | BLUECLDCOL 6 | 230 | 10.3144 | 10.3149 | 0.0005
GEN-2020-008 | 03 - Central | 525585 | BLUECLDPOI 6 | 230 | 10.9062 | 10.9068 | 0.0006
GEN-2020-008 | 03 - Central | 525586 | NEEDMORE 6 | 230 | 10.9062 | 10.9068 | 0.0006
GEN-2020-008 | 03 - Central | 525637 | LAMB_CNTY 6 | 230 | 5.7279 | 5.7281 | 0.0002
GEN-2020-008 | 03 - Central | 525830 | TUCO_INT 6 | 230 | 21.8663 | 21.8676 | 0.0013
GEN-2020-008 | 03 - Central | 525840 | ANTELOPE_1 6 | 230 | 21.6901 | 21.6914 | 0.0013
GEN-2020-008 | 03 - Central | 525957 | HALE_WNDCL16 | 230 | 10.7883 | 10.7886 | 0.0003
GEN-2020-008 | 03 - Central | 527598 | SAGA_NDCOL 7 | 345 | 7.7019 | 7.7023 | 0.0004
GEN-2020-008 | 03 - Central | 527599 | SAGA_SDCOL 7 | 345 | 8.967 | 8.9674 | 0.0004
GEN-2020-008 | 03 - Central | 527600 | SAGA_SMEAS 7 | 345 | 8.967 | 8.9674 | 0.0004
GEN-2020-008 | 03 - Central | 527601 | SAGA_NCOL 7 | 345 | 7.7019 | 7.7023 | 0.0004
GEN-2020-008 | 03 - Central | 527610 | SAGA_SCOL 7 | 345 | 8.967 | 8.9674 | 0.0004
GEN-2020-008 | 03 - Central | 527654 | RSVLT_CC_W 7 | 345 | 8.2302 | 8.2305 | 0.0003
GEN-2020-008 | 03 - Central | 527655 | RSVLT_CC_E 7 | 345 | 9.2674 | 9.2678 | 0.0004
GEN-2020-008 | 03 - Central | 527656 | CROSSROADS 7 | 345 | 10.4302 | 10.4308 | 0.0006
GEN-2020-008 | 03 - Central | 527666 | RSVLT_COL1 7 | 345 | 8.2302 | 8.2305 | 0.0003
GEN-2020-008 | 03 - Central | 527667 | RSVLT_COL2 7 | 345 | 8.2302 | 8.2305 | 0.0003
GEN-2020-008 | 03 - Central | 527802 | EDDY_CNTY 7 | 345 | 7.4472 | 7.4473 | 0.0001
GEN-2020-008 | 03 - Central | 527896 | HOBBS_INT 7 | 345 | 12.4965 | 12.4968 | 0.0003
GEN-2020-008 | 03 - Central | 530583 | POSTROCK7 | 345 | 8.2971 | 8.3009 | 0.0038
GEN-2020-008 | 03 - Central | 531210 | BLUEJAY3 | 115 | 2.213 | 2.2141 | 0.0011
GEN-2020-008 | 03 - Central | 531211 | CHRLSTN3 | 115 | 2.1491 | 2.1502 | 0.0011
GEN-2020-008 | 03 - Central | 531212 | TWNSPRG3 | 115 | 1.6716 | 1.6723 | 0.0007
GEN-2020-008 | 03 - Central | 531213 | SANTAFE3 | 115 | 2.8221 | 2.824 | 0.0019
GEN-2020-008 | 03 - Central | 531375 | PUCKET 3 | 115 | 5.0725 | 5.084 | 0.0115
GEN-2020-008 | 03 - Central | 531379 | JONES3 | 115 | 10.9759 | 10.9971 | 0.0212
GEN-2020-008 | 03 - Central | 531380 | HUGOTON2 | 69 | 2.9823 | 2.9918 | 0.0095
GEN-2020-008 | 03 - Central | 531384 | MOSCOW 2 | 69 | 2.2423 | 2.2498 | 0.0075
GEN-2020-008 | 03 - Central | 531385 | MOSCOWT2 | 69 | 2.3588 | 2.3671 | 0.0083
GEN-2020-008 | 03 - Central | 531388 | NORTH6 2 | 69 | 2.6537 | 2.6642 | 0.0105
GEN-2020-008 | 03 - Central | 531389 | NORTH6T2 | 69 | 3.1053 | 3.1198 | 0.0145
GEN-2020-008 | 03 - Central | 531392 | PIONTAP3 | 115 | 6.9869 | 7.0021 | 0.0152
GEN-2020-008 | 03 - Central | 531393 | PLYMELL3 | 115 | 8.0079 | 8.0236 | 0.0157
GEN-2020-008 | 03 - Central | 531395 | ROLLA 2 | 115 | 2.6508 | 2.6636 | 0.0128
GEN-2020-008 | 03 - Central | 531398 | SUBLETE3 | 115 | 6.2375 | 6.2496 | 0.0121
GEN-2020-008 | 03 - Central | 531400 | PK_GOAB3 | 115 | 5.0866 | 5.0982 | 0.0116
GEN-2020-008 | 03 - Central | 531404 | WALKMYR2 | 69 | 8.7202 | 8.8339 | 0.1137
GEN-2020-008 | 03 - Central | 531405 | WALKMYR3 | 115 | 10.2993 | 10.5697 | 0.2704
GEN-2020-008 | 03 - Central | 531406 | WOODS 2 | 69 | 6.4023 | 6.4645 | 0.0622
GEN-2020-008 | 03 - Central | 531407 | INGALLS3 | 115 | 2.8206 | 2.8225 | 0.0019
GEN-2020-008 | 03 - Central | 531408 | PIERCVL3 | 115 | 4.0454 | 4.0494 | 0.004
GEN-2020-008 | 03 - Central | 531420 | FLETCHR3 | 115 | 7.0432 | 7.0578 | 0.0146
GEN-2020-008 | 03 - Central | 531423 | GARDNCY2 | 69 | 3.7485 | 3.7497 | 0.0012
GEN-2020-008 | 03 - Central | 531426 | JAMESON3 | 115 | 10.4265 | 10.4451 | 0.0186
GEN-2020-008 | 03 - Central | 531429 | MINGO 3 | 115 | 12.8108 | 12.8267 | 0.0159
GEN-2020-008 | 03 - Central | 531433 | SCOTCTY3 | 115 | 9.0888 | 9.1046 | 0.0158
GEN-2020-008 | 03 - Central | 531440 | WILLIAM3 | 115 | 3.9343 | 3.9388 | 0.0045
GEN-2020-008 | 03 - Central | 531445 | GRDNCTY3 | 115 | 13.0031 | 13.0276 | 0.0245
GEN-2020-008 | 03 - Central | 531448 | HOLCOMB3 | 115 | 21.5655 | 21.657 | 0.0915
GEN-2020-008 | 03 - Central | 531449 | HOLCOMB7 | 345 | 10.2483 | 10.3753 | 0.127
GEN-2020-008 | 03 - Central | 531451 | MINGO 7 | 345 | 6.3044 | 6.317 | 0.0126
GEN-2020-008 | 03 - Central | 531464 | SETAB 3 | 115 | 10.647 | 10.6701 | 0.0231
GEN-2020-008 | 03 - Central | 531465 | SETAB 7 | 345 | 7.152 | 7.1901 | 0.0381
GEN-2020-008 | 03 - Central | 531469 | SPERVIL7 | 345 | 14.1082 | 14.1416 | 0.0334
GEN-2020-008 | 03 - Central | 531476 | SWNDTAP3 | 115 | 7.5154 | 7.5235 | 0.0081
GEN-2020-008 | 03 - Central | 531477 | S. WIND3 | 115 | 6.923 | 6.9298 | 0.0068
GEN-2020-008 | 03 - Central | 531479 | CHUGTON2 | 69 | 2.6842 | 2.692 | 0.0078
GEN-2020-008 | 03 - Central | 531480 | KSAVWTP3 | 115 | 12.6341 | 12.6575 | 0.0234
GEN-2020-008 | 03 - Central | 531481 | HUGOTON3 | 115 | 5.8657 | 5.9285 | 0.0628
GEN-2020-008 | 03 - Central | 531483 | GRANTTP3 | 115 | 5.0386 | 5.0634 | 0.0248
GEN-2020-008 | 03 - Central | 531484 | GRANT 3 | 115 | 4.7464 | 4.7683 | 0.0219
GEN-2020-008 | 03 - Central | 531485 | CNTRLPL3 | 115 | 6.172 | 6.1792 | 0.0072
GEN-2020-008 | 03 - Central | 531494 | ABBK 2 | 115 | 5.2764 | 5.3271 | 0.0507
GEN-2020-008 | 03 - Central | 531501 | BUCKNER7 | 345 | 9.5999 | 9.6505 | 0.0506
GEN-2020-008 | 03 - Central | 531502 | CIMRRN 7 | 345 | 7.6001 | 7.6317 | 0.0316
GEN-2020-008 | 03 - Central | 531504 | CIMWD2 7 | 345 | 7.726 | 7.7582 | 0.0322
GEN-2020-008 | 03 - Central | 531510 | HARBNGR3 | 115 | 10.9188 | 11.2449 | 0.3261
GEN-2020-008 | 03 - Central | 531512 | HARBNGR7 | 345 | 6.5727 | 7.0883 | 0.5156
GEN-2020-008 | 03 - Central | 531623 | EASTFORK3 | 115 | 10.1561 | 10.1658 | 0.0097
GEN-2020-008 | 03 - Central | 531632 | GEN-2015-065 | 345 | 5.5751 | 5.5847 | 0.0096
GEN-2020-008 | 03 - Central | 539117 | SPRVILL-EHVB | 230 | 12.9924 | 13.0073 | 0.0149
GEN-2020-008 | 03 - Central | 539640 | HAYNE3 | 115 | 5.6728 | 5.6939 | 0.0211
GEN-2020-008 | 03 - Central | 539652 | CMRIVTP3 | 115 | 6.0906 | 6.1129 | 0.0223
GEN-2020-008 | 03 - Central | 539654 | CIM-PLT3 | 115 | 6.8438 | 6.8755 | 0.0317
GEN-2020-008 | 03 - Central | 539695 | SPEARVL6 | 230 | 13.3168 | 13.3326 | 0.0158
GEN-2020-008 | 03 - Central | 539749 | N-CIMRN3 | 115 | 6.7642 | 6.795 | 0.0308
GEN-2020-008 | 03 - Central | 539759 | SPRVL 3 | 115 | 13.4184 | 13.4286 | 0.0102
GEN-2020-008 | 03 - Central | 539801 | THISTLE7 | 345 | 16.8799 | 16.8981 | 0.0182
GEN-2020-008 | 03 - Central | 539803 | IRONWOOD7 | 345 | 13.5834 | 13.6133 | 0.0299
GEN-2020-008 | 03 - Central | 539815 | IRONWOOD WF7 | 345 | 12.2852 | 12.3094 | 0.0242
GEN-2020-008 | 03 - Central | 560078 | G16-037-TAP | 345 | 9.7789 | 9.7816 | 0.0027
GEN-2020-008 | 03 - Central | 560577 | G06-44 | 115 | 6.6451 | 6.6629 | 0.0178
GEN-2020-008 | 03 - Central | 563269 | GEN-2015-093 | 345 | 10.1855 | 10.1862 | 0.0007
GEN-2020-008 | 03 - Central | 576395 | GEN-2010-014 | 345 | 8.6946 | 8.7873 | 0.0927
GEN-2020-008 | 03 - Central | 576397 | G10014G11022 | 345 | 8.6946 | 8.7873 | 0.0927
GEN-2020-008 | 03 - Central | 579480 | GEN-2008-124 | 345 | 13.1245 | 13.1523 | 0.0278
GEN-2020-008 | 03 - Central | 585190 | GEN-2015-082 | 345 | 6.4439 | 6.4681 | 0.0242
GEN-2020-008 | 03 - Central | 585300 | GEN-2015-095 | 138 | 14.6279 | 14.6346 | 0.0067
GEN-2020-008 | 03 - Central | 585410 | GREAT_WESTRN | 345 | 8.8188 | 8.8333 | 0.0145
GEN-2020-008 | 03 - Central | 585420 | COWBOY_RIDGE | 345 | 6.8058 | 6.8145 | 0.0087
GEN-2020-008 | 03 - Central | 585430 | PRSIMN_CRK1 | 345 | 10.6714 | 10.6928 | 0.0214
GEN-2020-008 | 03 - Central | 585440 | PRSIMN_CRK2 | 345 | 9.8091 | 9.8271 | 0.018
GEN-2020-008 | 03 - Central | 587230 | GEN-2016-037 | 345 | 9.289 | 9.2914 | 0.0024
GEN-2020-008 | 03 - Central | 588560 | GEN-2017-011 | 345 | 11.2981 | 11.3361 | 0.038
GEN-2020-008 | 03 - Central | 588630 | GEN-2017-018 | 345 | 16.8799 | 16.8981 | 0.0182
GEN-2020-008 | 03 - Central | 588860 | GEN-2017-047 | 115 | 4.1784 | 4.1826 | 0.0042
GEN-2020-008 | 03 - Central | 589380 | GEN-2017-100 | 115 | 4.8535 | 4.8598 | 0.0063
GEN-2020-008 | 03 - Central | 599950 | LAMAR7 | 345 | 2.7181 | 2.7258 | 0.0077
GEN-2020-008 | 03 - Central | 599955 | PNM-DC6 | 230 | 9.7895 | 9.7899 | 0.0004
GEN-2020-008 | 03 - Central | 640325 | REDWILO3 | 345 | 6.5146 | 6.5183 | 0.0037
GEN-2020-008 | 03 - Central | 762132 | GEN-2017-158 | 230 | 12.7144 | 12.7153 | 0.0009
GEN-2020-008 | 03 - Central | 762471 | GEN-2018-009 | 115 | 3.2096 | 3.2142 | 0.0046
GEN-2020-008 | 03 - Central | 762658 | GEN-2018-030 | 345 | 3.1813 | 3.1916 | 0.0103
GEN-2020-008 | 03 - Central | 762662 | G18-030-TAP | 345 | 3.3773 | 3.3892 | 0.0119
GEN-2020-008 | 03 - Central | 762834 | GEN-2018-049 | 345 | 7.1985 | 7.2017 | 0.0032
GEN-2020-008 | 03 - Central | 763186 | GEN-2018-089 | 230 | 10.4405 | 10.4416 | 0.0011
GEN-2020-008 | 03 - Central | 763483 | GEN-2019-003 | 230 | 8.7333 | 8.7336 | 0.0003
GEN-2020-008 | 03 - Central | 763527 | GEN-2019-012 | 345 | 17.2356 | 17.2912 | 0.0556
GEN-2020-008 | 03 - Central | 763538 | GEN-2019-013 | 230 | 3.7883 | 3.7887 | 0.0004
GEN-2020-008 | 03 - Central | 763670 | GEN-2019-030 | 345 | 9.7016 | 9.7142 | 0.0126
GEN-2020-008 | 03 - Central | 763677 | G19-030-TAP | 345 | 11.7708 | 11.7898 | 0.019
GEN-2020-008 | 03 - Central | 763769 | GEN-2019-045 | 138 | 14.8172 | 14.8241 | 0.0069
GEN-2020-008 | 03 - Central | 764825 | GEN-2020-017 | 230 | 5.7095 | 5.7096 | 0.0001
GEN-2020-008 | 03 - Central | 764980 | GEN-2020-008 | 345 | 6.5918 | 7.1111 | 0.5193
GEN-2020-008 | 03 - Central | 900001 | TRAVERSE3 | 345 | 5.4644 | 5.4647 | 0.0003
GEN-2020-008 | 03 - Central | 900002 | TRAVERSE-2 | 345 | 4.0935 | 4.0937 | 0.0002
GEN-2020-008 | 03 - Central | 900003 | TRAVERSE1 | 345 | 3.805 | 3.8052 | 0.0002
GEN-2020-008 | 03 - Central | 900004 | TRW2-TRW3 | 345 | 4.7533 | 4.7535 | 0.0002
GEN-2020-052 | 03 - Central | 300042 | 7HUBEN | 345 | 10.5761 | 10.5775 | 0.0014
GEN-2020-052 | 03 - Central | 300045 | 7MORGAN | 345 | 13.9856 | 13.9925 | 0.0069
GEN-2020-052 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 16.0729 | 16.1277 | 0.0548
GEN-2020-052 | 03 - Central | 300740 | 7SPORTSMAN | 345 | 24.6113 | 24.6206 | 0.0093
GEN-2020-052 | 03 - Central | 300741 | 5SPORTSMAN | 161 | 40.9278 | 40.935 | 0.0072
GEN-2020-052 | 03 - Central | 300794 | 5LAMAR | 161 | 8.9423 | 8.9451 | 0.0028
GEN-2020-052 | 03 - Central | 300949 | 7JASPER | 345 | 13.0166 | 13.0411 | 0.0245
GEN-2020-052 | 03 - Central | 300950 | 5JASPER | 161 | 13.0954 | 13.1047 | 0.0093
GEN-2020-052 | 03 - Central | 301348 | 5CHOTEAU2 | 161 | 42.5534 | 42.56 | 0.0066
GEN-2020-052 | 03 - Central | 301622 | 5MORGANXF2 | 161 | 19.7435 | 19.7477 | 0.0042
GEN-2020-052 | 03 - Central | 506945 | CHAMSPR7 | 345 | 10.4384 | 10.4392 | 0.0008
GEN-2020-052 | 03 - Central | 509721 | BA.NO-S4 | 138 | 12.6809 | 12.6819 | 0.001
GEN-2020-052 | 03 - Central | 509737 | BA101 S4 | 138 | 18.6801 | 18.6819 | 0.0018
GEN-2020-052 | 03 - Central | 509743 | DENVR-E4 | 138 | 8.2939 | 8.2946 | 0.0007
GEN-2020-052 | 03 - Central | 509745 | CLARKSV7 | 345 | 20.6549 | 20.6588 | 0.0039
GEN-2020-052 | 03 - Central | 509746 | DENVTAP4 | 138 | 9.725 | 9.7259 | 0.0009
GEN-2020-052 | 03 - Central | 509755 | WEKIWA-7 | 345 | 22.3858 | 22.3948 | 0.009
GEN-2020-052 | 03 - Central | 509757 | WEKIWA-4 | 138 | 33.5749 | 33.5813 | 0.0064
GEN-2020-052 | 03 - Central | 509768 | BA101ST4 | 138 | 19.3805 | 19.3824 | 0.0019
GEN-2020-052 | 03 - Central | 509769 | BA101-N4 | 138 | 20.2787 | 20.281 | 0.0023
GEN-2020-052 | 03 - Central | 509773 | RSS T1 4 | 138 | 52.0798 | 52.0876 | 0.0078
GEN-2020-052 | 03 - Central | 509782 | R.S.S.-7 | 345 | 30.7302 | 30.7387 | 0.0085
GEN-2020-052 | 03 - Central | 509786 | BA.N-ST4 | 138 | 24.6657 | 24.6693 | 0.0036
GEN-2020-052 | 03 - Central | 509806 | ONETA--4 | 138 | 51.0833 | 51.0993 | 0.016
GEN-2020-052 | 03 - Central | 509807 | ONETA--7 | 345 | 29.5153 | 29.5305 | 0.0152
GEN-2020-052 | 03 - Central | 509817 | T.NO.--4 | 138 | 35.6791 | 35.6916 | 0.0125
GEN-2020-052 | 03 - Central | 509822 | W.ED.-E4 | 138 | 8.1271 | 8.1277 | 0.0006
GEN-2020-052 | 03 - Central | 509834 | COGENT 7 | 345 | 28.7026 | 28.7099 | 0.0073
GEN-2020-052 | 03 - Central | 509836 | OEC 7 | 345 | 29.2421 | 29.2569 | 0.0148
GEN-2020-052 | 03 - Central | 509852 | T.NO.--7 | 345 | 24.2627 | 24.2856 | 0.0229
GEN-2020-052 | 03 - Central | 509869 | 121LYNN4 | 138 | 18.287 | 18.2888 | 0.0018
GEN-2020-052 | 03 - Central | 509870 | SAPLPRD7 | 345 | 22.679 | 22.6852 | 0.0062
GEN-2020-052 | 03 - Central | 509875 | RSS T2 4 | 138 | 52.9862 | 52.9943 | 0.0081
GEN-2020-052 | 03 - Central | 509891 | BA_71ST4 | 138 | 24.0134 | 24.0167 | 0.0033
GEN-2020-052 | 03 - Central | 509895 | T.NO.2-4 | 138 | 35.6239 | 35.6365 | 0.0126
GEN-2020-052 | 03 - Central | 510378 | SCOFCTY4 | 138 | 8.8498 | 8.8574 | 0.0076
GEN-2020-052 | 03 - Central | 510379 | DELWARE4 | 138 | 11.4908 | 11.5244 | 0.0336
GEN-2020-052 | 03 - Central | 510380 | DELWARE7 | 345 | 12.0993 | 12.2209 | 0.1216
GEN-2020-052 | 03 - Central | 510406 | N.E.S.-7 | 345 | 19.3689 | 19.4283 | 0.0594
GEN-2020-052 | 03 - Central | 510420 | SCOFFEYV4 | 138 | 8.4615 | 8.4685 | 0.007
GEN-2020-052 | 03 - Central | 512650 | GRDA1 7 | 345 | 26.9728 | 26.9828 | 0.01
GEN-2020-052 | 03 - Central | 512656 | GRDA1 5 | 161 | 44.3116 | 44.321 | 0.0094
GEN-2020-052 | 03 - Central | 512694 | CLEVLND7 | 345 | 15.0732 | 15.0776 | 0.0044
GEN-2020-052 | 03 - Central | 512729 | CLEVLND 4 | 138 | 17.1527 | 17.1544 | 0.0017
GEN-2020-052 | 03 - Central | 512734 | FARML 4 | 138 | 8.4362 | 8.4448 | 0.0086
GEN-2020-052 | 03 - Central | 512735 | COFCTY2 | 69 | 9.0546 | 9.0579 | 0.0033
GEN-2020-052 | 03 - Central | 512750 | TONECE7 | 345 | 15.4928 | 15.4951 | 0.0023
GEN-2020-052 | 03 - Central | 512865 | GREC TAP5 | 345 | 25.7903 | 25.7994 | 0.0091
GEN-2020-052 | 03 - Central | 513590 | CUSTDAY1 5 | 161 | 16.8384 | 16.8404 | 0.002
GEN-2020-052 | 03 - Central | 513591 | HERRON 5 | 161 | 17.2555 | 17.2577 | 0.0022
GEN-2020-052 | 03 - Central | 513593 | IGLOOV1 5 | 161 | 17.4524 | 17.4547 | 0.0023
GEN-2020-052 | 03 - Central | 513595 | IGLOOV2 5 | 161 | 17.4524 | 17.4547 | 0.0023
GEN-2020-052 | 03 - Central | 513596 | IGLOOV 7 | 345 | 20.5085 | 20.5151 | 0.0066
GEN-2020-052 | 03 - Central | 514803 | SOONER 7 | 345 | 26.2487 | 26.2537 | 0.005
GEN-2020-052 | 03 - Central | 514909 | REDBUD 7 | 345 | 26.9937 | 26.9943 | 0.0006
GEN-2020-052 | 03 - Central | 515224 | MUSKOGE7 | 345 | 28.2529 | 28.2557 | 0.0028
GEN-2020-052 | 03 - Central | 515235 | PECANCK7 | 345 | 21.8164 | 21.8185 | 0.0021
GEN-2020-052 | 03 - Central | 515894 | THUNDER7 | 345 | 10.5507 | 10.5515 | 0.0008
GEN-2020-052 | 03 - Central | 532774 | SWISVAL7 | 345 | 17.634 | 17.6348 | 0.0008
GEN-2020-052 | 03 - Central | 532777 | G17-009-TAP | 345 | 11.9937 | 12.069 | 0.0753
GEN-2020-052 | 03 - Central | 532778 | GEN-2017-009 | 345 | 11.0888 | 11.1528 | 0.064
GEN-2020-052 | 03 - Central | 532780 | CANEYRV7 | 345 | 9.9265 | 9.9404 | 0.0139
GEN-2020-052 | 03 - Central | 532781 | CANEYWF7 | 345 | 9.6463 | 9.6594 | 0.0131
GEN-2020-052 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18.2881 | 18.5326 | 0.2445
GEN-2020-052 | 03 - Central | 532794 | ROSEHIL7 | 345 | 19.6684 | 19.6793 | 0.0109
GEN-2020-052 | 03 - Central | 532797 | WOLFCRK7 | 345 | 22.1247 | 22.1344 | 0.0097
GEN-2020-052 | 03 - Central | 532799 | WAVERLY7 | 345 | 18.6075 | 18.6143 | 0.0068
GEN-2020-052 | 03 - Central | 532800 | LATHAMS7 | 345 | 10.5896 | 10.6019 | 0.0123
GEN-2020-052 | 03 - Central | 532801 | ELKRVR17 | 345 | 9.3832 | 9.3928 | 0.0096
GEN-2020-052 | 03 - Central | 532802 | WAVERTX7 | 345 | 15.1841 | 15.1886 | 0.0045
GEN-2020-052 | 03 - Central | 532926 | BAKER 2 | 69 | 5.1276 | 5.1286 | 0.001
GEN-2020-052 | 03 - Central | 532934 | MARMTNE5 | 161 | 8.4081 | 8.411 | 0.0029
GEN-2020-052 | 03 - Central | 532935 | MARMTNW5 | 161 | 8.4043 | 8.4072 | 0.0029
GEN-2020-052 | 03 - Central | 532937 | NEOSHO 5 | 161 | 23.8327 | 23.946 | 0.1133
GEN-2020-052 | 03 - Central | 533003 | LIBERTY4 | 138 | 7.6128 | 7.6188 | 0.006
GEN-2020-052 | 03 - Central | 533005 | NEPARSN4 | 138 | 13.1304 | 13.1555 | 0.0251
GEN-2020-052 | 03 - Central | 533008 | TV1MNDV4 | 138 | 7.261 | 7.2674 | 0.0064
GEN-2020-052 | 03 - Central | 533020 | NEOSHOS4 | 138 | 25.4045 | 25.5172 | 0.1127
GEN-2020-052 | 03 - Central | 533021 | NEOSHO 4 | 138 | 25.4475 | 25.5606 | 0.1131
GEN-2020-052 | 03 - Central | 533022 | NEOSHON4 | 138 | 25.3283 | 25.4402 | 0.1119
GEN-2020-052 | 03 - Central | 533629 | CC2SHAR2 | 69 | 4.8476 | 4.8477 | 0.0001
GEN-2020-052 | 03 - Central | 533639 | MARMATN2 | 69 | 9.0319 | 9.0332 | 0.0013
GEN-2020-052 | 03 - Central | 533640 | MCKEE 2 | 69 | 4.3643 | 4.3646 | 0.0003
GEN-2020-052 | 03 - Central | 533647 | UN1ELSM2 | 69 | 8.1262 | 8.1272 | 0.001
GEN-2020-052 | 03 - Central | 533653 | WOLFCRK2 | 69 | 6.2779 | 6.2781 | 0.0002
GEN-2020-052 | 03 - Central | 533695 | LABETTE2 | 69 | 4.219 | 4.2203 | 0.0013
GEN-2020-052 | 03 - Central | 533696 | LABETTS2 | 69 | 6.3959 | 6.3991 | 0.0032
GEN-2020-052 | 03 - Central | 533702 | ORDNCE 2 | 69 | 6.3299 | 6.333 | 0.0031
GEN-2020-052 | 03 - Central | 533703 | ORDNJCT2 | 69 | 8.7672 | 8.7733 | 0.0061
GEN-2020-052 | 03 - Central | 533704 | PARSONS2 | 69 | 5.0886 | 5.0906 | 0.002
GEN-2020-052 | 03 - Central | 533758 | CRAWFOR2 | 69 | 7.5694 | 7.5728 | 0.0034
GEN-2020-052 | 03 - Central | 533763 | HUDSON-2 | 69 | 4.8041 | 4.8048 | 0.0007
GEN-2020-052 | 03 - Central | 533768 | NEOSHON2 | 69 | 23.9998 | 24.0451 | 0.0453
GEN-2020-052 | 03 - Central | 533772 | SE1GREE2 | 69 | 6.3113 | 6.3132 | 0.0019
GEN-2020-052 | 03 - Central | 533773 | SOPITT 2 | 69 | 5.7459 | 5.7467 | 0.0008
GEN-2020-052 | 03 - Central | 533778 | NEOSHOS2 | 69 | 24.0248 | 24.0702 | 0.0454
GEN-2020-052 | 03 - Central | 541198 | PECULR 7 | 345 | 21.2309 | 21.2331 | 0.0022
GEN-2020-052 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2.6785 | 2.6785 | 0
GEN-2020-052 | 03 - Central | 542940 | ATLNTIC7 | 345 | 22.1858 | 22.188 | 0.0022
GEN-2020-052 | 03 - Central | 542965 | W.GRDNR7 | 345 | 31.1664 | 31.1725 | 0.0061
GEN-2020-052 | 03 - Central | 542966 | WGARDNR5 | 161 | 30.8139 | 30.8153 | 0.0014
GEN-2020-052 | 03 - Central | 542968 | STILWEL7 | 345 | 26.7746 | 26.7794 | 0.0048
GEN-2020-052 | 03 - Central | 542969 | STILWEL5 | 161 | 41.6802 | 41.684 | 0.0038
GEN-2020-052 | 03 - Central | 542981 | LACYGNE7 | 345 | 28.5915 | 28.609 | 0.0175
GEN-2020-052 | 03 - Central | 543054 | CEDARNL5 | 161 | 10.941 | 10.9412 | 0.0002
GEN-2020-052 | 03 - Central | 543105 | BULLCRK5 | 161 | 29.7865 | 29.7878 | 0.0013
GEN-2020-052 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27.8139 | 27.8304 | 0.0165
GEN-2020-052 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27.8139 | 27.8304 | 0.0165
GEN-2020-052 | 03 - Central | 543650 | DAKOTA_5 | 161 | 7.2159 | 7.2173 | 0.0014
GEN-2020-052 | 03 - Central | 543651 | PRQN_WIND5 | 161 | 6.1033 | 6.1042 | 0.0009
GEN-2020-052 | 03 - Central | 543659 | LACYGNE2 | 69 | 2.8177 | 2.8177 | 0
GEN-2020-052 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 0.6739 | 0.6739 | 0
GEN-2020-052 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 0.6454 | 0.6454 | 0
GEN-2020-052 | 03 - Central | 547459 | WWR477 | 161 | 22.2737 | 22.2791 | 0.0054
GEN-2020-052 | 03 - Central | 547467 | ORO110 5 | 161 | 20.0723 | 20.0777 | 0.0054
GEN-2020-052 | 03 - Central | 547469 | RIV4525 | 161 | 24.7988 | 24.8094 | 0.0106
GEN-2020-052 | 03 - Central | 547498 | STL439 5 | 161 | 24.3406 | 24.3471 | 0.0065
GEN-2020-052 | 03 - Central | 547501 | RIV453 5 | 161 | 23.3902 | 23.3993 | 0.0091
GEN-2020-052 | 03 - Central | 547502 | RIV167 5 | 161 | 22.9591 | 22.968 | 0.0089
GEN-2020-052 | 03 - Central | 547503 | RIV452T 5 | 161 | 24.325 | 24.335 | 0.01
GEN-2020-052 | 03 - Central | 547541 | RIV167 2 | 69 | 17.9845 | 17.9864 | 0.0019
GEN-2020-052 | 03 - Central | 547729 | BAX488 5 | 161 | 15.2718 | 15.2752 | 0.0034
GEN-2020-052 | 03 - Central | 549984 | BROOKLINE 7 | 345 | 11.9535 | 11.9564 | 0.0029
GEN-2020-052 | 03 - Central | 560056 | G15-066T | 345 | 18.3842 | 18.3876 | 0.0034
GEN-2020-052 | 03 - Central | 560389 | GEN-2010-055 | 138 | 33.5749 | 33.5813 | 0.0064
GEN-2020-052 | 03 - Central | 585040 | GEN-2015-066 | 345 | 18.2118 | 18.2152 | 0.0034
GEN-2020-052 | 03 - Central | 588039 | G16133G16146 | 345 | 30.7302 | 30.7387 | 0.0085
GEN-2020-052 | 03 - Central | 588040 | G16133_345GS | 345 | 16.0205 | 16.0228 | 0.0023
GEN-2020-052 | 03 - Central | 588041 | G16133_765GS | 765 | 5.298 | 5.2985 | 0.0005
GEN-2020-052 | 03 - Central | 588043 | G16133_765MP | 765 | 2.7659 | 2.7661 | 0.0002
GEN-2020-052 | 03 - Central | 588045 | G16133_765CS | 765 | 1.7221 | 1.7222 | 0.0001
GEN-2020-052 | 03 - Central | 588046 | G16133_345CS | 345 | 3.5138 | 3.5139 | 0.0001
GEN-2020-052 | 03 - Central | 588050 | ZONE-1 SUB | 345 | 3.0897 | 3.0898 | 0.0001
GEN-2020-052 | 03 - Central | 588060 | ZONE-2 SUB | 345 | 3.0929 | 3.093 | 0.0001
GEN-2020-052 | 03 - Central | 588070 | ZONE-3 SUB | 345 | 3.1567 | 3.1568 | 0.0001
GEN-2020-052 | 03 - Central | 588080 | ZONE-4 SUB | 345 | 3.4871 | 3.4872 | 0.0001
GEN-2020-052 | 03 - Central | 588090 | ZONE-5 SUB | 345 | 3.1497 | 3.1498 | 0.0001
GEN-2020-052 | 03 - Central | 588100 | ZONE-6 SUB | 345 | 3.2895 | 3.2896 | 0.0001
GEN-2020-052 | 03 - Central | 588500 | GEN-2017-005 | 161 | 6.9706 | 6.9722 | 0.0016
GEN-2020-052 | 03 - Central | 588504 | G17-005-TAP | 161 | 7.0559 | 7.0576 | 0.0017
GEN-2020-052 | 03 - Central | 588660 | GEN-2017-022 | 138 | 8.9107 | 8.917 | 0.0063
GEN-2020-052 | 03 - Central | 588664 | G17-022-TAP | 138 | 9.2776 | 9.2844 | 0.0068
GEN-2020-052 | 03 - Central | 709500 | GI-95_POI | 345 | 8.342 | 8.3444 | 0.0024
GEN-2020-052 | 03 - Central | 709501 | GI-95_HV | 345 | 8.342 | 8.3444 | 0.0024
GEN-2020-052 | 03 - Central | 760389 | GEN-2017-140 | 345 | 1.2086 | 1.2086 | 0
GEN-2020-052 | 03 - Central | 760393 | G17-140-BUS | 345 | 1.2012 | 1.2012 | 0
GEN-2020-052 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.658 | 19.6744 | 0.0164
GEN-2020-052 | 03 - Central | 760921 | G17-209-TAP | 345 | 20.182 | 20.1994 | 0.0174
GEN-2020-052 | 03 - Central | 762279 | GEN-2017-195 | 345 | 31.0739 | 31.08 | 0.0061
GEN-2020-052 | 03 - Central | 762300 | GEN-2017-196 | 345 | 30.9763 | 30.9823 | 0.006
GEN-2020-052 | 03 - Central | 762636 | GEN-2018-028 | 138 | 35.6076 | 35.6202 | 0.0126
GEN-2020-052 | 03 - Central | 762680 | GEN-2018-032 | 345 | 12.037 | 12.1425 | 0.1055
GEN-2020-052 | 03 - Central | 762823 | GEN-2018-048 | 345 | 16.2564 | 16.2576 | 0.0012
GEN-2020-052 | 03 - Central | 763109 | GEN-2018-079 | 138 | 6.6078 | 6.6173 | 0.0095
GEN-2020-052 | 03 - Central | 763113 | G18-079-TAP | 138 | 9.4012 | 9.4204 | 0.0192
GEN-2020-052 | 03 - Central | 764300 | GEN-2020-079 | 161 | 15.4035 | 15.4113 | 0.0078
GEN-2020-052 | 03 - Central | 764310 | G20-079-TAP | 161 | 18.5953 | 18.6071 | 0.0118
GEN-2020-052 | 03 - Central | 764375 | GEN-2020-058 | 345 | 22.1407 | 22.1428 | 0.0021
GEN-2020-052 | 03 - Central | 765100 | GEN-2020-052 | 345 | 9.5604 | 9.928 | 0.3676
GEN-2020-052 | 03 - Central | 765110 | G20-052-TAP | 345 | 12.7539 | 13.1185 | 0.3646
GEN-2020-052 | 03 - Central | 765115 | GEN-2020-057 | 345 | 22.1408 | 22.1429 | 0.0021
GEN-2020-052 | 03 - Central | 765145 | GEN-2020-076 | 345 | 12.5494 | 12.5518 | 0.0024
GEN-2020-052 | 03 - Central | 765155 | G20-076-TAP | 345 | 12.5571 | 12.5595 | 0.0024
GEN-2020-052 | 03 - Central | 765160 | GEN-2020-086 | 345 | 12.55 | 12.5524 | 0.0024
GEN-2020-052 | 03 - Central | 765175 | GEN-2020-089 | 161 | 4.2639 | 4.2644 | 0.0005
GEN-2020-052 | 03 - Central | 765190 | GEN-2020-090 | 345 | 8.7178 | 8.7262 | 0.0084
GEN-2020-052 | 03 - Central | 765200 | G20-090-TAP | 345 | 9.9421 | 9.9531 | 0.011
GEN-2020-052 | 03 - Central | 766260 | GEN-2020-007 | 345 | 25.1422 | 25.1555 | 0.0133
GEN-2020-052 | 03 - Central | 766261 | G20-007-TAP | 345 | 27.7536 | 27.7699 | 0.0163
GEN-2020-056 | 03 - Central | 530552 | GORHAM 3 | 115 | 3.2384 | 3.2387 | 0.0003
GEN-2020-056 | 03 - Central | 530553 | S HAYS 3 | 115 | 8.8584 | 8.8611 | 0.0027
GEN-2020-056 | 03 - Central | 530563 | HEIZER 2 | 69 | 9.1534 | 9.1625 | 0.0091
GEN-2020-056 | 03 - Central | 530568 | GB NTH 2 | 69 | 7.0644 | 7.0697 | 0.0053
GEN-2020-056 | 03 - Central | 530571 | SUSANK 2 | 69 | 1.6735 | 1.6738 | 0.0003
GEN-2020-056 | 03 - Central | 530572 | BNK HL 2 | 69 | 1.2701 | 1.2702 | 0.0001
GEN-2020-056 | 03 - Central | 530573 | HITHMN 2 | 69 | 1.1512 | 1.1514 | 0.0002
GEN-2020-056 | 03 - Central | 530582 | S HAYS6 | 230 | 9.2967 | 9.3026 | 0.0059
GEN-2020-056 | 03 - Central | 530584 | POSTROCK6 | 230 | 11.3755 | 11.3808 | 0.0053
GEN-2020-056 | 03 - Central | 530586 | ALBERT 2 | 69 | 3.8026 | 3.804 | 0.0014
GEN-2020-056 | 03 - Central | 530587 | WSPRTTP2 | 69 | 6.2264 | 6.2305 | 0.0041
GEN-2020-056 | 03 - Central | 530588 | WSTPRT 2 | 69 | 5.1729 | 5.1757 | 0.0028
GEN-2020-056 | 03 - Central | 530589 | BKHLTAP2 | 69 | 1.5102 | 1.5104 | 0.0002
GEN-2020-056 | 03 - Central | 530601 | HEIZER 3 | 115 | 12.7262 | 12.7591 | 0.0329
GEN-2020-056 | 03 - Central | 530602 | LAXTAP 3 | 115 | 4.2901 | 4.2923 | 0.0022
GEN-2020-056 | 03 - Central | 530603 | LACROS 3 | 115 | 3.7161 | 3.7178 | 0.0017
GEN-2020-056 | 03 - Central | 530608 | NEKOMA 3 | 115 | 4.165 | 4.1668 | 0.0018
GEN-2020-056 | 03 - Central | 530609 | HZRNGPL3 | 115 | 8.1423 | 8.1558 | 0.0135
GEN-2020-056 | 03 - Central | 530610 | SHAYS_230 | 230 | 3.593 | 3.5937 | 0.0007
GEN-2020-056 | 03 - Central | 530679 | SEWRDMW3 | 115 | 5.2952 | 5.2985 | 0.0033
GEN-2020-056 | 03 - Central | 530680 | HEIZER 6 | 230 | 9.1599 | 9.1745 | 0.0146
GEN-2020-056 | 03 - Central | 530681 | BUSHTON3 | 115 | 5.1616 | 5.1762 | 0.0146
GEN-2020-056 | 03 - Central | 530684 | RUSLPMP3 | 115 | 2.1143 | 2.1145 | 0.0002
GEN-2020-056 | 03 - Central | 530702 | BUCKEYE_230 | 230 | 8.3036 | 8.3063 | 0.0027
GEN-2020-056 | 03 - Central | 530714 | ANGUS 3 | 115 | 5.4568 | 5.4578 | 0.001
GEN-2020-056 | 03 - Central | 530725 | PFEIFER 3 | 115 | 3.5739 | 3.5743 | 0.0004
GEN-2020-056 | 03 - Central | 531373 | RHOADES3 | 115 | 3.282 | 3.2832 | 0.0012
GEN-2020-056 | 03 - Central | 532871 | CIRCLE 6 | 230 | 8.8727 | 8.8801 | 0.0074
GEN-2020-056 | 03 - Central | 539117 | SPRVILL-EHVB | 230 | 13.005 | 13.0073 | 0.0023
GEN-2020-056 | 03 - Central | 539642 | ELLSWTP3 | 115 | 4.1059 | 4.1964 | 0.0905
GEN-2020-056 | 03 - Central | 539643 | ROLLHLS3 | 115 | 3.763 | 3.8288 | 0.0658
GEN-2020-056 | 03 - Central | 539644 | COVERT 3 | 115 | 2.7411 | 2.7725 | 0.0314
GEN-2020-056 | 03 - Central | 539647 | IONIA 3 | 115 | 3.0719 | 3.0763 | 0.0044
GEN-2020-056 | 03 - Central | 539650 | BELOIT 3 | 115 | 3.3071 | 3.3096 | 0.0025
GEN-2020-056 | 03 - Central | 539660 | EHALLTP3 | 115 | 3.3934 | 3.4223 | 0.0289
GEN-2020-056 | 03 - Central | 539661 | 24-FREY3 | 115 | 8.7707 | 8.7843 | 0.0136
GEN-2020-056 | 03 - Central | 539662 | ELLSWTH3 | 115 | 3.6213 | 3.6425 | 0.0212
GEN-2020-056 | 03 - Central | 539663 | GLENELD3 | 115 | 2.9174 | 2.9204 | 0.003
GEN-2020-056 | 03 - Central | 539666 | GBENDTP3 | 115 | 9.0574 | 9.0719 | 0.0145
GEN-2020-056 | 03 - Central | 539669 | JEWELL 3 | 115 | 3.2571 | 3.2601 | 0.003
GEN-2020-056 | 03 - Central | 539678 | GRTBEND3 | 115 | 12.8276 | 12.8626 | 0.035
GEN-2020-056 | 03 - Central | 539679 | GRTBEND6 | 230 | 9.2202 | 9.2349 | 0.0147
GEN-2020-056 | 03 - Central | 539681 | N-GBEND3 | 115 | 9.676 | 9.6945 | 0.0185
GEN-2020-056 | 03 - Central | 539684 | OTISSUB3 | 115 | 3.0665 | 3.0685 | 0.002
GEN-2020-056 | 03 - Central | 539685 | PHLBURG3 | 115 | 3.5777 | 3.5812 | 0.0035
GEN-2020-056 | 03 - Central | 539686 | PLAINVL3 | 115 | 3.7768 | 3.7782 | 0.0014
GEN-2020-056 | 03 - Central | 539689 | 2ND-KS 3 | 115 | 8.6591 | 8.6723 | 0.0132
GEN-2020-056 | 03 - Central | 539692 | SEWARD 3 | 115 | 5.9935 | 5.9976 | 0.0041
GEN-2020-056 | 03 - Central | 539693 | SMITH-C3 | 115 | 3.9173 | 3.9291 | 0.0118
GEN-2020-056 | 03 - Central | 539695 | SPEARVL6 | 230 | 13.3302 | 13.3326 | 0.0024
GEN-2020-056 | 03 - Central | 539696 | ST-JOHN3 | 115 | 5.5166 | 5.5183 | 0.0017
GEN-2020-056 | 03 - Central | 539698 | WALDO 3 | 115 | 2.8655 | 2.9088 | 0.0433
GEN-2020-056 | 03 - Central | 539701 | RUSSELL3 | 115 | 3.5974 | 3.6983 | 0.1009
GEN-2020-056 | 03 - Central | 763329 | GEN-2018-116 | 115 | 8.7523 | 8.7658 | 0.0135
GEN-2020-056 | 03 - Central | 763846 | G19-053/055 | 230 | 7.4673 | 7.4701 | 0.0028
GEN-2020-056 | 03 - Central | 763850 | G19-055-TAP | 230 | 7.5575 | 7.5603 | 0.0028
GEN-2020-056 | 03 - Central | 763857 | G19-054/068 | 230 | 7.2359 | 7.2435 | 0.0076
GEN-2020-056 | 03 - Central | 763862 | G19-054-TAP | 230 | 7.3196 | 7.3275 | 0.0079
GEN-2020-056 | 03 - Central | 765010 | GEN-2020-056 | 115 | 3.5818 | 3.6826 | 0.1008
GEN-2020-057 | 03 - Central | 300071 | 5CLINTN | 161 | 14.2359 | 14.2379 | 0.002
GEN-2020-057 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 16.1251 | 16.1277 | 0.0026
GEN-2020-057 | 03 - Central | 300740 | 7SPORTSMAN | 345 | 24.6203 | 24.6206 | 0.0003
GEN-2020-057 | 03 - Central | 300949 | 7JASPER | 345 | 13.0398 | 13.0411 | 0.0013
GEN-2020-057 | 03 - Central | 514825 | KAYWIND7 | 345 | 12.6283 | 12.6287 | 0.0004
GEN-2020-057 | 03 - Central | 515621 | OPENSKY7 | 345 | 12.6616 | 12.662 | 0.0004
GEN-2020-057 | 03 - Central | 532765 | HOYT 7 | 345 | 16.1737 | 16.1848 | 0.0111
GEN-2020-057 | 03 - Central | 532766 | JEC N 7 | 345 | 22.3193 | 22.3292 | 0.0099
GEN-2020-057 | 03 - Central | 532768 | EMPEC 7 | 345 | 16.8186 | 16.8308 | 0.0122
GEN-2020-057 | 03 - Central | 532769 | LANG 7 | 345 | 16.6332 | 16.6452 | 0.012
GEN-2020-057 | 03 - Central | 532770 | MORRIS 7 | 345 | 12.9038 | 12.9096 | 0.0058
GEN-2020-057 | 03 - Central | 532772 | STRANGR7 | 345 | 27.7004 | 27.7712 | 0.0708
GEN-2020-057 | 03 - Central | 532774 | SWISVAL7 | 345 | 17.5881 | 17.6348 | 0.0467
GEN-2020-057 | 03 - Central | 532775 | 87TH 7 | 345 | 21.3624 | 21.5435 | 0.1811
GEN-2020-057 | 03 - Central | 532776 | READWF 7 | 345 | 14.0593 | 14.0678 | 0.0085
GEN-2020-057 | 03 - Central | 532777 | G17-009-TAP | 345 | 12.0674 | 12.069 | 0.0016
GEN-2020-057 | 03 - Central | 532778 | GEN-2017-009 | 345 | 11.1514 | 11.1528 | 0.0014
GEN-2020-057 | 03 - Central | 532780 | CANEYRV7 | 345 | 9.9395 | 9.9404 | 0.0009
GEN-2020-057 | 03 - Central | 532781 | CANEYWF7 | 345 | 9.6585 | 9.6594 | 0.0009
GEN-2020-057 | 03 - Central | 532791 | BENTON 7 | 345 | 20.2588 | 20.2629 | 0.0041
GEN-2020-057 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18.5283 | 18.5326 | 0.0043
GEN-2020-057 | 03 - Central | 532794 | ROSEHIL7 | 345 | 19.6755 | 19.6793 | 0.0038
GEN-2020-057 | 03 - Central | 532796 | WICHITA7 | 345 | 24.5033 | 24.5073 | 0.004
GEN-2020-057 | 03 - Central | 532797 | WOLFCRK7 | 345 | 22.1049 | 22.1344 | 0.0295
GEN-2020-057 | 03 - Central | 532799 | WAVERLY7 | 345 | 18.5925 | 18.6143 | 0.0218
GEN-2020-057 | 03 - Central | 532800 | LATHAMS7 | 345 | 10.6008 | 10.6019 | 0.0011
GEN-2020-057 | 03 - Central | 532801 | ELKRVR17 | 345 | 9.3919 | 9.3928 | 0.0009
GEN-2020-057 | 03 - Central | 532802 | WAVERTX7 | 345 | 15.1742 | 15.1886 | 0.0144
GEN-2020-057 | 03 - Central | 532851 | AUBURN 6 | 230 | 13.7326 | 13.7402 | 0.0076
GEN-2020-057 | 03 - Central | 532852 | JEC 6 | 230 | 23.5345 | 23.5412 | 0.0067
GEN-2020-057 | 03 - Central | 532853 | LAWHILL6 | 230 | 14.1297 | 14.1387 | 0.009
GEN-2020-057 | 03 - Central | 532854 | LEC U5 6 | 230 | 13.9968 | 14.0056 | 0.0088
GEN-2020-057 | 03 - Central | 532855 | MIDLAND6 | 230 | 12.5404 | 12.5477 | 0.0073
GEN-2020-057 | 03 - Central | 532856 | SWISVAL6 | 230 | 22.5655 | 22.5998 | 0.0343
GEN-2020-057 | 03 - Central | 532857 | TECHILL6 | 230 | 11.1719 | 11.179 | 0.0071
GEN-2020-057 | 03 - Central | 532863 | MORRIS 6 | 230 | 14.2192 | 14.2239 | 0.0047
GEN-2020-057 | 03 - Central | 532914 | SPRGHL 5 | 161 | 11.2178 | 11.2279 | 0.0101
GEN-2020-057 | 03 - Central | 532937 | NEOSHO 5 | 161 | 23.9436 | 23.946 | 0.0024
GEN-2020-057 | 03 - Central | 532986 | BENTON 4 | 138 | 29.156 | 29.159 | 0.003
GEN-2020-057 | 03 - Central | 532991 | WEAVER 4 | 138 | 22.9662 | 22.9679 | 0.0017
GEN-2020-057 | 03 - Central | 533021 | NEOSHO 4 | 138 | 25.5583 | 25.5606 | 0.0023
GEN-2020-057 | 03 - Central | 533039 | ELPASO 4 | 138 | 25.8075 | 25.8094 | 0.0019
GEN-2020-057 | 03 - Central | 533062 | ROSEHIL4 | 138 | 32.2762 | 32.2797 | 0.0035
GEN-2020-057 | 03 - Central | 533068 | STEARMN4 | 138 | 20.197 | 20.1982 | 0.0012
GEN-2020-057 | 03 - Central | 533151 | AUBURN 3 | 115 | 21.8745 | 21.8836 | 0.0091
GEN-2020-057 | 03 - Central | 533155 | CROOKED3 | 115 | 20.6986 | 20.7068 | 0.0082
GEN-2020-057 | 03 - Central | 533163 | HOYT 3 | 115 | 23.3249 | 23.3333 | 0.0084
GEN-2020-057 | 03 - Central | 533182 | TECHILE3 | 115 | 25.3713 | 25.3855 | 0.0142
GEN-2020-057 | 03 - Central | 533211 | ARNOLD 3 | 115 | 8.4095 | 8.4114 | 0.0019
GEN-2020-057 | 03 - Central | 533236 | FAIRGDS3 | 115 | 19.008 | 19.0188 | 0.0108
GEN-2020-057 | 03 - Central | 533240 | EUDORA 3 | 115 | 11.9252 | 11.9314 | 0.0062
GEN-2020-057 | 03 - Central | 533244 | JARBALO3 | 115 | 27.2888 | 27.3139 | 0.0251
GEN-2020-057 | 03 - Central | 533250 | LWRNCHL3 | 115 | 27.1026 | 27.1212 | 0.0186
GEN-2020-057 | 03 - Central | 533254 | MOONLIT3 | 115 | 11.3481 | 11.3582 | 0.0101
GEN-2020-057 | 03 - Central | 533259 | NW LEAV3 | 115 | 17.597 | 17.6066 | 0.0096
GEN-2020-057 | 03 - Central | 533261 | PENTAGN3 | 115 | 22.5042 | 22.5342 | 0.03
GEN-2020-057 | 03 - Central | 533265 | SOUTHTN3 | 115 | 11.4218 | 11.4315 | 0.0097
GEN-2020-057 | 03 - Central | 533268 | STRANGR3 | 115 | 37.4933 | 37.5377 | 0.0444
GEN-2020-057 | 03 - Central | 533272 | THORNTN3 | 115 | 16.5245 | 16.5331 | 0.0086
GEN-2020-057 | 03 - Central | 533273 | TIMBRLN3 | 115 | 13.6599 | 13.6743 | 0.0144
GEN-2020-057 | 03 - Central | 533278 | WAVERLY3 | 115 | 14.8202 | 14.8381 | 0.0179
GEN-2020-057 | 03 - Central | 533281 | MNTCLLO3 | 115 | 23.5546 | 23.5949 | 0.0403
GEN-2020-057 | 03 - Central | 533283 | 87TH 3 | 115 | 27.7253 | 27.7887 | 0.0634
GEN-2020-057 | 03 - Central | 533304 | LANG 3 | 115 | 15.6887 | 15.6919 | 0.0032
GEN-2020-057 | 03 - Central | 533624 | BURLING2 | 69 | 3.5605 | 3.5606 | 0.0001
GEN-2020-057 | 03 - Central | 533625 | BURLIND2 | 69 | 3.1729 | 3.173 | 0.0001
GEN-2020-057 | 03 - Central | 533626 | BURLJCT2 | 69 | 5.1831 | 5.1833 | 0.0002
GEN-2020-057 | 03 - Central | 533628 | CC1BURL2 | 69 | 3.559 | 3.5591 | 0.0001
GEN-2020-057 | 03 - Central | 533629 | CC2SHAR2 | 69 | 4.8475 | 4.8477 | 0.0002
GEN-2020-057 | 03 - Central | 533630 | CC3WEST2 | 69 | 4.7834 | 4.7836 | 0.0002
GEN-2020-057 | 03 - Central | 533653 | WOLFCRK2 | 69 | 6.2777 | 6.2781 | 0.0004
GEN-2020-057 | 03 - Central | 541198 | PECULR 7 | 345 | 21.1661 | 21.2331 | 0.067
GEN-2020-057 | 03 - Central | 541200 | PHILL 7 | 345 | 19.1067 | 19.1445 | 0.0378
GEN-2020-057 | 03 - Central | 541201 | SIBLEY 7 | 345 | 21.4632 | 21.4854 | 0.0222
GEN-2020-057 | 03 - Central | 541207 | ARCHIE 5 | 161 | 16.7419 | 16.7507 | 0.0088
GEN-2020-057 | 03 - Central | 541225 | PHILL 5 | 161 | 34.1069 | 34.1347 | 0.0278
GEN-2020-057 | 03 - Central | 541340 | BELTONS5 | 161 | 19.7294 | 19.7506 | 0.0212
GEN-2020-057 | 03 - Central | 541341 | S.HARP 5 | 161 | 21.2553 | 21.2789 | 0.0236
GEN-2020-057 | 03 - Central | 541342 | PECULR 5 | 161 | 23.391 | 23.4216 | 0.0306
GEN-2020-057 | 03 - Central | 541343 | S.HARP 2 | 69 | 4.5831 | 4.5835 | 0.0004
GEN-2020-057 | 03 - Central | 541344 | PECULRS5 | 161 | 21.8639 | 21.89 | 0.0261
GEN-2020-057 | 03 - Central | 541350 | IATAN5 | 161 | 15.591 | 15.5969 | 0.0059
GEN-2020-057 | 03 - Central | 541400 | EASTOWN7 | 345 | 18.8754 | 18.8863 | 0.0109
GEN-2020-057 | 03 - Central | 541414 | SIB REA1 | 345 | 19.1323 | 19.15 | 0.0177
GEN-2020-057 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2.6784 | 2.6785 | 0.0001
GEN-2020-057 | 03 - Central | 542940 | ATLNTIC7 | 345 | 21.4884 | 22.188 | 0.6996
GEN-2020-057 | 03 - Central | 542945 | CRAIG_CAP 5 | 161 | 35.1527 | 35.3191 | 0.1664
GEN-2020-057 | 03 - Central | 542947 | MERRIAM_CAP5 | 161 | 27.4006 | 27.4602 | 0.0596
GEN-2020-057 | 03 - Central | 542950 | STHTOWN_CAP5 | 161 | 30.7827 | 30.8321 | 0.0494
GEN-2020-057 | 03 - Central | 542965 | W.GRDNR7 | 345 | 30.7161 | 31.1725 | 0.4564
GEN-2020-057 | 03 - Central | 542966 | WGARDNR5 | 161 | 30.7088 | 30.8153 | 0.1065
GEN-2020-057 | 03 - Central | 542968 | STILWEL7 | 345 | 26.6351 | 26.7794 | 0.1443
GEN-2020-057 | 03 - Central | 542969 | STILWEL5 | 161 | 41.5573 | 41.684 | 0.1267
GEN-2020-057 | 03 - Central | 542977 | CRAIG 7 | 345 | 22.528 | 22.7852 | 0.2572
GEN-2020-057 | 03 - Central | 542978 | CRAIG 5 | 161 | 44.1283 | 44.3908 | 0.2625
GEN-2020-057 | 03 - Central | 542979 | PFLUMM 5 | 161 | 30.118 | 30.2201 | 0.1021
GEN-2020-057 | 03 - Central | 542980 | NASHUA 7 | 345 | 23.8442 | 23.8689 | 0.0247
GEN-2020-057 | 03 - Central | 542981 | LACYGNE7 | 345 | 28.5275 | 28.609 | 0.0815
GEN-2020-057 | 03 - Central | 542982 | IATAN 7 | 345 | 30.8823 | 30.9318 | 0.0495
GEN-2020-057 | 03 - Central | 542993 | STHTOWN5 | 161 | 37.4571 | 37.5302 | 0.0731
GEN-2020-057 | 03 - Central | 542994 | HICKMAN5 | 161 | 20.1001 | 20.1235 | 0.0234
GEN-2020-057 | 03 - Central | 543002 | MARTCIT5 | 161 | 25.3939 | 25.4296 | 0.0357
GEN-2020-057 | 03 - Central | 543031 | SHWNMSN5 | 161 | 37.1222 | 37.2389 | 0.1167
GEN-2020-057 | 03 - Central | 543032 | MERRIAM5 | 161 | 32.5662 | 32.6504 | 0.0842
GEN-2020-057 | 03 - Central | 543033 | BRKRIDG5 | 161 | 24.6052 | 24.6639 | 0.0587
GEN-2020-057 | 03 - Central | 543034 | KNLWRTH5 | 161 | 27.5743 | 27.641 | 0.0667
GEN-2020-057 | 03 - Central | 543036 | OLATHE 5 | 161 | 27.6821 | 27.7658 | 0.0837
GEN-2020-057 | 03 - Central | 543037 | QUARRY 5 | 161 | 16.3439 | 16.373 | 0.0291
GEN-2020-057 | 03 - Central | 543038 | LENEXA 5 | 161 | 38.4601 | 38.639 | 0.1789
GEN-2020-057 | 03 - Central | 543041 | SHAWNEE5 | 161 | 27.8874 | 27.9438 | 0.0564
GEN-2020-057 | 03 - Central | 543043 | MURLEN 5 | 161 | 18.6569 | 18.6948 | 0.0379
GEN-2020-057 | 03 - Central | 543044 | MOONLT 5 | 161 | 18.0473 | 18.0827 | 0.0354
GEN-2020-057 | 03 - Central | 543045 | SWITZER5 | 161 | 19.9603 | 20.002 | 0.0417
GEN-2020-057 | 03 - Central | 543046 | OXFORD 5 | 161 | 21.4868 | 21.5315 | 0.0447
GEN-2020-057 | 03 - Central | 543047 | OVERLPK5 | 161 | 32.856 | 32.9586 | 0.1026
GEN-2020-057 | 03 - Central | 543048 | COLLEGE5 | 161 | 30.7997 | 30.9182 | 0.1185
GEN-2020-057 | 03 - Central | 543049 | CEDRCRK5 | 161 | 31.2334 | 31.3524 | 0.119
GEN-2020-057 | 03 - Central | 543050 | ANTIOCH5 | 161 | 23.4647 | 23.5112 | 0.0465
GEN-2020-057 | 03 - Central | 543052 | REEDER 5 | 161 | 21.5606 | 21.6073 | 0.0467
GEN-2020-057 | 03 - Central | 543053 | REDEL 5 | 161 | 25.2992 | 25.3399 | 0.0407
GEN-2020-057 | 03 - Central | 543054 | CEDARNL5 | 161 | 10.9277 | 10.9412 | 0.0135
GEN-2020-057 | 03 - Central | 543055 | SEOTTWA5 | 161 | 8.2429 | 8.2466 | 0.0037
GEN-2020-057 | 03 - Central | 543056 | GARDNER5 | 161 | 16.7887 | 16.8192 | 0.0305
GEN-2020-057 | 03 - Central | 543057 | BUCYRUS5 | 161 | 21.1933 | 21.2232 | 0.0299
GEN-2020-057 | 03 - Central | 543058 | NLOUISB5 | 161 | 9.3635 | 9.3694 | 0.0059
GEN-2020-057 | 03 - Central | 543068 | WAGSTAF5 | 161 | 14.582 | 14.5945 | 0.0125
GEN-2020-057 | 03 - Central | 543077 | PLSTVAL5 | 161 | 10.6874 | 10.6971 | 0.0097
GEN-2020-057 | 03 - Central | 543105 | BULLCRK5 | 161 | 29.6902 | 29.7878 | 0.0976
GEN-2020-057 | 03 - Central | 543126 | LACKMAN5 | 161 | 13.9278 | 13.9429 | 0.0151
GEN-2020-057 | 03 - Central | 543132 | BNSF 5 | 161 | 22.4965 | 22.5528 | 0.0563
GEN-2020-057 | 03 - Central | 543166 | NEASTOTTW5 | 161 | 7.0194 | 7.0221 | 0.0027
GEN-2020-057 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27.7533 | 27.8304 | 0.0771
GEN-2020-057 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27.7533 | 27.8304 | 0.0771
GEN-2020-057 | 03 - Central | 543659 | LACYGNE2 | 69 | 2.8175 | 2.8177 | 0.0002
GEN-2020-057 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 0.6738 | 0.6739 | 0.0001
GEN-2020-057 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 0.6454 | 0.6454 | 0
GEN-2020-057 | 03 - Central | 546742 | METRO 5 | 161 | 27.4301 | 27.4746 | 0.0445
GEN-2020-057 | 03 - Central | 560053 | G15-052T | 345 | 13.4629 | 13.4639 | 0.001
GEN-2020-057 | 03 - Central | 562476 | G14-001-TAP | 345 | 10.8398 | 10.8417 | 0.0019
GEN-2020-057 | 03 - Central | 583850 | GEN-2014-001 | 345 | 7.3065 | 7.3073 | 0.0008
GEN-2020-057 | 03 - Central | 584900 | GEN-2015-052 | 345 | 13.4129 | 13.4138 | 0.0009
GEN-2020-057 | 03 - Central | 588240 | GEN-2016-149 | 345 | 9.0674 | 9.0727 | 0.0053
GEN-2020-057 | 03 - Central | 588250 | GEN-2016-174 | 345 | 5.9113 | 5.9129 | 0.0016
GEN-2020-057 | 03 - Central | 588260 | GEN-2016-176 | 345 | 4.7936 | 4.7946 | 0.001
GEN-2020-057 | 03 - Central | 588270 | GEN-2016-150 | 345 | 3.5667 | 3.5671 | 0.0004
GEN-2020-057 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.6411 | 19.6744 | 0.0333
GEN-2020-057 | 03 - Central | 760921 | G17-209-TAP | 345 | 20.1642 | 20.1994 | 0.0352
GEN-2020-057 | 03 - Central | 761271 | GEN-2017-108 | 161 | 7.5433 | 7.5441 | 0.0008
GEN-2020-057 | 03 - Central | 761278 | G17-108-TAP | 161 | 12.4179 | 12.4206 | 0.0027
GEN-2020-057 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5.3892 | 5.3931 | 0.0039
GEN-2020-057 | 03 - Central | 762279 | GEN-2017-195 | 345 | 30.6263 | 31.08 | 0.4537
GEN-2020-057 | 03 - Central | 762300 | GEN-2017-196 | 345 | 30.5315 | 30.9823 | 0.4508
GEN-2020-057 | 03 - Central | 762405 | ASG-2018-010 | 161 | 3.3617 | 3.3626 | 0.0009
GEN-2020-057 | 03 - Central | 762680 | GEN-2018-032 | 345 | 12.1407 | 12.1425 | 0.0018
GEN-2020-057 | 03 - Central | 764375 | GEN-2020-058 | 345 | 21.4461 | 22.1428 | 0.6967
GEN-2020-057 | 03 - Central | 764390 | GEN-2020-073 | 161 | 8.3888 | 8.3928 | 0.004
GEN-2020-057 | 03 - Central | 764400 | G20-073-TAP | 161 | 8.4697 | 8.4738 | 0.0041
GEN-2020-057 | 03 - Central | 765100 | GEN-2020-052 | 345 | 9.9271 | 9.928 | 0.0009
GEN-2020-057 | 03 - Central | 765110 | G20-052-TAP | 345 | 13.1171 | 13.1185 | 0.0014
GEN-2020-057 | 03 - Central | 765115 | GEN-2020-057 | 345 | 21.4433 | 22.1429 | 0.6996
GEN-2020-057 | 03 - Central | 765130 | GEN-2020-071 | 230 | 11.3727 | 11.3791 | 0.0064
GEN-2020-057 | 03 - Central | 765140 | G20-071-TAP | 230 | 11.3727 | 11.3791 | 0.0064
GEN-2020-057 | 03 - Central | 765145 | GEN-2020-076 | 345 | 12.5493 | 12.5518 | 0.0025
GEN-2020-057 | 03 - Central | 765155 | G20-076-TAP | 345 | 12.557 | 12.5595 | 0.0025
GEN-2020-057 | 03 - Central | 765160 | GEN-2020-086 | 345 | 12.5499 | 12.5524 | 0.0025
GEN-2020-057 | 03 - Central | 765190 | GEN-2020-090 | 345 | 8.7244 | 8.7262 | 0.0018
GEN-2020-057 | 03 - Central | 765200 | G20-090-TAP | 345 | 9.9508 | 9.9531 | 0.0023
GEN-2020-057 | 03 - Central | 766260 | GEN-2020-007 | 345 | 25.0939 | 25.1555 | 0.0616
GEN-2020-057 | 03 - Central | 766261 | G20-007-TAP | 345 | 27.6939 | 27.7699 | 0.076
GEN-2020-058 | 03 - Central | 300071 | 5CLINTN | 161 | 14.236 | 14.2379 | 0.0019
GEN-2020-058 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 16.1252 | 16.1277 | 0.0025
GEN-2020-058 | 03 - Central | 300740 | 7SPORTSMAN | 345 | 24.6203 | 24.6206 | 0.0003
GEN-2020-058 | 03 - Central | 300949 | 7JASPER | 345 | 13.0398 | 13.0411 | 0.0013
GEN-2020-058 | 03 - Central | 514825 | KAYWIND7 | 345 | 12.6283 | 12.6287 | 0.0004
GEN-2020-058 | 03 - Central | 515621 | OPENSKY7 | 345 | 12.6616 | 12.662 | 0.0004
GEN-2020-058 | 03 - Central | 532765 | HOYT 7 | 345 | 16.1742 | 16.1848 | 0.0106
GEN-2020-058 | 03 - Central | 532766 | JEC N 7 | 345 | 22.3198 | 22.3292 | 0.0094
GEN-2020-058 | 03 - Central | 532768 | EMPEC 7 | 345 | 16.8191 | 16.8308 | 0.0117
GEN-2020-058 | 03 - Central | 532769 | LANG 7 | 345 | 16.6337 | 16.6452 | 0.0115
GEN-2020-058 | 03 - Central | 532770 | MORRIS 7 | 345 | 12.9041 | 12.9096 | 0.0055
GEN-2020-058 | 03 - Central | 532772 | STRANGR7 | 345 | 27.7034 | 27.7712 | 0.0678
GEN-2020-058 | 03 - Central | 532774 | SWISVAL7 | 345 | 17.5901 | 17.6348 | 0.0447
GEN-2020-058 | 03 - Central | 532775 | 87TH 7 | 345 | 21.37 | 21.5435 | 0.1735
GEN-2020-058 | 03 - Central | 532776 | READWF 7 | 345 | 14.0597 | 14.0678 | 0.0081
GEN-2020-058 | 03 - Central | 532777 | G17-009-TAP | 345 | 12.0674 | 12.069 | 0.0016
GEN-2020-058 | 03 - Central | 532778 | GEN-2017-009 | 345 | 11.1515 | 11.1528 | 0.0013
GEN-2020-058 | 03 - Central | 532780 | CANEYRV7 | 345 | 9.9395 | 9.9404 | 0.0009
GEN-2020-058 | 03 - Central | 532781 | CANEYWF7 | 345 | 9.6585 | 9.6594 | 0.0009
GEN-2020-058 | 03 - Central | 532791 | BENTON 7 | 345 | 20.259 | 20.2629 | 0.0039
GEN-2020-058 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18.5285 | 18.5326 | 0.0041
GEN-2020-058 | 03 - Central | 532794 | ROSEHIL7 | 345 | 19.6756 | 19.6793 | 0.0037
GEN-2020-058 | 03 - Central | 532796 | WICHITA7 | 345 | 24.5035 | 24.5073 | 0.0038
GEN-2020-058 | 03 - Central | 532797 | WOLFCRK7 | 345 | 22.1061 | 22.1344 | 0.0283
GEN-2020-058 | 03 - Central | 532799 | WAVERLY7 | 345 | 18.5934 | 18.6143 | 0.0209
GEN-2020-058 | 03 - Central | 532800 | LATHAMS7 | 345 | 10.6008 | 10.6019 | 0.0011
GEN-2020-058 | 03 - Central | 532801 | ELKRVR17 | 345 | 9.392 | 9.3928 | 0.0008
GEN-2020-058 | 03 - Central | 532802 | WAVERTX7 | 345 | 15.1748 | 15.1886 | 0.0138
GEN-2020-058 | 03 - Central | 532851 | AUBURN 6 | 230 | 13.7329 | 13.7402 | 0.0073
GEN-2020-058 | 03 - Central | 532852 | JEC 6 | 230 | 23.5348 | 23.5412 | 0.0064
GEN-2020-058 | 03 - Central | 532853 | LAWHILL6 | 230 | 14.1301 | 14.1387 | 0.0086
GEN-2020-058 | 03 - Central | 532854 | LEC U5 6 | 230 | 13.9972 | 14.0056 | 0.0084
GEN-2020-058 | 03 - Central | 532855 | MIDLAND6 | 230 | 12.5407 | 12.5477 | 0.007
GEN-2020-058 | 03 - Central | 532856 | SWISVAL6 | 230 | 22.5669 | 22.5998 | 0.0329
GEN-2020-058 | 03 - Central | 532857 | TECHILL6 | 230 | 11.1722 | 11.179 | 0.0068
GEN-2020-058 | 03 - Central | 532863 | MORRIS 6 | 230 | 14.2194 | 14.2239 | 0.0045
GEN-2020-058 | 03 - Central | 532914 | SPRGHL 5 | 161 | 11.2182 | 11.2279 | 0.0097
GEN-2020-058 | 03 - Central | 532937 | NEOSHO 5 | 161 | 23.9437 | 23.946 | 0.0023
GEN-2020-058 | 03 - Central | 532986 | BENTON 4 | 138 | 29.1562 | 29.159 | 0.0028
GEN-2020-058 | 03 - Central | 532991 | WEAVER 4 | 138 | 22.9662 | 22.9679 | 0.0017
GEN-2020-058 | 03 - Central | 533021 | NEOSHO 4 | 138 | 25.5584 | 25.5606 | 0.0022
GEN-2020-058 | 03 - Central | 533039 | ELPASO 4 | 138 | 25.8076 | 25.8094 | 0.0018
GEN-2020-058 | 03 - Central | 533062 | ROSEHIL4 | 138 | 32.2763 | 32.2797 | 0.0034
GEN-2020-058 | 03 - Central | 533068 | STEARMN4 | 138 | 20.1971 | 20.1982 | 0.0011
GEN-2020-058 | 03 - Central | 533151 | AUBURN 3 | 115 | 21.8749 | 21.8836 | 0.0087
GEN-2020-058 | 03 - Central | 533155 | CROOKED3 | 115 | 20.699 | 20.7068 | 0.0078
GEN-2020-058 | 03 - Central | 533163 | HOYT 3 | 115 | 23.3252 | 23.3333 | 0.0081
GEN-2020-058 | 03 - Central | 533182 | TECHILE3 | 115 | 25.3719 | 25.3855 | 0.0136
GEN-2020-058 | 03 - Central | 533211 | ARNOLD 3 | 115 | 8.4096 | 8.4114 | 0.0018
GEN-2020-058 | 03 - Central | 533236 | FAIRGDS3 | 115 | 19.0085 | 19.0188 | 0.0103
GEN-2020-058 | 03 - Central | 533240 | EUDORA 3 | 115 | 11.9255 | 11.9314 | 0.0059
GEN-2020-058 | 03 - Central | 533244 | JARBALO3 | 115 | 27.2898 | 27.3139 | 0.0241
GEN-2020-058 | 03 - Central | 533250 | LWRNCHL3 | 115 | 27.1034 | 27.1212 | 0.0178
GEN-2020-058 | 03 - Central | 533254 | MOONLIT3 | 115 | 11.3485 | 11.3582 | 0.0097
GEN-2020-058 | 03 - Central | 533259 | NW LEAV3 | 115 | 17.5974 | 17.6066 | 0.0092
GEN-2020-058 | 03 - Central | 533261 | PENTAGN3 | 115 | 22.5055 | 22.5342 | 0.0287
GEN-2020-058 | 03 - Central | 533265 | SOUTHTN3 | 115 | 11.4223 | 11.4315 | 0.0092
GEN-2020-058 | 03 - Central | 533268 | STRANGR3 | 115 | 37.4952 | 37.5377 | 0.0425
GEN-2020-058 | 03 - Central | 533272 | THORNTN3 | 115 | 16.5248 | 16.5331 | 0.0083
GEN-2020-058 | 03 - Central | 533273 | TIMBRLN3 | 115 | 13.6605 | 13.6743 | 0.0138
GEN-2020-058 | 03 - Central | 533278 | WAVERLY3 | 115 | 14.821 | 14.8381 | 0.0171
GEN-2020-058 | 03 - Central | 533281 | MNTCLLO3 | 115 | 23.5562 | 23.5949 | 0.0387
GEN-2020-058 | 03 - Central | 533283 | 87TH 3 | 115 | 27.728 | 27.7887 | 0.0607
GEN-2020-058 | 03 - Central | 533304 | LANG 3 | 115 | 15.6888 | 15.6919 | 0.0031
GEN-2020-058 | 03 - Central | 533624 | BURLING2 | 69 | 3.5605 | 3.5606 | 0.0001
GEN-2020-058 | 03 - Central | 533625 | BURLIND2 | 69 | 3.1729 | 3.173 | 0.0001
GEN-2020-058 | 03 - Central | 533626 | BURLJCT2 | 69 | 5.1832 | 5.1833 | 0.0001
GEN-2020-058 | 03 - Central | 533628 | CC1BURL2 | 69 | 3.559 | 3.5591 | 0.0001
GEN-2020-058 | 03 - Central | 533629 | CC2SHAR2 | 69 | 4.8476 | 4.8477 | 0.0001
GEN-2020-058 | 03 - Central | 533630 | CC3WEST2 | 69 | 4.7835 | 4.7836 | 0.0001
GEN-2020-058 | 03 - Central | 533653 | WOLFCRK2 | 69 | 6.2778 | 6.2781 | 0.0003
GEN-2020-058 | 03 - Central | 541198 | PECULR 7 | 345 | 21.169 | 21.2331 | 0.0641
GEN-2020-058 | 03 - Central | 541200 | PHILL 7 | 345 | 19.1083 | 19.1445 | 0.0362
GEN-2020-058 | 03 - Central | 541201 | SIBLEY 7 | 345 | 21.4641 | 21.4854 | 0.0213
GEN-2020-058 | 03 - Central | 541207 | ARCHIE 5 | 161 | 16.7423 | 16.7507 | 0.0084
GEN-2020-058 | 03 - Central | 541225 | PHILL 5 | 161 | 34.1081 | 34.1347 | 0.0266
GEN-2020-058 | 03 - Central | 541340 | BELTONS5 | 161 | 19.7303 | 19.7506 | 0.0203
GEN-2020-058 | 03 - Central | 541341 | S.HARP 5 | 161 | 21.2563 | 21.2789 | 0.0226
GEN-2020-058 | 03 - Central | 541342 | PECULR 5 | 161 | 23.3923 | 23.4216 | 0.0293
GEN-2020-058 | 03 - Central | 541343 | S.HARP 2 | 69 | 4.5831 | 4.5835 | 0.0004
GEN-2020-058 | 03 - Central | 541344 | PECULRS5 | 161 | 21.865 | 21.89 | 0.025
GEN-2020-058 | 03 - Central | 541350 | IATAN5 | 161 | 15.5913 | 15.5969 | 0.0056
GEN-2020-058 | 03 - Central | 541400 | EASTOWN7 | 345 | 18.8759 | 18.8863 | 0.0104
GEN-2020-058 | 03 - Central | 541414 | SIB REA1 | 345 | 19.1331 | 19.15 | 0.0169
GEN-2020-058 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2.6784 | 2.6785 | 0.0001
GEN-2020-058 | 03 - Central | 542940 | ATLNTIC7 | 345 | 21.5169 | 22.188 | 0.6711
GEN-2020-058 | 03 - Central | 542945 | CRAIG_CAP 5 | 161 | 35.1596 | 35.3191 | 0.1595
GEN-2020-058 | 03 - Central | 542947 | MERRIAM_CAP5 | 161 | 27.4031 | 27.4602 | 0.0571
GEN-2020-058 | 03 - Central | 542950 | STHTOWN_CAP5 | 161 | 30.7848 | 30.8321 | 0.0473
GEN-2020-058 | 03 - Central | 542965 | W.GRDNR7 | 345 | 30.735 | 31.1725 | 0.4375
GEN-2020-058 | 03 - Central | 542966 | WGARDNR5 | 161 | 30.7132 | 30.8153 | 0.1021
GEN-2020-058 | 03 - Central | 542968 | STILWEL7 | 345 | 26.6412 | 26.7794 | 0.1382
GEN-2020-058 | 03 - Central | 542969 | STILWEL5 | 161 | 41.5626 | 41.684 | 0.1214
GEN-2020-058 | 03 - Central | 542977 | CRAIG 7 | 345 | 22.5387 | 22.7852 | 0.2465
GEN-2020-058 | 03 - Central | 542978 | CRAIG 5 | 161 | 44.1393 | 44.3908 | 0.2515
GEN-2020-058 | 03 - Central | 542979 | PFLUMM 5 | 161 | 30.1222 | 30.2201 | 0.0979
GEN-2020-058 | 03 - Central | 542980 | NASHUA 7 | 345 | 23.8453 | 23.8689 | 0.0236
GEN-2020-058 | 03 - Central | 542981 | LACYGNE7 | 345 | 28.5309 | 28.609 | 0.0781
GEN-2020-058 | 03 - Central | 542982 | IATAN 7 | 345 | 30.8844 | 30.9318 | 0.0474
GEN-2020-058 | 03 - Central | 542993 | STHTOWN5 | 161 | 37.4602 | 37.5302 | 0.07
GEN-2020-058 | 03 - Central | 542994 | HICKMAN5 | 161 | 20.1011 | 20.1235 | 0.0224
GEN-2020-058 | 03 - Central | 543002 | MARTCIT5 | 161 | 25.3954 | 25.4296 | 0.0342
GEN-2020-058 | 03 - Central | 543031 | SHWNMSN5 | 161 | 37.1272 | 37.2389 | 0.1117
GEN-2020-058 | 03 - Central | 543032 | MERRIAM5 | 161 | 32.5697 | 32.6504 | 0.0807
GEN-2020-058 | 03 - Central | 543033 | BRKRIDG5 | 161 | 24.6076 | 24.6639 | 0.0563
GEN-2020-058 | 03 - Central | 543034 | KNLWRTH5 | 161 | 27.5772 | 27.641 | 0.0638
GEN-2020-058 | 03 - Central | 543036 | OLATHE 5 | 161 | 27.6856 | 27.7658 | 0.0802
GEN-2020-058 | 03 - Central | 543037 | QUARRY 5 | 161 | 16.3451 | 16.373 | 0.0279
GEN-2020-058 | 03 - Central | 543038 | LENEXA 5 | 161 | 38.4675 | 38.639 | 0.1715
GEN-2020-058 | 03 - Central | 543041 | SHAWNEE5 | 161 | 27.8897 | 27.9438 | 0.0541
GEN-2020-058 | 03 - Central | 543043 | MURLEN 5 | 161 | 18.6585 | 18.6948 | 0.0363
GEN-2020-058 | 03 - Central | 543044 | MOONLT 5 | 161 | 18.0488 | 18.0827 | 0.0339
GEN-2020-058 | 03 - Central | 543045 | SWITZER5 | 161 | 19.9621 | 20.002 | 0.0399
GEN-2020-058 | 03 - Central | 543046 | OXFORD 5 | 161 | 21.4887 | 21.5315 | 0.0428
GEN-2020-058 | 03 - Central | 543047 | OVERLPK5 | 161 | 32.8603 | 32.9586 | 0.0983
GEN-2020-058 | 03 - Central | 543048 | COLLEGE5 | 161 | 30.8047 | 30.9182 | 0.1135
GEN-2020-058 | 03 - Central | 543049 | CEDRCRK5 | 161 | 31.2383 | 31.3524 | 0.1141
GEN-2020-058 | 03 - Central | 543050 | ANTIOCH5 | 161 | 23.4667 | 23.5112 | 0.0445
GEN-2020-058 | 03 - Central | 543052 | REEDER 5 | 161 | 21.5625 | 21.6073 | 0.0448
GEN-2020-058 | 03 - Central | 543053 | REDEL 5 | 161 | 25.301 | 25.3399 | 0.0389
GEN-2020-058 | 03 - Central | 543054 | CEDARNL5 | 161 | 10.9283 | 10.9412 | 0.0129
GEN-2020-058 | 03 - Central | 543055 | SEOTTWA5 | 161 | 8.243 | 8.2466 | 0.0036
GEN-2020-058 | 03 - Central | 543056 | GARDNER5 | 161 | 16.79 | 16.8192 | 0.0292
GEN-2020-058 | 03 - Central | 543057 | BUCYRUS5 | 161 | 21.1946 | 21.2232 | 0.0286
GEN-2020-058 | 03 - Central | 543058 | NLOUISB5 | 161 | 9.3638 | 9.3694 | 0.0056
GEN-2020-058 | 03 - Central | 543068 | WAGSTAF5 | 161 | 14.5825 | 14.5945 | 0.012
GEN-2020-058 | 03 - Central | 543077 | PLSTVAL5 | 161 | 10.6878 | 10.6971 | 0.0093
GEN-2020-058 | 03 - Central | 543105 | BULLCRK5 | 161 | 29.6943 | 29.7878 | 0.0935
GEN-2020-058 | 03 - Central | 543126 | LACKMAN5 | 161 | 13.9284 | 13.9429 | 0.0145
GEN-2020-058 | 03 - Central | 543132 | BNSF 5 | 161 | 22.4989 | 22.5528 | 0.0539
GEN-2020-058 | 03 - Central | 543166 | NEASTOTTW5 | 161 | 7.0195 | 7.0221 | 0.0026
GEN-2020-058 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27.7566 | 27.8304 | 0.0738
GEN-2020-058 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27.7566 | 27.8304 | 0.0738
GEN-2020-058 | 03 - Central | 543659 | LACYGNE2 | 69 | 2.8176 | 2.8177 | 0.0001
GEN-2020-058 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 0.6738 | 0.6739 | 0.0001
GEN-2020-058 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 0.6454 | 0.6454 | 0
GEN-2020-058 | 03 - Central | 546742 | METRO 5 | 161 | 27.432 | 27.4746 | 0.0426
GEN-2020-058 | 03 - Central | 560053 | G15-052T | 345 | 13.463 | 13.4639 | 0.0009
GEN-2020-058 | 03 - Central | 562476 | G14-001-TAP | 345 | 10.8398 | 10.8417 | 0.0019
GEN-2020-058 | 03 - Central | 583850 | GEN-2014-001 | 345 | 7.3065 | 7.3073 | 0.0008
GEN-2020-058 | 03 - Central | 584900 | GEN-2015-052 | 345 | 13.4129 | 13.4138 | 0.0009
GEN-2020-058 | 03 - Central | 588240 | GEN-2016-149 | 345 | 9.0677 | 9.0727 | 0.005
GEN-2020-058 | 03 - Central | 588250 | GEN-2016-174 | 345 | 5.9113 | 5.9129 | 0.0016
GEN-2020-058 | 03 - Central | 588260 | GEN-2016-176 | 345 | 4.7936 | 4.7946 | 0.001
GEN-2020-058 | 03 - Central | 588270 | GEN-2016-150 | 345 | 3.5667 | 3.5671 | 0.0004
GEN-2020-058 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.6425 | 19.6744 | 0.0319
GEN-2020-058 | 03 - Central | 760921 | G17-209-TAP | 345 | 20.1657 | 20.1994 | 0.0337
GEN-2020-058 | 03 - Central | 761271 | GEN-2017-108 | 161 | 7.5433 | 7.5441 | 0.0008
GEN-2020-058 | 03 - Central | 761278 | G17-108-TAP | 161 | 12.418 | 12.4206 | 0.0026
GEN-2020-058 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5.3894 | 5.3931 | 0.0037
GEN-2020-058 | 03 - Central | 762279 | GEN-2017-195 | 345 | 30.6451 | 31.08 | 0.4349
GEN-2020-058 | 03 - Central | 762300 | GEN-2017-196 | 345 | 30.5502 | 30.9823 | 0.4321
GEN-2020-058 | 03 - Central | 762405 | ASG-2018-010 | 161 | 3.3618 | 3.3626 | 0.0008
GEN-2020-058 | 03 - Central | 762680 | GEN-2018-032 | 345 | 12.1407 | 12.1425 | 0.0018
GEN-2020-058 | 03 - Central | 764375 | GEN-2020-058 | 345 | 21.4717 | 22.1428 | 0.6711
GEN-2020-058 | 03 - Central | 764390 | GEN-2020-073 | 161 | 8.389 | 8.3928 | 0.0038
GEN-2020-058 | 03 - Central | 764400 | G20-073-TAP | 161 | 8.4699 | 8.4738 | 0.0039
GEN-2020-058 | 03 - Central | 765100 | GEN-2020-052 | 345 | 9.9272 | 9.928 | 0.0008
GEN-2020-058 | 03 - Central | 765110 | G20-052-TAP | 345 | 13.1171 | 13.1185 | 0.0014
GEN-2020-058 | 03 - Central | 765115 | GEN-2020-057 | 345 | 21.4746 | 22.1429 | 0.6683
GEN-2020-058 | 03 - Central | 765130 | GEN-2020-071 | 230 | 11.373 | 11.3791 | 0.0061
GEN-2020-058 | 03 - Central | 765140 | G20-071-TAP | 230 | 11.373 | 11.3791 | 0.0061
GEN-2020-058 | 03 - Central | 765145 | GEN-2020-076 | 345 | 12.5494 | 12.5518 | 0.0024
GEN-2020-058 | 03 - Central | 765155 | G20-076-TAP | 345 | 12.5571 | 12.5595 | 0.0024
GEN-2020-058 | 03 - Central | 765160 | GEN-2020-086 | 345 | 12.5501 | 12.5524 | 0.0023
GEN-2020-058 | 03 - Central | 765190 | GEN-2020-090 | 345 | 8.7245 | 8.7262 | 0.0017
GEN-2020-058 | 03 - Central | 765200 | G20-090-TAP | 345 | 9.9509 | 9.9531 | 0.0022
GEN-2020-058 | 03 - Central | 766260 | GEN-2020-007 | 345 | 25.0965 | 25.1555 | 0.059
GEN-2020-058 | 03 - Central | 766261 | G20-007-TAP | 345 | 27.6971 | 27.7699 | 0.0728
GEN-2020-061 | 03 - Central | 41453 | J1145 SUB | 345 | 17.8631 | 17.877 | 0.0139
GEN-2020-061 | 03 - Central | 44888 | J1490_POI | 345 | 17.8631 | 17.877 | 0.0139
GEN-2020-061 | 03 - Central | 300043 | 7KINGDM | 345 | 15.2438 | 15.2563 | 0.0125
GEN-2020-061 | 03 - Central | 300044 | 7MCCRED | 345 | 17.7724 | 17.7897 | 0.0173
GEN-2020-061 | 03 - Central | 300049 | 7THOMHL | 345 | 14.919 | 14.9246 | 0.0056
GEN-2020-061 | 03 - Central | 300071 | 5CLINTN | 161 | 14.1507 | 14.2379 | 0.0872
GEN-2020-061 | 03 - Central | 300124 | 5HOLDENB2 | 161 | 7.8576 | 7.8805 | 0.0229
GEN-2020-061 | 03 - Central | 300500 | 5HUNTSDL | 161 | 10.8046 | 10.8104 | 0.0058
GEN-2020-061 | 03 - Central | 300688 | 2AUSTIN | 69 | 4.3486 | 4.3659 | 0.0173
GEN-2020-061 | 03 - Central | 300689 | 2BUTLER | 69 | 6.0244 | 6.0439 | 0.0195
GEN-2020-061 | 03 - Central | 300692 | 2CLINTN | 69 | 14.0615 | 14.1001 | 0.0386
GEN-2020-061 | 03 - Central | 300698 | 2ELYNNE | 69 | 3.3123 | 3.3263 | 0.014
GEN-2020-061 | 03 - Central | 300699 | 2ELYNTP | 69 | 6.1148 | 6.1605 | 0.0457
GEN-2020-061 | 03 - Central | 300705 | 2PECULR | 69 | 3.3601 | 3.3715 | 0.0114
GEN-2020-061 | 03 - Central | 300709 | 2SHARSNV | 69 | 6.4057 | 6.4581 | 0.0524
GEN-2020-061 | 03 - Central | 301342 | 5BUTLER | 161 | 6.8424 | 6.9146 | 0.0722
GEN-2020-061 | 03 - Central | 301477 | 5OSCEOKCTP | 161 | 6.6903 | 6.7007 | 0.0104
GEN-2020-061 | 03 - Central | 301503 | 7THOMHLGSU3 | 345 | 14.81 | 14.8155 | 0.0055
GEN-2020-061 | 03 - Central | 301515 | 5SHARSNV | 161 | 14.632 | 15.5814 | 0.9494
GEN-2020-061 | 03 - Central | 301522 | 5OSCEOKC | 161 | 6.6828 | 6.6932 | 0.0104
GEN-2020-061 | 03 - Central | 345221 | 5MOBERLY | 161 | 15.8942 | 15.901 | 0.0068
GEN-2020-061 | 03 - Central | 345408 | 7OVERTON | 345 | 12.9618 | 12.9884 | 0.0266
GEN-2020-061 | 03 - Central | 345409 | 5OVERTON | 161 | 21.3207 | 21.347 | 0.0263
GEN-2020-061 | 03 - Central | 345411 | 5OVERTON 2 | 161 | 21.3207 | 21.347 | 0.0263
GEN-2020-061 | 03 - Central | 346117 | 2OVERTON | 69 | 3.6867 | 3.6871 | 0.0004
GEN-2020-061 | 03 - Central | 505502 | TRUMAN 5 | 161 | 7.57 | 7.5785 | 0.0085
GEN-2020-061 | 03 - Central | 532774 | SWISVAL7 | 345 | 17.589 | 17.6348 | 0.0458
GEN-2020-061 | 03 - Central | 532797 | WOLFCRK7 | 345 | 22.0916 | 22.1344 | 0.0428
GEN-2020-061 | 03 - Central | 541149 | WSTELEC_CAP5 | 161 | 14.4535 | 15.5665 | 1.113
GEN-2020-061 | 03 - Central | 541197 | MULLNCR7 | 345 | 8.5968 | 8.6111 | 0.0143
GEN-2020-061 | 03 - Central | 541198 | PECULR 7 | 345 | 20.2906 | 21.2331 | 0.9425
GEN-2020-061 | 03 - Central | 541200 | PHILL 7 | 345 | 17.96 | 19.1445 | 1.1845
GEN-2020-061 | 03 - Central | 541201 | SIBLEY 7 | 345 | 20.9383 | 21.4854 | 0.5471
GEN-2020-061 | 03 - Central | 541202 | SIBLEY 5 | 161 | 26.9592 | 27.5039 | 0.5447
GEN-2020-061 | 03 - Central | 541206 | PRALEE 5 | 161 | 19.1776 | 20.8981 | 1.7205
GEN-2020-061 | 03 - Central | 541207 | ARCHIE 5 | 161 | 16.0232 | 16.7507 | 0.7275
GEN-2020-061 | 03 - Central | 541208 | NEVADA 5 | 161 | 6.2399 | 6.2615 | 0.0216
GEN-2020-061 | 03 - Central | 541210 | MARTCTY5 | 161 | 27.2362 | 28.4383 | 1.2021
GEN-2020-061 | 03 - Central | 541211 | BLSPS 5 | 161 | 18.9246 | 20.0711 | 1.1465
GEN-2020-061 | 03 - Central | 541215 | HLLMRK 5 | 161 | 14.1262 | 14.2066 | 0.0804
GEN-2020-061 | 03 - Central | 541217 | WINDSR 5 | 161 | 8.5863 | 8.6111 | 0.0248
GEN-2020-061 | 03 - Central | 541218 | GRNWD 5 | 161 | 20.8168 | 24.3758 | 3.559
GEN-2020-061 | 03 - Central | 541222 | WSTELEC5 | 161 | 15.7731 | 17.108 | 1.3349
GEN-2020-061 | 03 - Central | 541223 | GRDVWE 5 | 161 | 19.3655 | 20.5284 | 1.1629
GEN-2020-061 | 03 - Central | 541224 | LNGVW 5 | 161 | 20.6337 | 23.0685 | 2.4348
GEN-2020-061 | 03 - Central | 541225 | PHILL 5 | 161 | 25.3526 | 34.1347 | 8.7821
GEN-2020-061 | 03 - Central | 541231 | NRAYMORETP 5 | 161 | 5.8716 | 5.9551 | 0.0835
GEN-2020-061 | 03 - Central | 541233 | LEESUM 5 | 161 | 18.5456 | 20.6017 | 2.0561
GEN-2020-061 | 03 - Central | 541235 | DUNCAN 5 | 161 | 19.2157 | 19.8889 | 0.6732
GEN-2020-061 | 03 - Central | 541239 | HSNVL 5 | 161 | 14.7597 | 15.7268 | 0.9671
GEN-2020-061 | 03 - Central | 541240 | ADRIAN 5 | 161 | 8.3843 | 8.5297 | 0.1454
GEN-2020-061 | 03 - Central | 541242 | CLINTON5 | 161 | 14.0951 | 14.1815 | 0.0864
GEN-2020-061 | 03 - Central | 541243 | LKWINBG5 | 161 | 21.0364 | 25.2983 | 4.2619
GEN-2020-061 | 03 - Central | 541244 | ORRICK 5 | 161 | 14.0013 | 14.1631 | 0.1618
GEN-2020-061 | 03 - Central | 541245 | KCSOUTH5 | 161 | 13.2911 | 14.191 | 0.8999
GEN-2020-061 | 03 - Central | 541246 | STROTHR5 | 161 | 13.8179 | 14.7679 | 0.95
GEN-2020-061 | 03 - Central | 541249 | HOOKRD 5 | 161 | 20.062 | 23.0917 | 3.0297
GEN-2020-061 | 03 - Central | 541250 | SIBLEYPL | 161 | 28.4939 | 29.119 | 0.6251
GEN-2020-061 | 03 - Central | 541259 | TURNER_RD5 | 161 | 18.0837 | 18.5934 | 0.5097
GEN-2020-061 | 03 - Central | 541263 | SIBLEY 2 | 69 | 11.843 | 11.8838 | 0.0408
GEN-2020-061 | 03 - Central | 541278 | HOLDEN 2 | 69 | 4.0011 | 4.0169 | 0.0158
GEN-2020-061 | 03 - Central | 541279 | RGREEN 2 | 69 | 9.387 | 9.5656 | 0.1786
GEN-2020-061 | 03 - Central | 541280 | PHILL 2 | 69 | 10.1744 | 10.3958 | 0.2214
GEN-2020-061 | 03 - Central | 541282 | LNGVW 2 | 69 | 10.5435 | 10.6677 | 0.1242
GEN-2020-061 | 03 - Central | 541283 | BRMALL 2 | 69 | 15.3955 | 15.4574 | 0.0619
GEN-2020-061 | 03 - Central | 541284 | GRDVWTP2 | 69 | 9.3891 | 9.4843 | 0.0952
GEN-2020-061 | 03 - Central | 541289 | BELTON 2 | 69 | 9.2586 | 9.3579 | 0.0993
GEN-2020-061 | 03 - Central | 541290 | BELTONS2 | 69 | 10.0149 | 10.1341 | 0.1192
GEN-2020-061 | 03 - Central | 541291 | FREEMAN2 | 69 | 4.5076 | 4.532 | 0.0244
GEN-2020-061 | 03 - Central | 541292 | ANCONDA2 | 69 | 6.3697 | 6.4335 | 0.0638
GEN-2020-061 | 03 - Central | 541293 | HSNVLW 2 | 69 | 6.4729 | 6.5392 | 0.0663
GEN-2020-061 | 03 - Central | 541294 | HSNVLS 2 | 69 | 7.1405 | 7.2238 | 0.0833
GEN-2020-061 | 03 - Central | 541295 | HSNVL 2 | 69 | 8.3946 | 8.5144 | 0.1198
GEN-2020-061 | 03 - Central | 541296 | HSNVLSW2 | 69 | 7.6793 | 7.7813 | 0.102
GEN-2020-061 | 03 - Central | 541297 | HSNVLN 2 | 69 | 7.0282 | 7.1161 | 0.0879
GEN-2020-061 | 03 - Central | 541298 | GRDNCTY2 | 69 | 4.1228 | 4.1517 | 0.0289
GEN-2020-061 | 03 - Central | 541299 | GUNNPS2 | 69 | 3.9463 | 3.9727 | 0.0264
GEN-2020-061 | 03 - Central | 541313 | HARRIS | 161 | 21.6448 | 26.2227 | 4.5779
GEN-2020-061 | 03 - Central | 541340 | BELTONS5 | 161 | 19.1829 | 19.7506 | 0.5677
GEN-2020-061 | 03 - Central | 541341 | S.HARP 5 | 161 | 20.6012 | 21.2789 | 0.6777
GEN-2020-061 | 03 - Central | 541342 | PECULR 5 | 161 | 22.6616 | 23.4216 | 0.76
GEN-2020-061 | 03 - Central | 541343 | S.HARP 2 | 69 | 4.5609 | 4.5835 | 0.0226
GEN-2020-061 | 03 - Central | 541344 | PECULRS5 | 161 | 21.2052 | 21.89 | 0.6848
GEN-2020-061 | 03 - Central | 541347 | RAYMORE | 69 | 8.3705 | 8.47 | 0.0995
GEN-2020-061 | 03 - Central | 541348 | RAYTAP | 69 | 9.0975 | 9.2037 | 0.1062
GEN-2020-061 | 03 - Central | 541386 | HLDENTP2 | 69 | 4.1441 | 4.1611 | 0.017
GEN-2020-061 | 03 - Central | 541387 | KNGSVIL 2 | 69 | 4.2918 | 4.3146 | 0.0228
GEN-2020-061 | 03 - Central | 541388 | KNGSVRL2 | 69 | 4.7127 | 4.7446 | 0.0319
GEN-2020-061 | 03 - Central | 541411 | MC REAC1 | 345 | 8.1965 | 8.2095 | 0.013
GEN-2020-061 | 03 - Central | 541412 | MC REAC2 | 345 | 8.1965 | 8.2095 | 0.013
GEN-2020-061 | 03 - Central | 541413 | MC REAC3 | 345 | 8.1965 | 8.2095 | 0.013
GEN-2020-061 | 03 - Central | 541414 | SIB REA1 | 345 | 18.7143 | 19.15 | 0.4357
GEN-2020-061 | 03 - Central | 541500 | KETCHEM7 | 345 | 8.165 | 8.1946 | 0.0296
GEN-2020-061 | 03 - Central | 541501 | OSBORN7 | 345 | 7.2548 | 7.2779 | 0.0231
GEN-2020-061 | 03 - Central | 541510 | HOLT 7 | 345 | 9.6996 | 9.7102 | 0.0106
GEN-2020-061 | 03 - Central | 541511 | ROCKCK7 | 345 | 7.3742 | 7.3798 | 0.0056
GEN-2020-061 | 03 - Central | 541517 | HOLT_REACT7 | 345 | 9.6461 | 9.6566 | 0.0105
GEN-2020-061 | 03 - Central | 541540 | FREEMAN_SP2 | 69 | 4.204 | 4.2245 | 0.0205
GEN-2020-061 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2.6782 | 2.6785 | 0.0003
GEN-2020-061 | 03 - Central | 541543 | OUTLAW | 345 | 6.0281 | 6.0317 | 0.0036
GEN-2020-061 | 03 - Central | 542940 | ATLNTIC7 | 345 | 21.9968 | 22.188 | 0.1912
GEN-2020-061 | 03 - Central | 542965 | W.GRDNR7 | 345 | 30.7594 | 31.1725 | 0.4131
GEN-2020-061 | 03 - Central | 542966 | WGARDNR5 | 161 | 30.6583 | 30.8153 | 0.157
GEN-2020-061 | 03 - Central | 542968 | STILWEL7 | 345 | 25.939 | 26.7794 | 0.8404
GEN-2020-061 | 03 - Central | 542969 | STILWEL5 | 161 | 40.4923 | 41.684 | 1.1917
GEN-2020-061 | 03 - Central | 542972 | HAWTH 7 | 345 | 23.1005 | 23.4746 | 0.3741
GEN-2020-061 | 03 - Central | 542973 | HAWTHS5 | 161 | 57.0889 | 58.0616 | 0.9727
GEN-2020-061 | 03 - Central | 542976 | LEVEE 5 | 161 | 51.6533 | 52.4249 | 0.7716
GEN-2020-061 | 03 - Central | 542980 | NASHUA 7 | 345 | 23.6553 | 23.8689 | 0.2136
GEN-2020-061 | 03 - Central | 542981 | LACYGNE7 | 345 | 28.4023 | 28.609 | 0.2067
GEN-2020-061 | 03 - Central | 542982 | IATAN 7 | 345 | 30.7925 | 30.9318 | 0.1393
GEN-2020-061 | 03 - Central | 542994 | HICKMAN5 | 161 | 19.8557 | 20.1235 | 0.2678
GEN-2020-061 | 03 - Central | 543000 | BLUEVLY5 | 161 | 38.7994 | 39.2498 | 0.4504
GEN-2020-061 | 03 - Central | 543011 | CHOUTEU5 | 161 | 36.359 | 36.7258 | 0.3668
GEN-2020-061 | 03 - Central | 543027 | RANDLPH5 | 161 | 33.4179 | 33.7344 | 0.3165
GEN-2020-061 | 03 - Central | 543028 | NASHUA-5 | 161 | 34.4703 | 34.734 | 0.2637
GEN-2020-061 | 03 - Central | 543050 | ANTIOCH5 | 161 | 23.2037 | 23.5112 | 0.3075
GEN-2020-061 | 03 - Central | 543053 | REDEL 5 | 161 | 24.6931 | 25.3399 | 0.6468
GEN-2020-061 | 03 - Central | 543054 | CEDARNL5 | 161 | 10.9214 | 10.9412 | 0.0198
GEN-2020-061 | 03 - Central | 543057 | BUCYRUS5 | 161 | 20.9523 | 21.2232 | 0.2709
GEN-2020-061 | 03 - Central | 543058 | NLOUISB5 | 161 | 9.3162 | 9.3694 | 0.0532
GEN-2020-061 | 03 - Central | 543105 | BULLCRK5 | 161 | 29.644 | 29.7878 | 0.1438
GEN-2020-061 | 03 - Central | 543126 | LACKMAN5 | 161 | 13.8243 | 13.9429 | 0.1186
GEN-2020-061 | 03 - Central | 543129 | HAWTHS_G65 | 161 | 56.3026 | 57.2474 | 0.9448
GEN-2020-061 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27.6348 | 27.8304 | 0.1956
GEN-2020-061 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27.6348 | 27.8304 | 0.1956
GEN-2020-061 | 03 - Central | 543659 | LACYGNE2 | 69 | 2.8173 | 2.8177 | 0.0004
GEN-2020-061 | 03 - Central | 543665 | HAWTHN5 | 161 | 57.7296 | 58.7145 | 0.9849
GEN-2020-061 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 0.6738 | 0.6739 | 0.0001
GEN-2020-061 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 0.6453 | 0.6454 | 0.0001
GEN-2020-061 | 03 - Central | 548808 | ECKLES-161 | 161 | 25.3294 | 25.7073 | 0.3779
GEN-2020-061 | 03 - Central | 760746 | GEN-2017-115 | 345 | 7.8842 | 7.8911 | 0.0069
GEN-2020-061 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.5893 | 19.6744 | 0.0851
GEN-2020-061 | 03 - Central | 760921 | G17-209-TAP | 345 | 20.1095 | 20.1994 | 0.0899
GEN-2020-061 | 03 - Central | 761271 | GEN-2017-108 | 161 | 7.5107 | 7.5441 | 0.0334
GEN-2020-061 | 03 - Central | 761278 | G17-108-TAP | 161 | 12.3092 | 12.4206 | 0.1114
GEN-2020-061 | 03 - Central | 761376 | GEN-2017-183 | 345 | 8.9568 | 8.9738 | 0.017
GEN-2020-061 | 03 - Central | 761383 | G17-183-TAP | 345 | 17.7533 | 17.834 | 0.0807
GEN-2020-061 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5.3893 | 5.3931 | 0.0038
GEN-2020-061 | 03 - Central | 762279 | GEN-2017-195 | 345 | 30.6694 | 31.08 | 0.4106
GEN-2020-061 | 03 - Central | 762300 | GEN-2017-196 | 345 | 30.5743 | 30.9823 | 0.408
GEN-2020-061 | 03 - Central | 762581 | GEN-2018-022 | 345 | 7.3136 | 7.3237 | 0.0101
GEN-2020-061 | 03 - Central | 764375 | GEN-2020-058 | 345 | 21.9524 | 22.1428 | 0.1904
GEN-2020-061 | 03 - Central | 765115 | GEN-2020-057 | 345 | 21.9525 | 22.1429 | 0.1904
GEN-2020-061 | 03 - Central | 766260 | GEN-2020-007 | 345 | 24.9998 | 25.1555 | 0.1557
GEN-2020-061 | 03 - Central | 766261 | G20-007-TAP | 345 | 27.5778 | 27.7699 | 0.1921
GEN-2020-061 | 03 - Central | 992001 | VSC2_1 | 276 | 5.7245 | 5.7259 | 0.0014
GEN-2020-061 | 03 - Central | 992002 | VSC2_2 | 276 | 5.7245 | 5.7259 | 0.0014
GEN-2020-061 | 03 - Central | 992003 | VSC2_3 | 345 | 7.055 | 7.0577 | 0.0027
GEN-2020-061 | 03 - Central | 992005 | VSC2_5 | 276 | 5.7245 | 5.7259 | 0.0014
GEN-2020-061 | 03 - Central | 992006 | VSC2_6 | 276 | 5.7245 | 5.7259 | 0.0014
GEN-2020-064 | 03 - Central | 300680 | 2VERONA | 69 | 6.5764 | 6.5956 | 0.0192
GEN-2020-064 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 16.0959 | 16.1277 | 0.0318
GEN-2020-064 | 03 - Central | 300748 | 2NEOSAC | 69 | 10.1075 | 10.2004 | 0.0929
GEN-2020-064 | 03 - Central | 300763 | 2WASHBRN | 69 | 6.7832 | 6.7995 | 0.0163
GEN-2020-064 | 03 - Central | 505480 | BEAVER 5 | 161 | 11.2662 | 11.3035 | 0.0373
GEN-2020-064 | 03 - Central | 505485 | WASHBURN5 | 161 | 8.3008 | 8.3493 | 0.0485
GEN-2020-064 | 03 - Central | 505486 | NEO SPA5 | 161 | 15.1027 | 15.8028 | 0.7001
GEN-2020-064 | 03 - Central | 505488 | CARTHAG5 | 161 | 16.2408 | 16.9087 | 0.6679
GEN-2020-064 | 03 - Central | 505490 | CARTHG 2 | 69 | 13.9321 | 14.0947 | 0.1626
GEN-2020-064 | 03 - Central | 505492 | SPRGFLD5 | 161 | 27.3763 | 27.4351 | 0.0588
GEN-2020-064 | 03 - Central | 510417 | VINTAJC4 | 138 | 5.2138 | 5.231 | 0.0172
GEN-2020-064 | 03 - Central | 512630 | MIAMI 2 | 69 | 12.383 | 12.4993 | 0.1163
GEN-2020-064 | 03 - Central | 512631 | MIAMI 5 | 161 | 9.5004 | 9.6789 | 0.1785
GEN-2020-064 | 03 - Central | 512632 | AFTON 5 | 161 | 8.5016 | 8.5761 | 0.0745
GEN-2020-064 | 03 - Central | 513020 | MIAMI1 2 | 69 | 10.6121 | 10.6974 | 0.0853
GEN-2020-064 | 03 - Central | 513022 | MIAMI4 2 | 69 | 9.0383 | 9.1001 | 0.0618
GEN-2020-064 | 03 - Central | 513026 | COMMTP 2 | 69 | 9.4783 | 9.5463 | 0.068
GEN-2020-064 | 03 - Central | 532777 | G17-009-TAP | 345 | 12.0469 | 12.069 | 0.0221
GEN-2020-064 | 03 - Central | 532778 | GEN-2017-009 | 345 | 11.134 | 11.1528 | 0.0188
GEN-2020-064 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18.4613 | 18.5326 | 0.0713
GEN-2020-064 | 03 - Central | 532934 | MARMTNE5 | 161 | 8.3841 | 8.411 | 0.0269
GEN-2020-064 | 03 - Central | 532935 | MARMTNW5 | 161 | 8.3804 | 8.4072 | 0.0268
GEN-2020-064 | 03 - Central | 532937 | NEOSHO 5 | 161 | 23.7427 | 23.946 | 0.2033
GEN-2020-064 | 03 - Central | 533008 | TV1MNDV4 | 138 | 7.2606 | 7.2674 | 0.0068
GEN-2020-064 | 03 - Central | 533020 | NEOSHOS4 | 138 | 25.3598 | 25.5172 | 0.1574
GEN-2020-064 | 03 - Central | 533021 | NEOSHO 4 | 138 | 25.4029 | 25.5606 | 0.1577
GEN-2020-064 | 03 - Central | 533022 | NEOSHON4 | 138 | 25.284 | 25.4402 | 0.1562
GEN-2020-064 | 03 - Central | 533639 | MARMATN2 | 69 | 9.0215 | 9.0332 | 0.0117
GEN-2020-064 | 03 - Central | 533778 | NEOSHOS2 | 69 | 23.9866 | 24.0702 | 0.0836
GEN-2020-064 | 03 - Central | 547400 | MON376J2 | 69 | 4.121 | 4.13 | 0.009
GEN-2020-064 | 03 - Central | 547401 | MON376 2 | 69 | 6.679 | 6.7028 | 0.0238
GEN-2020-064 | 03 - Central | 547402 | MON416J2 | 69 | 3.6302 | 3.637 | 0.0068
GEN-2020-064 | 03 - Central | 547403 | MON416 2 | 69 | 3.536 | 3.5425 | 0.0065
GEN-2020-064 | 03 - Central | 547404 | PUR390 2 | 69 | 1.7984 | 1.7999 | 0.0015
GEN-2020-064 | 03 - Central | 547405 | MON352J2 | 69 | 7.8982 | 7.9316 | 0.0334
GEN-2020-064 | 03 - Central | 547406 | MON352 2 | 69 | 7.5882 | 7.619 | 0.0308
GEN-2020-064 | 03 - Central | 547407 | MON311J2 | 69 | 6.7635 | 6.7879 | 0.0244
GEN-2020-064 | 03 - Central | 547408 | MON311 2 | 69 | 6.679 | 6.7028 | 0.0238
GEN-2020-064 | 03 - Central | 547409 | SCAM66 2 | 69 | 2.5416 | 2.5514 | 0.0098
GEN-2020-064 | 03 - Central | 547411 | COL282 2 | 69 | 4.6629 | 4.6981 | 0.0352
GEN-2020-064 | 03 - Central | 547412 | SEK225T2 | 69 | 3.5991 | 3.6193 | 0.0202
GEN-2020-064 | 03 - Central | 547413 | SEK225 2 | 69 | 3.5526 | 3.5722 | 0.0196
GEN-2020-064 | 03 - Central | 547414 | SMN425 2 | 69 | 2.0298 | 2.0362 | 0.0064
GEN-2020-064 | 03 - Central | 547415 | SHR444 2 | 69 | 2.7961 | 2.8078 | 0.0117
GEN-2020-064 | 03 - Central | 547416 | CHE299T2 | 69 | 1.9034 | 1.9082 | 0.0048
GEN-2020-064 | 03 - Central | 547417 | CHE299 2 | 69 | 1.8233 | 1.8277 | 0.0044
GEN-2020-064 | 03 - Central | 547418 | CHE300 2 | 69 | 1.8645 | 1.8692 | 0.0047
GEN-2020-064 | 03 - Central | 547419 | TWN388 2 | 69 | 1.8115 | 1.8159 | 0.0044
GEN-2020-064 | 03 - Central | 547420 | WEL186 2 | 69 | 1.166 | 1.1677 | 0.0017
GEN-2020-064 | 03 - Central | 547426 | SEN375 2 | 69 | 3.0605 | 3.0769 | 0.0164
GEN-2020-064 | 03 - Central | 547431 | WEB105 2 | 69 | 8.0122 | 8.1295 | 0.1173
GEN-2020-064 | 03 - Central | 547438 | EXP449T2 | 69 | 8.9273 | 9.107 | 0.1797
GEN-2020-064 | 03 - Central | 547439 | EXP4492 | 69 | 7.4306 | 7.5539 | 0.1233
GEN-2020-064 | 03 - Central | 547449 | PRC460 2 | 69 | 5.7349 | 5.7586 | 0.0237
GEN-2020-064 | 03 - Central | 547455 | SCM66T 2 | 69 | 4.4898 | 4.5211 | 0.0313
GEN-2020-064 | 03 - Central | 547459 | WWR477 | 161 | 18.6728 | 22.2791 | 3.6063
GEN-2020-064 | 03 - Central | 547462 | SVRCK469 5 | 161 | 13.2202 | 14.4236 | 1.2034
GEN-2020-064 | 03 - Central | 547463 | KOD471 2 | 69 | 11.9757 | 12.245 | 0.2693
GEN-2020-064 | 03 - Central | 547466 | ATL109 5 | 161 | 15.5976 | 16.5632 | 0.9656
GEN-2020-064 | 03 - Central | 547467 | ORO110 5 | 161 | 18.4124 | 20.0777 | 1.6653
GEN-2020-064 | 03 - Central | 547468 | AUR124 5 | 161 | 10.7345 | 10.82 | 0.0855
GEN-2020-064 | 03 - Central | 547469 | RIV4525 | 161 | 22.4601 | 24.8094 | 2.3493
GEN-2020-064 | 03 - Central | 547470 | JOP145 5 | 161 | 16.9745 | 19.1474 | 2.1729
GEN-2020-064 | 03 - Central | 547471 | NEO184 5 | 161 | 14.0155 | 14.5735 | 0.558
GEN-2020-064 | 03 - Central | 547472 | TIP292 5 | 161 | 16.3434 | 17.777 | 1.4336
GEN-2020-064 | 03 - Central | 547476 | ASB349 5 | 161 | 11.0395 | 11.3142 | 0.2747
GEN-2020-064 | 03 - Central | 547477 | CJ 366 5 | 161 | 12.1469 | 12.7105 | 0.5636
GEN-2020-064 | 03 - Central | 547479 | LAR382 5 | 161 | 15.4101 | 15.6765 | 0.2664
GEN-2020-064 | 03 - Central | 547480 | MON383 5 | 161 | 12.0094 | 12.2093 | 0.1999
GEN-2020-064 | 03 - Central | 547483 | JOP389 5 | 161 | 17.6408 | 20.0887 | 2.4479
GEN-2020-064 | 03 - Central | 547485 | CAR395 5 | 161 | 12.1781 | 12.5434 | 0.3653
GEN-2020-064 | 03 - Central | 547486 | HOC404 4 | 138 | 6.6755 | 6.7604 | 0.0849
GEN-2020-064 | 03 - Central | 547487 | HOC404 5 | 161 | 13.0664 | 13.5889 | 0.5225
GEN-2020-064 | 03 - Central | 547490 | FIR417 5 | 161 | 13.8349 | 14.6466 | 0.8117
GEN-2020-064 | 03 - Central | 547494 | OAK432 5 | 161 | 16.8855 | 18.1868 | 1.3013
GEN-2020-064 | 03 - Central | 547496 | NOL435 5 | 161 | 10.1246 | 10.212 | 0.0874
GEN-2020-064 | 03 - Central | 547498 | STL439 5 | 161 | 20.1052 | 24.3471 | 4.2419
GEN-2020-064 | 03 - Central | 547499 | CPK446 5 | 161 | 8.7437 | 8.7765 | 0.0328
GEN-2020-064 | 03 - Central | 547500 | RNM393 5 | 161 | 13.4508 | 14.4879 | 1.0371
GEN-2020-064 | 03 - Central | 547501 | RIV453 5 | 161 | 21.351 | 23.3993 | 2.0483
GEN-2020-064 | 03 - Central | 547502 | RIV167 5 | 161 | 20.957 | 22.968 | 2.011
GEN-2020-064 | 03 - Central | 547503 | RIV452T 5 | 161 | 22.0891 | 24.335 | 2.2459
GEN-2020-064 | 03 - Central | 547524 | NEO 56 2 | 69 | 7.8803 | 7.9678 | 0.0875
GEN-2020-064 | 03 - Central | 547525 | JOP 59 2 | 69 | 19.1631 | 19.9658 | 0.8027
GEN-2020-064 | 03 - Central | 547526 | JOP 64 2 | 69 | 18.83 | 19.6039 | 0.7739
GEN-2020-064 | 03 - Central | 547527 | WEB436 2 | 69 | 9.5414 | 9.7038 | 0.1624
GEN-2020-064 | 03 - Central | 547530 | COL 94 2 | 69 | 6.5221 | 6.5895 | 0.0674
GEN-2020-064 | 03 - Central | 547531 | JOP100 2 | 69 | 15.8232 | 16.3556 | 0.5324
GEN-2020-064 | 03 - Central | 547532 | CAR108 2 | 69 | 8.4101 | 8.5107 | 0.1006
GEN-2020-064 | 03 - Central | 547533 | ATL109 2 | 69 | 20.3796 | 21.1739 | 0.7943
GEN-2020-064 | 03 - Central | 547534 | ORO110 2 | 69 | 17.6401 | 18.2668 | 0.6267
GEN-2020-064 | 03 - Central | 547537 | AUR124 2 | 69 | 12.5596 | 12.6096 | 0.05
GEN-2020-064 | 03 - Central | 547539 | JOP145 2 | 69 | 20.3211 | 21.2624 | 0.9413
GEN-2020-064 | 03 - Central | 547540 | MON152 2 | 69 | 10.9447 | 11.0061 | 0.0614
GEN-2020-064 | 03 - Central | 547541 | RIV167 2 | 69 | 17.4043 | 17.9864 | 0.5821
GEN-2020-064 | 03 - Central | 547543 | NEO184 2 | 69 | 11.8948 | 12.0789 | 0.1841
GEN-2020-064 | 03 - Central | 547551 | GAT258 2 | 69 | 14.2564 | 14.6783 | 0.4219
GEN-2020-064 | 03 - Central | 547554 | BAX271 2 | 69 | 9.5672 | 9.7076 | 0.1404
GEN-2020-064 | 03 - Central | 547555 | GAL278 2 | 69 | 12.9651 | 13.329 | 0.3639
GEN-2020-064 | 03 - Central | 547556 | OAK280 2 | 69 | 15.6951 | 16.1797 | 0.4846
GEN-2020-064 | 03 - Central | 547557 | JOP284 2 | 69 | 16.3945 | 16.9696 | 0.5751
GEN-2020-064 | 03 - Central | 547559 | TIP292 2 | 69 | 9.92 | 10.0962 | 0.1762
GEN-2020-064 | 03 - Central | 547574 | JOP341 2 | 69 | 17.7292 | 18.4213 | 0.6921
GEN-2020-064 | 03 - Central | 547589 | RAC375 2 | 69 | 6.2183 | 6.2925 | 0.0742
GEN-2020-064 | 03 - Central | 547590 | QUA377 2 | 69 | 7.2812 | 7.3504 | 0.0692
GEN-2020-064 | 03 - Central | 547591 | MON383 2 | 69 | 12.6119 | 12.6978 | 0.0859
GEN-2020-064 | 03 - Central | 547592 | JOP389 2 | 69 | 15.0145 | 15.5762 | 0.5617
GEN-2020-064 | 03 - Central | 547593 | JOP391 5 | 161 | 12.6417 | 13.6025 | 0.9608
GEN-2020-064 | 03 - Central | 547595 | RNM393 2 | 69 | 18.9775 | 19.6947 | 0.7172
GEN-2020-064 | 03 - Central | 547601 | HOC404 2 | 69 | 9.6937 | 9.8264 | 0.1327
GEN-2020-064 | 03 - Central | 547602 | RIV406 2 | 69 | 15.5087 | 15.9643 | 0.4556
GEN-2020-064 | 03 - Central | 547607 | JOP422 5 | 161 | 12.4366 | 13.4218 | 0.9852
GEN-2020-064 | 03 - Central | 547608 | JOP430 2 | 69 | 15.5409 | 16.0904 | 0.5495
GEN-2020-064 | 03 - Central | 547685 | PLB447 2 | 69 | 14.2163 | 14.6328 | 0.4165
GEN-2020-064 | 03 - Central | 547690 | GLF339 2 | 69 | 11.8415 | 12.1232 | 0.2817
GEN-2020-064 | 03 - Central | 547728 | GAL278T | 69 | 13.2428 | 13.6227 | 0.3799
GEN-2020-064 | 03 - Central | 547729 | BAX488 5 | 161 | 14.533 | 15.2752 | 0.7422
GEN-2020-064 | 03 - Central | 588980 | GEN-2017-060 | 161 | 6.2053 | 6.2434 | 0.0381
GEN-2020-064 | 03 - Central | 589200 | GEN-2017-082 | 161 | 7.5589 | 7.6802 | 0.1213
GEN-2020-064 | 03 - Central | 760242 | GEN-2017-188 | 161 | 2.0246 | 2.0299 | 0.0053
GEN-2020-064 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.6685 | 19.6744 | 0.0059
GEN-2020-064 | 03 - Central | 760921 | G17-209-TAP | 345 | 20.1931 | 20.1994 | 0.0063
GEN-2020-064 | 03 - Central | 762680 | GEN-2018-032 | 345 | 12.1118 | 12.1425 | 0.0307
GEN-2020-064 | 03 - Central | 763692 | GEN-2019-035 | 161 | 7.844 | 7.8727 | 0.0287
GEN-2020-064 | 03 - Central | 763696 | G19-035-TAP | 161 | 7.8615 | 7.8903 | 0.0288
GEN-2020-064 | 03 - Central | 764300 | GEN-2020-079 | 161 | 14.7693 | 15.4113 | 0.642
GEN-2020-064 | 03 - Central | 764310 | G20-079-TAP | 161 | 17.646 | 18.6071 | 0.9611
GEN-2020-064 | 03 - Central | 764315 | GEN-2020-088 | 161 | 14.9522 | 15.2024 | 0.2502
GEN-2020-064 | 03 - Central | 765100 | GEN-2020-052 | 345 | 9.9136 | 9.928 | 0.0144
GEN-2020-064 | 03 - Central | 765110 | G20-052-TAP | 345 | 13.093 | 13.1185 | 0.0255
GEN-2020-071 | 03 - Central | 530592 | SMOKYHL6 | 230 | 6.3434 | 6.3444 | 0.001
GEN-2020-071 | 03 - Central | 530593 | SMKYP1 6 | 230 | 5.5704 | 5.5711 | 0.0007
GEN-2020-071 | 03 - Central | 530599 | SMKYP2 6 | 230 | 5.8459 | 5.8467 | 0.0008
GEN-2020-071 | 03 - Central | 530720 | KNOLL S 6 | 230 | 11.2806 | 11.2811 | 0.0005
GEN-2020-071 | 03 - Central | 532765 | HOYT 7 | 345 | 16.1649 | 16.1848 | 0.0199
GEN-2020-071 | 03 - Central | 532766 | JEC N 7 | 345 | 22.2858 | 22.3292 | 0.0434
GEN-2020-071 | 03 - Central | 532767 | GEARY 7 | 345 | 10.3257 | 10.3363 | 0.0106
GEN-2020-071 | 03 - Central | 532768 | EMPEC 7 | 345 | 16.764 | 16.8308 | 0.0668
GEN-2020-071 | 03 - Central | 532769 | LANG 7 | 345 | 16.5797 | 16.6452 | 0.0655
GEN-2020-071 | 03 - Central | 532770 | MORRIS 7 | 345 | 12.853 | 12.9096 | 0.0566
GEN-2020-071 | 03 - Central | 532772 | STRANGR7 | 345 | 27.752 | 27.7712 | 0.0192
GEN-2020-071 | 03 - Central | 532773 | SUMMIT 7 | 345 | 11.3559 | 11.3648 | 0.0089
GEN-2020-071 | 03 - Central | 532774 | SWISVAL7 | 345 | 17.4822 | 17.6348 | 0.1526
GEN-2020-071 | 03 - Central | 532776 | READWF 7 | 345 | 14.0214 | 14.0678 | 0.0464
GEN-2020-071 | 03 - Central | 532794 | ROSEHIL7 | 345 | 19.6765 | 19.6793 | 0.0028
GEN-2020-071 | 03 - Central | 532796 | WICHITA7 | 345 | 24.498 | 24.5073 | 0.0093
GEN-2020-071 | 03 - Central | 532797 | WOLFCRK7 | 345 | 22.1297 | 22.1344 | 0.0047
GEN-2020-071 | 03 - Central | 532799 | WAVERLY7 | 345 | 18.6109 | 18.6143 | 0.0034
GEN-2020-071 | 03 - Central | 532802 | WAVERTX7 | 345 | 15.1864 | 15.1886 | 0.0022
GEN-2020-071 | 03 - Central | 532851 | AUBURN 6 | 230 | 13.6713 | 13.7402 | 0.0689
GEN-2020-071 | 03 - Central | 532852 | JEC 6 | 230 | 23.5018 | 23.5412 | 0.0394
GEN-2020-071 | 03 - Central | 532853 | LAWHILL6 | 230 | 14.0941 | 14.1387 | 0.0446
GEN-2020-071 | 03 - Central | 532854 | LEC U5 6 | 230 | 13.9622 | 14.0056 | 0.0434
GEN-2020-071 | 03 - Central | 532855 | MIDLAND6 | 230 | 12.514 | 12.5477 | 0.0337
GEN-2020-071 | 03 - Central | 532856 | SWISVAL6 | 230 | 22.2139 | 22.5998 | 0.3859
GEN-2020-071 | 03 - Central | 532857 | TECHILL6 | 230 | 11.1139 | 11.179 | 0.0651
GEN-2020-071 | 03 - Central | 532861 | EMANHAT6 | 230 | 10.247 | 10.2557 | 0.0087
GEN-2020-071 | 03 - Central | 532862 | MCDOWEL6 | 230 | 7.2398 | 7.2575 | 0.0177
GEN-2020-071 | 03 - Central | 532863 | MORRIS 6 | 230 | 14.1073 | 14.2239 | 0.1166
GEN-2020-071 | 03 - Central | 532865 | NMANHT6 | 230 | 9.3841 | 9.3914 | 0.0073
GEN-2020-071 | 03 - Central | 532871 | CIRCLE 6 | 230 | 8.8783 | 8.8801 | 0.0018
GEN-2020-071 | 03 - Central | 532872 | EMCPHER6 | 230 | 8.0934 | 8.0958 | 0.0024
GEN-2020-071 | 03 - Central | 532873 | SUMMIT 6 | 230 | 13.4832 | 13.4946 | 0.0114
GEN-2020-071 | 03 - Central | 532874 | UNIONRG6 | 230 | 8.2931 | 8.3074 | 0.0143
GEN-2020-071 | 03 - Central | 532875 | DVISTA 6 | 230 | 4.8953 | 4.8995 | 0.0042
GEN-2020-071 | 03 - Central | 532920 | TECHILL5 | 161 | 5.8405 | 5.8451 | 0.0046
GEN-2020-071 | 03 - Central | 533151 | AUBURN 3 | 115 | 21.8148 | 21.8836 | 0.0688
GEN-2020-071 | 03 - Central | 533153 | COLINE 3 | 115 | 17.9932 | 18.028 | 0.0348
GEN-2020-071 | 03 - Central | 533155 | CROOKED3 | 115 | 20.6451 | 20.7068 | 0.0617
GEN-2020-071 | 03 - Central | 533156 | 54&MERI3 | 115 | 14.7984 | 14.8191 | 0.0207
GEN-2020-071 | 03 - Central | 533160 | 41CALIF3 | 115 | 17.1446 | 17.1845 | 0.0399
GEN-2020-071 | 03 - Central | 533162 | INDNOLA3 | 115 | 19.3813 | 19.4222 | 0.0409
GEN-2020-071 | 03 - Central | 533163 | HOYT 3 | 115 | 23.3068 | 23.3333 | 0.0265
GEN-2020-071 | 03 - Central | 533166 | INDIANH3 | 115 | 17.7113 | 17.7525 | 0.0412
GEN-2020-071 | 03 - Central | 533167 | KEENE 3 | 115 | 9.9963 | 10.0088 | 0.0125
GEN-2020-071 | 03 - Central | 533175 | 17&FAIR3 | 115 | 18.4894 | 18.5328 | 0.0434
GEN-2020-071 | 03 - Central | 533176 | SHAWNEE3 | 115 | 13.2701 | 13.2942 | 0.0241
GEN-2020-071 | 03 - Central | 533177 | 6 GOLDN3 | 115 | 15.4359 | 15.4668 | 0.0309
GEN-2020-071 | 03 - Central | 533178 | S GAGEE3 | 115 | 20.2516 | 20.3065 | 0.0549
GEN-2020-071 | 03 - Central | 533181 | TECHILW3 | 115 | 25.2422 | 25.3309 | 0.0887
GEN-2020-071 | 03 - Central | 533182 | TECHILE3 | 115 | 25.2963 | 25.3855 | 0.0892
GEN-2020-071 | 03 - Central | 533183 | WM BROS3 | 115 | 12.7483 | 12.7698 | 0.0215
GEN-2020-071 | 03 - Central | 533187 | 27CROCO3 | 115 | 18.4933 | 18.5403 | 0.047
GEN-2020-071 | 03 - Central | 533194 | SHERWOD3 | 115 | 19.959 | 20.0156 | 0.0566
GEN-2020-071 | 03 - Central | 533197 | HARTLND3 | 115 | 13.3872 | 13.411 | 0.0238
GEN-2020-071 | 03 - Central | 533203 | TEC E 3 | 115 | 24.0689 | 24.1495 | 0.0806
GEN-2020-071 | 03 - Central | 533232 | BALDCRK3 | 115 | 14.5133 | 14.5286 | 0.0153
GEN-2020-071 | 03 - Central | 533241 | FMC 3 | 115 | 18.0977 | 18.1207 | 0.023
GEN-2020-071 | 03 - Central | 533244 | JARBALO3 | 115 | 27.2969 | 27.3139 | 0.017
GEN-2020-071 | 03 - Central | 533248 | LEC U3 3 | 115 | 25.472 | 25.5191 | 0.0471
GEN-2020-071 | 03 - Central | 533249 | LEC U4 3 | 115 | 25.4406 | 25.4854 | 0.0448
GEN-2020-071 | 03 - Central | 533250 | LWRNCHL3 | 115 | 27.068 | 27.1212 | 0.0532
GEN-2020-071 | 03 - Central | 533252 | MIDLADN3 | 115 | 25.9972 | 26.0462 | 0.049
GEN-2020-071 | 03 - Central | 533253 | MOCKBRD3 | 115 | 17.907 | 17.9318 | 0.0248
GEN-2020-071 | 03 - Central | 533257 | FREESTATE3 | 115 | 19.2896 | 19.316 | 0.0264
GEN-2020-071 | 03 - Central | 533260 | MIDLADS3 | 115 | 26.0147 | 26.0636 | 0.0489
GEN-2020-071 | 03 - Central | 533261 | PENTAGN3 | 115 | 22.5241 | 22.5342 | 0.0101
GEN-2020-071 | 03 - Central | 533264 | 6TH ST 3 | 115 | 18.5642 | 18.5886 | 0.0244
GEN-2020-071 | 03 - Central | 533269 | STULL 3 | 115 | 12.0408 | 12.055 | 0.0142
GEN-2020-071 | 03 - Central | 533270 | STULL T3 | 115 | 12.1633 | 12.1779 | 0.0146
GEN-2020-071 | 03 - Central | 533271 | SWLWRNC3 | 115 | 19.2546 | 19.2815 | 0.0269
GEN-2020-071 | 03 - Central | 533280 | WREN 3 | 115 | 18.9455 | 18.9711 | 0.0256
GEN-2020-071 | 03 - Central | 533301 | EAST ST3 | 115 | 10.1685 | 10.1784 | 0.0099
GEN-2020-071 | 03 - Central | 533302 | EEUREKA3 | 115 | 4.3299 | 4.3303 | 0.0004
GEN-2020-071 | 03 - Central | 533304 | LANG 3 | 115 | 15.6695 | 15.6919 | 0.0224
GEN-2020-071 | 03 - Central | 533305 | MORRIS 3 | 115 | 12.978 | 13.0201 | 0.0421
GEN-2020-071 | 03 - Central | 533307 | PRAIRIE3 | 115 | 10.3081 | 10.3183 | 0.0102
GEN-2020-071 | 03 - Central | 533308 | VAUGHN 3 | 115 | 4.4876 | 4.4888 | 0.0012
GEN-2020-071 | 03 - Central | 533309 | WEMPORI3 | 115 | 11.2807 | 11.2932 | 0.0125
GEN-2020-071 | 03 - Central | 533310 | WMBROS 3 | 115 | 7.451 | 7.456 | 0.005
GEN-2020-071 | 03 - Central | 533311 | WMBROSJ3 | 115 | 7.5311 | 7.5362 | 0.0051
GEN-2020-071 | 03 - Central | 533320 | CLAYCSS3 | 115 | 2.4368 | 2.4371 | 0.0003
GEN-2020-071 | 03 - Central | 533323 | CLAYCTR3 | 115 | 3.1055 | 3.106 | 0.0005
GEN-2020-071 | 03 - Central | 533324 | TCRILEY 3 | 115 | 2.1377 | 2.1379 | 0.0002
GEN-2020-071 | 03 - Central | 533325 | CLAYGEN3 | 115 | 2.3639 | 2.3642 | 0.0003
GEN-2020-071 | 03 - Central | 533326 | EMANHAT3 | 115 | 13.8673 | 13.8771 | 0.0098
GEN-2020-071 | 03 - Central | 533327 | LEVEE 3 | 115 | 13.2174 | 13.2263 | 0.0089
GEN-2020-071 | 03 - Central | 533328 | FT JCT 3 | 115 | 15.8291 | 15.8432 | 0.0141
GEN-2020-071 | 03 - Central | 533330 | JCTCTY 3 | 115 | 13.4537 | 13.4639 | 0.0102
GEN-2020-071 | 03 - Central | 533335 | MCDOWEL3 | 115 | 19.1159 | 19.1461 | 0.0302
GEN-2020-071 | 03 - Central | 533336 | GEARY 3 | 115 | 19.7747 | 19.7945 | 0.0198
GEN-2020-071 | 03 - Central | 533339 | S ALMA 3 | 115 | 8.78 | 8.7883 | 0.0083
GEN-2020-071 | 03 - Central | 533341 | STAGGHL3 | 115 | 10.0719 | 10.0784 | 0.0065
GEN-2020-071 | 03 - Central | 533342 | WJCCTY 3 | 115 | 14.2762 | 14.2874 | 0.0112
GEN-2020-071 | 03 - Central | 533345 | WILDCAT3 | 115 | 10.2854 | 10.2916 | 0.0062
GEN-2020-071 | 03 - Central | 533359 | UNIONRG3 | 115 | 3.881 | 3.8826 | 0.0016
GEN-2020-071 | 03 - Central | 533360 | TCHOPE 3 | 115 | 3.4592 | 3.4605 | 0.0013
GEN-2020-071 | 03 - Central | 533362 | CHAPMAN3 | 115 | 11.8464 | 11.8531 | 0.0067
GEN-2020-071 | 03 - Central | 533366 | FLORENC3 | 115 | 3.5005 | 3.501 | 0.0005
GEN-2020-071 | 03 - Central | 533371 | NORTHVW3 | 115 | 12.4632 | 12.4678 | 0.0046
GEN-2020-071 | 03 - Central | 533374 | MENTOR 3 | 115 | 12.81 | 12.8147 | 0.0047
GEN-2020-071 | 03 - Central | 533379 | SO GATE3 | 115 | 10.6378 | 10.6411 | 0.0033
GEN-2020-071 | 03 - Central | 533381 | SUMMIT 3 | 115 | 17.9623 | 17.9721 | 0.0098
GEN-2020-071 | 03 - Central | 533417 | EMCPHER3 | 115 | 11.722 | 11.7244 | 0.0024
GEN-2020-071 | 03 - Central | 533456 | COLINE 2 | 69 | 9.7989 | 9.8047 | 0.0058
GEN-2020-071 | 03 - Central | 533629 | CC2SHAR2 | 69 | 4.8477 | 4.8477 | 0
GEN-2020-071 | 03 - Central | 533653 | WOLFCRK2 | 69 | 6.278 | 6.2781 | 0.0001
GEN-2020-071 | 03 - Central | 541198 | PECULR 7 | 345 | 21.2255 | 21.2331 | 0.0076
GEN-2020-071 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2.6785 | 2.6785 | 0
GEN-2020-071 | 03 - Central | 542940 | ATLNTIC7 | 345 | 22.1676 | 22.188 | 0.0204
GEN-2020-071 | 03 - Central | 542965 | W.GRDNR7 | 345 | 31.1214 | 31.1725 | 0.0511
GEN-2020-071 | 03 - Central | 542966 | WGARDNR5 | 161 | 30.8047 | 30.8153 | 0.0106
GEN-2020-071 | 03 - Central | 542968 | STILWEL7 | 345 | 26.7632 | 26.7794 | 0.0162
GEN-2020-071 | 03 - Central | 542969 | STILWEL5 | 161 | 41.6702 | 41.684 | 0.0138
GEN-2020-071 | 03 - Central | 542977 | CRAIG 7 | 345 | 22.7693 | 22.7852 | 0.0159
GEN-2020-071 | 03 - Central | 542981 | LACYGNE7 | 345 | 28.5993 | 28.609 | 0.0097
GEN-2020-071 | 03 - Central | 543049 | CEDRCRK5 | 161 | 31.3428 | 31.3524 | 0.0096
GEN-2020-071 | 03 - Central | 543054 | CEDARNL5 | 161 | 10.9399 | 10.9412 | 0.0013
GEN-2020-071 | 03 - Central | 543077 | PLSTVAL5 | 161 | 10.6961 | 10.6971 | 0.001
GEN-2020-071 | 03 - Central | 543105 | BULLCRK5 | 161 | 29.7781 | 29.7878 | 0.0097
GEN-2020-071 | 03 - Central | 543132 | BNSF 5 | 161 | 22.5473 | 22.5528 | 0.0055
GEN-2020-071 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27.8213 | 27.8304 | 0.0091
GEN-2020-071 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27.8213 | 27.8304 | 0.0091
GEN-2020-071 | 03 - Central | 543659 | LACYGNE2 | 69 | 2.8177 | 2.8177 | 0
GEN-2020-071 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 0.6739 | 0.6739 | 0
GEN-2020-071 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 0.6454 | 0.6454 | 0
GEN-2020-071 | 03 - Central | 562476 | G14-001-TAP | 345 | 10.8336 | 10.8417 | 0.0081
GEN-2020-071 | 03 - Central | 583850 | GEN-2014-001 | 345 | 7.3037 | 7.3073 | 0.0036
GEN-2020-071 | 03 - Central | 587880 | GEN-2016-111 | 345 | 6.8043 | 6.8062 | 0.0019
GEN-2020-071 | 03 - Central | 587884 | G16-111-TAP | 345 | 10.2166 | 10.2212 | 0.0046
GEN-2020-071 | 03 - Central | 588240 | GEN-2016-149 | 345 | 9.0713 | 9.0727 | 0.0014
GEN-2020-071 | 03 - Central | 588250 | GEN-2016-174 | 345 | 5.9125 | 5.9129 | 0.0004
GEN-2020-071 | 03 - Central | 588260 | GEN-2016-176 | 345 | 4.7943 | 4.7946 | 0.0003
GEN-2020-071 | 03 - Central | 588270 | GEN-2016-150 | 345 | 3.567 | 3.5671 | 0.0001
GEN-2020-071 | 03 - Central | 588490 | GEN-2017-004 | 345 | 8.4061 | 8.4108 | 0.0047
GEN-2020-071 | 03 - Central | 588494 | G17-004-TAP | 345 | 9.7358 | 9.7422 | 0.0064
GEN-2020-071 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.6704 | 19.6744 | 0.004
GEN-2020-071 | 03 - Central | 760921 | G17-209-TAP | 345 | 20.1951 | 20.1994 | 0.0043
GEN-2020-071 | 03 - Central | 762279 | GEN-2017-195 | 345 | 31.0292 | 31.08 | 0.0508
GEN-2020-071 | 03 - Central | 762300 | GEN-2017-196 | 345 | 30.9319 | 30.9823 | 0.0504
GEN-2020-071 | 03 - Central | 762405 | ASG-2018-010 | 161 | 3.3625 | 3.3626 | 0.0001
GEN-2020-071 | 03 - Central | 764375 | GEN-2020-058 | 345 | 22.1225 | 22.1428 | 0.0203
GEN-2020-071 | 03 - Central | 765115 | GEN-2020-057 | 345 | 22.1226 | 22.1429 | 0.0203
GEN-2020-071 | 03 - Central | 765130 | GEN-2020-071 | 230 | 10.8077 | 11.3791 | 0.5714
GEN-2020-071 | 03 - Central | 765140 | G20-071-TAP | 230 | 10.8077 | 11.3791 | 0.5714
GEN-2020-071 | 03 - Central | 765145 | GEN-2020-076 | 345 | 12.5504 | 12.5518 | 0.0014
GEN-2020-071 | 03 - Central | 765155 | G20-076-TAP | 345 | 12.5581 | 12.5595 | 0.0014
GEN-2020-071 | 03 - Central | 765160 | GEN-2020-086 | 345 | 12.551 | 12.5524 | 0.0014
GEN-2020-071 | 03 - Central | 765190 | GEN-2020-090 | 345 | 8.7259 | 8.7262 | 0.0003
GEN-2020-071 | 03 - Central | 765200 | G20-090-TAP | 345 | 9.9527 | 9.9531 | 0.0004
GEN-2020-071 | 03 - Central | 766260 | GEN-2020-007 | 345 | 25.1481 | 25.1555 | 0.0074
GEN-2020-071 | 03 - Central | 766261 | G20-007-TAP | 345 | 27.7608 | 27.7699 | 0.0091
GEN-2020-072 | 03 - Central | 99911 | GI91POI | 69 | 2.949 | 2.9532 | 0.0042
GEN-2020-072 | 03 - Central | 300034 | 5EDMONS | 161 | 6.6217 | 6.6455 | 0.0238
GEN-2020-072 | 03 - Central | 300071 | 5CLINTN | 161 | 13.8165 | 14.2379 | 0.4214
GEN-2020-072 | 03 - Central | 300082 | 5GEORGE | 161 | 8.4604 | 8.6368 | 0.1764
GEN-2020-072 | 03 - Central | 300105 | 5NORTON | 161 | 6.8038 | 6.8371 | 0.0333
GEN-2020-072 | 03 - Central | 300108 | 5OSCEOLTP | 161 | 6.6647 | 6.702 | 0.0373
GEN-2020-072 | 03 - Central | 300110 | 5PITTSV | 161 | 8.81 | 8.8245 | 0.0145
GEN-2020-072 | 03 - Central | 300117 | 5SEDALA | 161 | 9.1243 | 9.4505 | 0.3262
GEN-2020-072 | 03 - Central | 300124 | 5HOLDENB2 | 161 | 7.8515 | 7.8805 | 0.029
GEN-2020-072 | 03 - Central | 300323 | 2CENTRV | 69 | 4.4832 | 4.487 | 0.0038
GEN-2020-072 | 03 - Central | 300327 | 2ELM | 69 | 4.4554 | 4.4585 | 0.0031
GEN-2020-072 | 03 - Central | 300328 | 2MAGNOL | 69 | 2.2772 | 2.2781 | 0.0009
GEN-2020-072 | 03 - Central | 300336 | 2HOLDEN | 69 | 6.5746 | 6.5824 | 0.0078
GEN-2020-072 | 03 - Central | 300527 | 2BEAMAN | 69 | 3.8552 | 3.8658 | 0.0106
GEN-2020-072 | 03 - Central | 300528 | 2DRESDN | 69 | 5.9564 | 5.9903 | 0.0339
GEN-2020-072 | 03 - Central | 300529 | 2GEOGT1 | 69 | 7.4262 | 7.477 | 0.0508
GEN-2020-072 | 03 - Central | 300530 | 2GEOGT2 | 69 | 8.0149 | 8.0757 | 0.0608
GEN-2020-072 | 03 - Central | 300531 | 2GEORGE | 69 | 8.1067 | 8.1682 | 0.0615
GEN-2020-072 | 03 - Central | 300534 | 2LINCLN | 69 | 4.9652 | 4.9837 | 0.0185
GEN-2020-072 | 03 - Central | 300541 | 2SEDALI | 69 | 10.3511 | 10.4581 | 0.107
GEN-2020-072 | 03 - Central | 300542 | 2SMTHTN | 69 | 4.5038 | 4.5183 | 0.0145
GEN-2020-072 | 03 - Central | 300553 | 2FLORNC | 69 | 3.8026 | 3.8085 | 0.0059
GEN-2020-072 | 03 - Central | 300557 | 2IVYBND | 69 | 2.7904 | 2.7934 | 0.003
GEN-2020-072 | 03 - Central | 300558 | 2MTHULD | 69 | 2.9766 | 2.9814 | 0.0048
GEN-2020-072 | 03 - Central | 300562 | 2STOVER | 69 | 1.9628 | 1.9649 | 0.0021
GEN-2020-072 | 03 - Central | 300690 | 2BUTLERE | 69 | 4.8354 | 4.8387 | 0.0033
GEN-2020-072 | 03 - Central | 300692 | 2CLINTN | 69 | 13.9624 | 14.1001 | 0.1377
GEN-2020-072 | 03 - Central | 300696 | 2CREIGH | 69 | 4.1531 | 4.1567 | 0.0036
GEN-2020-072 | 03 - Central | 300701 | 2GAINES | 69 | 4.6754 | 4.6878 | 0.0124
GEN-2020-072 | 03 - Central | 300702 | 2LADUE | 69 | 4.0843 | 4.0929 | 0.0086
GEN-2020-072 | 03 - Central | 300703 | 2LEETON | 69 | 4.0325 | 4.0406 | 0.0081
GEN-2020-072 | 03 - Central | 300706 | 2PIPER | 69 | 3.7528 | 3.7585 | 0.0057
GEN-2020-072 | 03 - Central | 300789 | 2TRUMAN | 69 | 1.9276 | 1.9293 | 0.0017
GEN-2020-072 | 03 - Central | 300810 | 2MTZION | 69 | 3.9954 | 4.0027 | 0.0073
GEN-2020-072 | 03 - Central | 300816 | 5COLLINS | 161 | 6.7663 | 6.7884 | 0.0221
GEN-2020-072 | 03 - Central | 301040 | 5OSCEOL | 161 | 6.6487 | 6.6858 | 0.0371
GEN-2020-072 | 03 - Central | 301370 | 5TURKEYCRK | 161 | 5.397 | 5.4155 | 0.0185
GEN-2020-072 | 03 - Central | 301402 | 5LOSTVALY | 161 | 7.33 | 7.365 | 0.035
GEN-2020-072 | 03 - Central | 301477 | 5OSCEOKCTP | 161 | 6.6633 | 6.7007 | 0.0374
GEN-2020-072 | 03 - Central | 301522 | 5OSCEOKC | 161 | 6.6559 | 6.6932 | 0.0373
GEN-2020-072 | 03 - Central | 301561 | 5HOLDENB1 | 161 | 7.8476 | 7.8765 | 0.0289
GEN-2020-072 | 03 - Central | 301567 | 5NORTONTP | 161 | 6.3049 | 6.3423 | 0.0374
GEN-2020-072 | 03 - Central | 301626 | 2CLINTNLD | 69 | 13.7774 | 13.9115 | 0.1341
GEN-2020-072 | 03 - Central | 344233 | 5CALIF UE 1 | 161 | 10.8067 | 10.8178 | 0.0111
GEN-2020-072 | 03 - Central | 345071 | 5MCBAIN T | 161 | 14.5537 | 14.5631 | 0.0094
GEN-2020-072 | 03 - Central | 345409 | 5OVERTON | 161 | 21.3068 | 21.347 | 0.0402
GEN-2020-072 | 03 - Central | 345411 | 5OVERTON 2 | 161 | 21.3068 | 21.347 | 0.0402
GEN-2020-072 | 03 - Central | 346117 | 2OVERTON | 69 | 3.6866 | 3.6871 | 0.0005
GEN-2020-072 | 03 - Central | 503507 | 2BUTLEREGEN | 69 | 4.8329 | 4.8361 | 0.0032
GEN-2020-072 | 03 - Central | 505502 | TRUMAN 5 | 161 | 7.5388 | 7.5785 | 0.0397
GEN-2020-072 | 03 - Central | 541138 | CLNTPLT_CAP2 | 69 | 8.4823 | 8.5357 | 0.0534
GEN-2020-072 | 03 - Central | 541146 | SEDLIAW_CAP5 | 161 | 9.3944 | 9.6416 | 0.2472
GEN-2020-072 | 03 - Central | 541148 | WBURGE_CAP5 | 161 | 6.413 | 6.4642 | 0.0512
GEN-2020-072 | 03 - Central | 541207 | ARCHIE 5 | 161 | 16.7148 | 16.7507 | 0.0359
GEN-2020-072 | 03 - Central | 541209 | SEDALIA5 | 161 | 9.9338 | 10.2107 | 0.2769
GEN-2020-072 | 03 - Central | 541217 | WINDSR 5 | 161 | 7.765 | 8.6111 | 0.8461
GEN-2020-072 | 03 - Central | 541228 | WBURGE 5 | 161 | 6.6599 | 6.7152 | 0.0553
GEN-2020-072 | 03 - Central | 541239 | HSNVL 5 | 161 | 15.7027 | 15.7268 | 0.0241
GEN-2020-072 | 03 - Central | 541240 | ADRIAN 5 | 161 | 8.5197 | 8.5297 | 0.01
GEN-2020-072 | 03 - Central | 541241 | SEDEAST5 | 161 | 7.7866 | 7.9089 | 0.1223
GEN-2020-072 | 03 - Central | 541242 | CLINTON5 | 161 | 13.7633 | 14.1815 | 0.4182
GEN-2020-072 | 03 - Central | 541270 | KNOSTER2 | 69 | 4.9825 | 4.9968 | 0.0143
GEN-2020-072 | 03 - Central | 541271 | SEDN 2 | 69 | 8.0202 | 8.0734 | 0.0532
GEN-2020-072 | 03 - Central | 541272 | SEDS 2 | 69 | 6.8125 | 6.8559 | 0.0434
GEN-2020-072 | 03 - Central | 541273 | KELHYS 2 | 69 | 7.5404 | 7.588 | 0.0476
GEN-2020-072 | 03 - Central | 541274 | PITTCRN2 | 69 | 6.7765 | 6.8184 | 0.0419
GEN-2020-072 | 03 - Central | 541275 | SEDPLT 2 | 69 | 7.0271 | 7.0699 | 0.0428
GEN-2020-072 | 03 - Central | 541301 | CLNTPLT2 | 69 | 8.6644 | 8.7201 | 0.0557
GEN-2020-072 | 03 - Central | 541302 | CLNTGRN2 | 69 | 8.3962 | 8.4494 | 0.0532
GEN-2020-072 | 03 - Central | 541303 | CLNTN N2 | 69 | 8.1839 | 8.2357 | 0.0518
GEN-2020-072 | 03 - Central | 541314 | NWARSAW5 | 161 | 7.3144 | 7.3493 | 0.0349
GEN-2020-072 | 03 - Central | 541320 | CLNTN S2 | 69 | 8.4512 | 8.5052 | 0.054
GEN-2020-072 | 03 - Central | 541335 | WAFBW_SW5 | 161 | 6.7506 | 6.8258 | 0.0752
GEN-2020-072 | 03 - Central | 541336 | WAFBW5 | 161 | 6.1378 | 6.2 | 0.0622
GEN-2020-072 | 03 - Central | 541337 | WAFBE_SW5 | 161 | 6.7795 | 6.8569 | 0.0774
GEN-2020-072 | 03 - Central | 541338 | WAFBE5 | 161 | 6.1653 | 6.2294 | 0.0641
GEN-2020-072 | 03 - Central | 541341 | S.HARP 5 | 161 | 21.2579 | 21.2789 | 0.021
GEN-2020-072 | 03 - Central | 541395 | NUCOR5 | 161 | 7.2991 | 7.4064 | 0.1073
GEN-2020-072 | 03 - Central | 541534 | KNOSTERTP | 69 | 5.0386 | 5.0532 | 0.0146
GEN-2020-072 | 03 - Central | 541535 | LAMONTETP | 69 | 5.2455 | 5.2647 | 0.0192
GEN-2020-072 | 03 - Central | 541536 | LAMONTE | 69 | 5.0812 | 5.0992 | 0.018
GEN-2020-072 | 03 - Central | 542968 | STILWEL7 | 345 | 26.762 | 26.7794 | 0.0174
GEN-2020-072 | 03 - Central | 542969 | STILWEL5 | 161 | 41.6448 | 41.684 | 0.0392
GEN-2020-072 | 03 - Central | 542994 | HICKMAN5 | 161 | 20.1167 | 20.1235 | 0.0068
GEN-2020-072 | 03 - Central | 543050 | ANTIOCH5 | 161 | 23.5016 | 23.5112 | 0.0096
GEN-2020-072 | 03 - Central | 543053 | REDEL 5 | 161 | 25.3253 | 25.3399 | 0.0146
GEN-2020-072 | 03 - Central | 543057 | BUCYRUS5 | 161 | 21.2144 | 21.2232 | 0.0088
GEN-2020-072 | 03 - Central | 543058 | NLOUISB5 | 161 | 9.3677 | 9.3694 | 0.0017
GEN-2020-072 | 03 - Central | 543126 | LACKMAN5 | 161 | 13.9391 | 13.9429 | 0.0038
GEN-2020-072 | 03 - Central | 761271 | GEN-2017-108 | 161 | 7.5022 | 7.5441 | 0.0419
GEN-2020-072 | 03 - Central | 761278 | G17-108-TAP | 161 | 12.2812 | 12.4206 | 0.1394
GEN-2020-072 | 03 - Central | 762988 | GEN-2018-063 | 69 | 7.8734 | 7.9246 | 0.0512
GEN-2020-072 | 03 - Central | 762992 | G18-063-TAP | 69 | 7.9706 | 8.0231 | 0.0525
GEN-2020-072 | 03 - Central | 764345 | GEN-2020-072 | 161 | 7.6415 | 8.514 | 0.8725
GEN-2020-072 | 03 - Central | 764355 | G20-072-TAP | 161 | 7.7277 | 8.5989 | 0.8712
GEN-2020-073 | 03 - Central | 532768 | EMPEC 7 | 345 | 16.8283 | 16.8308 | 0.0025
GEN-2020-073 | 03 - Central | 532774 | SWISVAL7 | 345 | 17.6253 | 17.6348 | 0.0095
GEN-2020-073 | 03 - Central | 532776 | READWF 7 | 345 | 14.066 | 14.0678 | 0.0018
GEN-2020-073 | 03 - Central | 532794 | ROSEHIL7 | 345 | 19.6781 | 19.6793 | 0.0012
GEN-2020-073 | 03 - Central | 532797 | WOLFCRK7 | 345 | 22.1269 | 22.1344 | 0.0075
GEN-2020-073 | 03 - Central | 532799 | WAVERLY7 | 345 | 18.6086 | 18.6143 | 0.0057
GEN-2020-073 | 03 - Central | 532802 | WAVERTX7 | 345 | 15.1849 | 15.1886 | 0.0037
GEN-2020-073 | 03 - Central | 532856 | SWISVAL6 | 230 | 22.5928 | 22.5998 | 0.007
GEN-2020-073 | 03 - Central | 533629 | CC2SHAR2 | 69 | 4.8477 | 4.8477 | 0
GEN-2020-073 | 03 - Central | 533653 | WOLFCRK2 | 69 | 6.2779 | 6.2781 | 0.0002
GEN-2020-073 | 03 - Central | 541198 | PECULR 7 | 345 | 21.2023 | 21.2331 | 0.0308
GEN-2020-073 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2.6785 | 2.6785 | 0
GEN-2020-073 | 03 - Central | 542940 | ATLNTIC7 | 345 | 22.1473 | 22.188 | 0.0407
GEN-2020-073 | 03 - Central | 542945 | CRAIG_CAP 5 | 161 | 35.2535 | 35.3191 | 0.0656
GEN-2020-073 | 03 - Central | 542947 | MERRIAM_CAP5 | 161 | 27.4313 | 27.4602 | 0.0289
GEN-2020-073 | 03 - Central | 542965 | W.GRDNR7 | 345 | 31.0793 | 31.1725 | 0.0932
GEN-2020-073 | 03 - Central | 542966 | WGARDNR5 | 161 | 30.4591 | 30.8153 | 0.3562
GEN-2020-073 | 03 - Central | 542968 | STILWEL7 | 345 | 26.7179 | 26.7794 | 0.0615
GEN-2020-073 | 03 - Central | 542969 | STILWEL5 | 161 | 41.543 | 41.684 | 0.141
GEN-2020-073 | 03 - Central | 542977 | CRAIG 7 | 345 | 22.747 | 22.7852 | 0.0382
GEN-2020-073 | 03 - Central | 542978 | CRAIG 5 | 161 | 44.2872 | 44.3908 | 0.1036
GEN-2020-073 | 03 - Central | 542979 | PFLUMM 5 | 161 | 30.1753 | 30.2201 | 0.0448
GEN-2020-073 | 03 - Central | 542981 | LACYGNE7 | 345 | 28.5844 | 28.609 | 0.0246
GEN-2020-073 | 03 - Central | 543031 | SHWNMSN5 | 161 | 37.1849 | 37.2389 | 0.054
GEN-2020-073 | 03 - Central | 543032 | MERRIAM5 | 161 | 32.6095 | 32.6504 | 0.0409
GEN-2020-073 | 03 - Central | 543037 | QUARRY 5 | 161 | 16.3211 | 16.373 | 0.0519
GEN-2020-073 | 03 - Central | 543038 | LENEXA 5 | 161 | 38.5656 | 38.639 | 0.0734
GEN-2020-073 | 03 - Central | 543041 | SHAWNEE5 | 161 | 27.9177 | 27.9438 | 0.0261
GEN-2020-073 | 03 - Central | 543044 | MOONLT 5 | 161 | 17.9976 | 18.0827 | 0.0851
GEN-2020-073 | 03 - Central | 543048 | COLLEGE5 | 161 | 30.8577 | 30.9182 | 0.0605
GEN-2020-073 | 03 - Central | 543049 | CEDRCRK5 | 161 | 31.2807 | 31.3524 | 0.0717
GEN-2020-073 | 03 - Central | 543054 | CEDARNL5 | 161 | 10.8959 | 10.9412 | 0.0453
GEN-2020-073 | 03 - Central | 543055 | SEOTTWA5 | 161 | 7.4501 | 8.2466 | 0.7965
GEN-2020-073 | 03 - Central | 543056 | GARDNER5 | 161 | 16.7459 | 16.8192 | 0.0733
GEN-2020-073 | 03 - Central | 543065 | CNTRVIL5 | 161 | 6.256 | 6.2884 | 0.0324
GEN-2020-073 | 03 - Central | 543066 | S.OTTWA5 | 161 | 7.4133 | 8.0822 | 0.6689
GEN-2020-073 | 03 - Central | 543067 | CENTENL5 | 161 | 10.691 | 10.8747 | 0.1837
GEN-2020-073 | 03 - Central | 543068 | WAGSTAF5 | 161 | 14.4913 | 14.5945 | 0.1032
GEN-2020-073 | 03 - Central | 543069 | PAOLA 5 | 161 | 10.7397 | 10.9709 | 0.2312
GEN-2020-073 | 03 - Central | 543077 | PLSTVAL5 | 161 | 10.2072 | 10.6971 | 0.4899
GEN-2020-073 | 03 - Central | 543105 | BULLCRK5 | 161 | 29.4613 | 29.7878 | 0.3265
GEN-2020-073 | 03 - Central | 543112 | OSAWAT 5 | 161 | 10.6476 | 10.8742 | 0.2266
GEN-2020-073 | 03 - Central | 543132 | BNSF 5 | 161 | 22.3871 | 22.5528 | 0.1657
GEN-2020-073 | 03 - Central | 543135 | OSAWTM_CAP5 | 161 | 10.0294 | 10.2302 | 0.2008
GEN-2020-073 | 03 - Central | 543166 | NEASTOTTW5 | 161 | 6.4361 | 7.0221 | 0.586
GEN-2020-073 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27.8072 | 27.8304 | 0.0232
GEN-2020-073 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27.8072 | 27.8304 | 0.0232
GEN-2020-073 | 03 - Central | 543650 | DAKOTA_5 | 161 | 7.2016 | 7.2173 | 0.0157
GEN-2020-073 | 03 - Central | 543651 | PRQN_WIND5 | 161 | 6.0935 | 6.1042 | 0.0107
GEN-2020-073 | 03 - Central | 543659 | LACYGNE2 | 69 | 2.8177 | 2.8177 | 0
GEN-2020-073 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 0.6739 | 0.6739 | 0
GEN-2020-073 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 0.6454 | 0.6454 | 0
GEN-2020-073 | 03 - Central | 546742 | METRO 5 | 161 | 27.4553 | 27.4746 | 0.0193
GEN-2020-073 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.664 | 19.6744 | 0.0104
GEN-2020-073 | 03 - Central | 760921 | G17-209-TAP | 345 | 20.1884 | 20.1994 | 0.011
GEN-2020-073 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5.3923 | 5.3931 | 0.0008
GEN-2020-073 | 03 - Central | 762279 | GEN-2017-195 | 345 | 30.9874 | 31.08 | 0.0926
GEN-2020-073 | 03 - Central | 762300 | GEN-2017-196 | 345 | 30.8903 | 30.9823 | 0.092
GEN-2020-073 | 03 - Central | 762405 | ASG-2018-010 | 161 | 3.3146 | 3.3626 | 0.048
GEN-2020-073 | 03 - Central | 762416 | ASG-2018-011 | 161 | 2.9655 | 3.0646 | 0.0991
GEN-2020-073 | 03 - Central | 764375 | GEN-2020-058 | 345 | 22.1023 | 22.1428 | 0.0405
GEN-2020-073 | 03 - Central | 764390 | GEN-2020-073 | 161 | 7.4646 | 8.3928 | 0.9282
GEN-2020-073 | 03 - Central | 764400 | G20-073-TAP | 161 | 7.5469 | 8.4738 | 0.9269
GEN-2020-073 | 03 - Central | 765115 | GEN-2020-057 | 345 | 22.1024 | 22.1429 | 0.0405
GEN-2020-073 | 03 - Central | 765145 | GEN-2020-076 | 345 | 12.5511 | 12.5518 | 0.0007
GEN-2020-073 | 03 - Central | 765155 | G20-076-TAP | 345 | 12.5588 | 12.5595 | 0.0007
GEN-2020-073 | 03 - Central | 765160 | GEN-2020-086 | 345 | 12.5517 | 12.5524 | 0.0007
GEN-2020-073 | 03 - Central | 765175 | GEN-2020-089 | 161 | 4.2593 | 4.2644 | 0.0051
GEN-2020-073 | 03 - Central | 765190 | GEN-2020-090 | 345 | 8.7256 | 8.7262 | 0.0006
GEN-2020-073 | 03 - Central | 765200 | G20-090-TAP | 345 | 9.9523 | 9.9531 | 0.0008
GEN-2020-073 | 03 - Central | 766260 | GEN-2020-007 | 345 | 25.1369 | 25.1555 | 0.0186
GEN-2020-073 | 03 - Central | 766261 | G20-007-TAP | 345 | 27.747 | 27.7699 | 0.0229
GEN-2020-076 | 03 - Central | 300045 | 7MORGAN | 345 | 13.992 | 13.9925 | 0.0005
GEN-2020-076 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 16.1238 | 16.1277 | 0.0039
GEN-2020-076 | 03 - Central | 300740 | 7SPORTSMAN | 345 | 24.62 | 24.6206 | 0.0006
GEN-2020-076 | 03 - Central | 300741 | 5SPORTSMAN | 161 | 40.9345 | 40.935 | 0.0005
GEN-2020-076 | 03 - Central | 300949 | 7JASPER | 345 | 13.0393 | 13.0411 | 0.0018
GEN-2020-076 | 03 - Central | 300950 | 5JASPER | 161 | 13.104 | 13.1047 | 0.0007
GEN-2020-076 | 03 - Central | 512650 | GRDA1 7 | 345 | 26.9821 | 26.9828 | 0.0007
GEN-2020-076 | 03 - Central | 514825 | KAYWIND7 | 345 | 12.6188 | 12.6287 | 0.0099
GEN-2020-076 | 03 - Central | 515543 | RENFROW7 | 345 | 12.282 | 12.2871 | 0.0051
GEN-2020-076 | 03 - Central | 515576 | RANCHRD7 | 345 | 13.5969 | 13.6043 | 0.0074
GEN-2020-076 | 03 - Central | 515621 | OPENSKY7 | 345 | 12.6521 | 12.662 | 0.0099
GEN-2020-076 | 03 - Central | 515646 | GRNTWD 7 | 345 | 10.8893 | 10.8933 | 0.004
GEN-2020-076 | 03 - Central | 515688 | FRNTWND7 | 345 | 10.7735 | 10.7781 | 0.0046
GEN-2020-076 | 03 - Central | 515852 | DGRASSE7 | 345 | 14.6043 | 14.6079 | 0.0036
GEN-2020-076 | 03 - Central | 516066 | FRNT2WD7 | 345 | 10.5462 | 10.5507 | 0.0045
GEN-2020-076 | 03 - Central | 529200 | OMCDLEC7 | 345 | 13.5763 | 13.5837 | 0.0074
GEN-2020-076 | 03 - Central | 532768 | EMPEC 7 | 345 | 16.8268 | 16.8308 | 0.004
GEN-2020-076 | 03 - Central | 532769 | LANG 7 | 345 | 16.6412 | 16.6452 | 0.004
GEN-2020-076 | 03 - Central | 532770 | MORRIS 7 | 345 | 12.9079 | 12.9096 | 0.0017
GEN-2020-076 | 03 - Central | 532771 | RENO 7 | 345 | 11.5917 | 11.6004 | 0.0087
GEN-2020-076 | 03 - Central | 532773 | SUMMIT 7 | 345 | 11.3621 | 11.3648 | 0.0027
GEN-2020-076 | 03 - Central | 532774 | SWISVAL7 | 345 | 17.632 | 17.6348 | 0.0028
GEN-2020-076 | 03 - Central | 532775 | 87TH 7 | 345 | 21.542 | 21.5435 | 0.0015
GEN-2020-076 | 03 - Central | 532776 | READWF 7 | 345 | 14.065 | 14.0678 | 0.0028
GEN-2020-076 | 03 - Central | 532777 | G17-009-TAP | 345 | 12.0639 | 12.069 | 0.0051
GEN-2020-076 | 03 - Central | 532778 | GEN-2017-009 | 345 | 11.1485 | 11.1528 | 0.0043
GEN-2020-076 | 03 - Central | 532780 | CANEYRV7 | 345 | 9.9273 | 9.9404 | 0.0131
GEN-2020-076 | 03 - Central | 532781 | CANEYWF7 | 345 | 9.647 | 9.6594 | 0.0124
GEN-2020-076 | 03 - Central | 532782 | BUFFALO7 | 345 | 21.3118 | 21.3663 | 0.0545
GEN-2020-076 | 03 - Central | 532783 | KINGMAN7 | 345 | 7.1875 | 7.1921 | 0.0046
GEN-2020-076 | 03 - Central | 532784 | NINN1WF7 | 345 | 6.0045 | 6.0075 | 0.003
GEN-2020-076 | 03 - Central | 532785 | PRATTWF7 | 345 | 5.0124 | 5.0145 | 0.0021
GEN-2020-076 | 03 - Central | 532791 | BENTON 7 | 345 | 20.0626 | 20.2629 | 0.2003
GEN-2020-076 | 03 - Central | 532792 | FR2EAST7 | 345 | 7.1009 | 7.1037 | 0.0028
GEN-2020-076 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18.5263 | 18.5326 | 0.0063
GEN-2020-076 | 03 - Central | 532794 | ROSEHIL7 | 345 | 19.5797 | 19.6793 | 0.0996
GEN-2020-076 | 03 - Central | 532795 | FR2WEST7 | 345 | 5.7148 | 5.7166 | 0.0018
GEN-2020-076 | 03 - Central | 532796 | WICHITA7 | 345 | 24.4193 | 24.5073 | 0.088
GEN-2020-076 | 03 - Central | 532797 | WOLFCRK7 | 345 | 22.0782 | 22.1344 | 0.0562
GEN-2020-076 | 03 - Central | 532798 | VIOLA 7 | 345 | 14.3058 | 14.3211 | 0.0153
GEN-2020-076 | 03 - Central | 532799 | WAVERLY7 | 345 | 18.5799 | 18.6143 | 0.0344
GEN-2020-076 | 03 - Central | 532800 | LATHAMS7 | 345 | 10.5845 | 10.6019 | 0.0174
GEN-2020-076 | 03 - Central | 532801 | ELKRVR17 | 345 | 9.3793 | 9.3928 | 0.0135
GEN-2020-076 | 03 - Central | 532802 | WAVERTX7 | 345 | 15.1658 | 15.1886 | 0.0228
GEN-2020-076 | 03 - Central | 532851 | AUBURN 6 | 230 | 13.7395 | 13.7402 | 0.0007
GEN-2020-076 | 03 - Central | 532853 | LAWHILL6 | 230 | 14.1383 | 14.1387 | 0.0004
GEN-2020-076 | 03 - Central | 532854 | LEC U5 6 | 230 | 14.0052 | 14.0056 | 0.0004
GEN-2020-076 | 03 - Central | 532856 | SWISVAL6 | 230 | 22.5975 | 22.5998 | 0.0023
GEN-2020-076 | 03 - Central | 532857 | TECHILL6 | 230 | 11.1785 | 11.179 | 0.0005
GEN-2020-076 | 03 - Central | 532937 | NEOSHO 5 | 161 | 23.9426 | 23.946 | 0.0034
GEN-2020-076 | 03 - Central | 532984 | SUMNER 4 | 138 | 12.6111 | 12.6174 | 0.0063
GEN-2020-076 | 03 - Central | 532986 | BENTON 4 | 138 | 29.0422 | 29.159 | 0.1168
GEN-2020-076 | 03 - Central | 532987 | BUTLER 4 | 138 | 11.3328 | 11.3447 | 0.0119
GEN-2020-076 | 03 - Central | 532988 | BELAIRE4 | 138 | 19.5863 | 19.6358 | 0.0495
GEN-2020-076 | 03 - Central | 532989 | BUTLERS4 | 138 | 11.3255 | 11.3374 | 0.0119
GEN-2020-076 | 03 - Central | 532990 | MIDIAN 4 | 138 | 11.3887 | 11.4017 | 0.013
GEN-2020-076 | 03 - Central | 532991 | WEAVER 4 | 138 | 22.9177 | 22.9679 | 0.0502
GEN-2020-076 | 03 - Central | 532993 | TALLGRS4 | 138 | 10.7972 | 10.8082 | 0.011
GEN-2020-076 | 03 - Central | 532994 | TCBURNS4 | 138 | 4.1517 | 4.1534 | 0.0017
GEN-2020-076 | 03 - Central | 532996 | TIOGA 4 | 138 | 5.7118 | 5.712 | 0.0002
GEN-2020-076 | 03 - Central | 532997 | OTTRCRK4 | 138 | 5.7452 | 5.7465 | 0.0013
GEN-2020-076 | 03 - Central | 533015 | BENTLEY4 | 138 | 11.1005 | 11.1069 | 0.0064
GEN-2020-076 | 03 - Central | 533016 | WWUPLNT4 | 138 | 8.4193 | 8.4231 | 0.0038
GEN-2020-076 | 03 - Central | 533021 | NEOSHO 4 | 138 | 25.5571 | 25.5606 | 0.0035
GEN-2020-076 | 03 - Central | 533024 | 29TH 4 | 138 | 20.2486 | 20.3017 | 0.0531
GEN-2020-076 | 03 - Central | 533026 | ANDOVER4 | 138 | 18.4853 | 18.5212 | 0.0359
GEN-2020-076 | 03 - Central | 533029 | 59TH ST4 | 138 | 17.886 | 17.9079 | 0.0219
GEN-2020-076 | 03 - Central | 533030 | BOEINGE4 | 138 | 17.4571 | 17.4832 | 0.0261
GEN-2020-076 | 03 - Central | 533032 | BU11PON4 | 138 | 15.6223 | 15.6441 | 0.0218
GEN-2020-076 | 03 - Central | 533035 | CHISHLM4 | 138 | 22.1018 | 22.1472 | 0.0454
GEN-2020-076 | 03 - Central | 533036 | CLEARWT4 | 138 | 14.6523 | 14.6633 | 0.011
GEN-2020-076 | 03 - Central | 533037 | COMOTAR4 | 138 | 19.2855 | 19.332 | 0.0465
GEN-2020-076 | 03 - Central | 533039 | ELPASO 4 | 138 | 25.7563 | 25.8094 | 0.0531
GEN-2020-076 | 03 - Central | 533040 | EVANS N4 | 138 | 32.9034 | 32.9669 | 0.0635
GEN-2020-076 | 03 - Central | 533041 | EVANS S4 | 138 | 32.8245 | 32.8877 | 0.0632
GEN-2020-076 | 03 - Central | 533047 | GILL 4 | 138 | 22.5927 | 22.6227 | 0.03
GEN-2020-076 | 03 - Central | 533052 | PARKCTY4 | 138 | 20.8959 | 20.9403 | 0.0444
GEN-2020-076 | 03 - Central | 533053 | LAKERDG4 | 138 | 17.7141 | 17.7334 | 0.0193
GEN-2020-076 | 03 - Central | 533054 | MAIZE 4 | 138 | 21.4948 | 21.5278 | 0.033
GEN-2020-076 | 03 - Central | 533059 | ELPASOE4 | 138 | 25.7128 | 25.7657 | 0.0529
GEN-2020-076 | 03 - Central | 533060 | NOEASTE4 | 138 | 21.2138 | 21.2678 | 0.054
GEN-2020-076 | 03 - Central | 533061 | NOEASTW4 | 138 | 21.1829 | 21.2368 | 0.0539
GEN-2020-076 | 03 - Central | 533062 | ROSEHIL4 | 138 | 32.1816 | 32.2797 | 0.0981
GEN-2020-076 | 03 - Central | 533064 | 17TH 4 | 138 | 18.1915 | 18.2208 | 0.0293
GEN-2020-076 | 03 - Central | 533065 | SG12COL4 | 138 | 19.9491 | 19.9717 | 0.0226
GEN-2020-076 | 03 - Central | 533067 | SPRNGDL4 | 138 | 14.9876 | 15.0083 | 0.0207
GEN-2020-076 | 03 - Central | 533068 | STEARMN4 | 138 | 20.1634 | 20.1982 | 0.0348
GEN-2020-076 | 03 - Central | 533074 | 45TH ST4 | 138 | 24.2813 | 24.3161 | 0.0348
GEN-2020-076 | 03 - Central | 533075 | VIOLA 4 | 138 | 24.9122 | 24.9343 | 0.0221
GEN-2020-076 | 03 - Central | 533413 | CIRCLE 3 | 115 | 19.2269 | 19.2321 | 0.0052
GEN-2020-076 | 03 - Central | 533415 | DAVIS 3 | 115 | 8.4257 | 8.4268 | 0.0011
GEN-2020-076 | 03 - Central | 533416 | RENO 3 | 115 | 23.1947 | 23.2037 | 0.009
GEN-2020-076 | 03 - Central | 533429 | MOUNDRG3 | 115 | 8.8169 | 8.8189 | 0.002
GEN-2020-076 | 03 - Central | 533430 | MNDRGCT3 | 115 | 6.8001 | 6.8013 | 0.0012
GEN-2020-076 | 03 - Central | 533438 | WMCPHER3 | 115 | 11.4231 | 11.4242 | 0.0011
GEN-2020-076 | 03 - Central | 533583 | BUTLERN2 | 69 | 14.3055 | 14.315 | 0.0095
GEN-2020-076 | 03 - Central | 533584 | BU6DEGR2 | 69 | 2.6155 | 2.6158 | 0.0003
GEN-2020-076 | 03 - Central | 533589 | CHESNEY2 | 69 | 9.4623 | 9.4665 | 0.0042
GEN-2020-076 | 03 - Central | 533597 | MIDIANW2 | 69 | 14.6902 | 14.7003 | 0.0101
GEN-2020-076 | 03 - Central | 533599 | PEABODY2 | 69 | 1.819 | 1.8192 | 0.0002
GEN-2020-076 | 03 - Central | 533601 | POTWIN 2 | 69 | 3.7121 | 3.7127 | 0.0006
GEN-2020-076 | 03 - Central | 533603 | THUNBRD2 | 69 | 8.5789 | 8.5823 | 0.0034
GEN-2020-076 | 03 - Central | 533604 | WEAVER 2 | 69 | 12.3901 | 12.3965 | 0.0064
GEN-2020-076 | 03 - Central | 533610 | MIDIANE2 | 69 | 14.6854 | 14.6956 | 0.0102
GEN-2020-076 | 03 - Central | 533624 | BURLING2 | 69 | 3.5604 | 3.5606 | 0.0002
GEN-2020-076 | 03 - Central | 533625 | BURLIND2 | 69 | 3.1728 | 3.173 | 0.0002
GEN-2020-076 | 03 - Central | 533626 | BURLJCT2 | 69 | 5.183 | 5.1833 | 0.0003
GEN-2020-076 | 03 - Central | 533628 | CC1BURL2 | 69 | 3.559 | 3.5591 | 0.0001
GEN-2020-076 | 03 - Central | 533629 | CC2SHAR2 | 69 | 4.8474 | 4.8477 | 0.0003
GEN-2020-076 | 03 - Central | 533630 | CC3WEST2 | 69 | 4.7833 | 4.7836 | 0.0003
GEN-2020-076 | 03 - Central | 533636 | GREEN 2 | 69 | 4.2408 | 4.241 | 0.0002
GEN-2020-076 | 03 - Central | 533653 | WOLFCRK2 | 69 | 6.2775 | 6.2781 | 0.0006
GEN-2020-076 | 03 - Central | 533786 | CHISHLM2 | 69 | 20.5728 | 20.5911 | 0.0183
GEN-2020-076 | 03 - Central | 533823 | NOEASTE2 | 69 | 26.3411 | 26.3769 | 0.0358
GEN-2020-076 | 03 - Central | 539008 | MILAN_GOAB | 138 | 12.1636 | 12.1687 | 0.0051
GEN-2020-076 | 03 - Central | 539009 | CONWAY | 138 | 11.6804 | 11.6848 | 0.0044
GEN-2020-076 | 03 - Central | 539676 | MILAN 4 | 138 | 10.808 | 10.812 | 0.004
GEN-2020-076 | 03 - Central | 539800 | CLARKCOUNTY7 | 345 | 13.4145 | 13.4165 | 0.002
GEN-2020-076 | 03 - Central | 539801 | THISTLE7 | 345 | 16.8871 | 16.8981 | 0.011
GEN-2020-076 | 03 - Central | 539804 | THISTLE4 | 138 | 18.2026 | 18.2076 | 0.005
GEN-2020-076 | 03 - Central | 539813 | TRANSFORMER | 345 | 11.2111 | 11.2125 | 0.0014
GEN-2020-076 | 03 - Central | 539840 | GEN-2011-008 | 345 | 11.0814 | 11.0827 | 0.0013
GEN-2020-076 | 03 - Central | 539841 | G-2011-008-1 | 345 | 11.0814 | 11.0827 | 0.0013
GEN-2020-076 | 03 - Central | 539855 | G-2011-008-2 | 345 | 9.2746 | 9.2755 | 0.0009
GEN-2020-076 | 03 - Central | 539857 | G-2011-008-3 | 345 | 8.6832 | 8.684 | 0.0008
GEN-2020-076 | 03 - Central | 541198 | PECULR 7 | 345 | 21.2311 | 21.2331 | 0.002
GEN-2020-076 | 03 - Central | 541200 | PHILL 7 | 345 | 19.1434 | 19.1445 | 0.0011
GEN-2020-076 | 03 - Central | 541341 | S.HARP 5 | 161 | 21.2783 | 21.2789 | 0.0006
GEN-2020-076 | 03 - Central | 541342 | PECULR 5 | 161 | 23.4208 | 23.4216 | 0.0008
GEN-2020-076 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2.6785 | 2.6785 | 0
GEN-2020-076 | 03 - Central | 542940 | ATLNTIC7 | 345 | 22.1846 | 22.188 | 0.0034
GEN-2020-076 | 03 - Central | 542945 | CRAIG_CAP 5 | 161 | 35.3175 | 35.3191 | 0.0016
GEN-2020-076 | 03 - Central | 542965 | W.GRDNR7 | 345 | 31.1627 | 31.1725 | 0.0098
GEN-2020-076 | 03 - Central | 542966 | WGARDNR5 | 161 | 30.8134 | 30.8153 | 0.0019
GEN-2020-076 | 03 - Central | 542968 | STILWEL7 | 345 | 26.775 | 26.7794 | 0.0044
GEN-2020-076 | 03 - Central | 542969 | STILWEL5 | 161 | 41.6808 | 41.684 | 0.0032
GEN-2020-076 | 03 - Central | 542977 | CRAIG 7 | 345 | 22.7833 | 22.7852 | 0.0019
GEN-2020-076 | 03 - Central | 542978 | CRAIG 5 | 161 | 44.3882 | 44.3908 | 0.0026
GEN-2020-076 | 03 - Central | 542981 | LACYGNE7 | 345 | 28.5998 | 28.609 | 0.0092
GEN-2020-076 | 03 - Central | 542994 | HICKMAN5 | 161 | 20.123 | 20.1235 | 0.0005
GEN-2020-076 | 03 - Central | 543031 | SHWNMSN5 | 161 | 37.2376 | 37.2389 | 0.0013
GEN-2020-076 | 03 - Central | 543044 | MOONLT 5 | 161 | 18.0821 | 18.0827 | 0.0006
GEN-2020-076 | 03 - Central | 543049 | CEDRCRK5 | 161 | 31.351 | 31.3524 | 0.0014
GEN-2020-076 | 03 - Central | 543050 | ANTIOCH5 | 161 | 23.5103 | 23.5112 | 0.0009
GEN-2020-076 | 03 - Central | 543053 | REDEL 5 | 161 | 25.339 | 25.3399 | 0.0009
GEN-2020-076 | 03 - Central | 543054 | CEDARNL5 | 161 | 10.941 | 10.9412 | 0.0002
GEN-2020-076 | 03 - Central | 543056 | GARDNER5 | 161 | 16.8187 | 16.8192 | 0.0005
GEN-2020-076 | 03 - Central | 543057 | BUCYRUS5 | 161 | 21.2225 | 21.2232 | 0.0007
GEN-2020-076 | 03 - Central | 543058 | NLOUISB5 | 161 | 9.3692 | 9.3694 | 0.0002
GEN-2020-076 | 03 - Central | 543077 | PLSTVAL5 | 161 | 10.6969 | 10.6971 | 0.0002
GEN-2020-076 | 03 - Central | 543105 | BULLCRK5 | 161 | 29.7861 | 29.7878 | 0.0017
GEN-2020-076 | 03 - Central | 543126 | LACKMAN5 | 161 | 13.9426 | 13.9429 | 0.0003
GEN-2020-076 | 03 - Central | 543132 | BNSF 5 | 161 | 22.5518 | 22.5528 | 0.001
GEN-2020-076 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27.8218 | 27.8304 | 0.0086
GEN-2020-076 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27.8218 | 27.8304 | 0.0086
GEN-2020-076 | 03 - Central | 543659 | LACYGNE2 | 69 | 2.8177 | 2.8177 | 0
GEN-2020-076 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 0.6739 | 0.6739 | 0
GEN-2020-076 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 0.6454 | 0.6454 | 0
GEN-2020-076 | 03 - Central | 560053 | G15-052T | 345 | 13.4402 | 13.4639 | 0.0237
GEN-2020-076 | 03 - Central | 562476 | G14-001-TAP | 345 | 10.8331 | 10.8417 | 0.0086
GEN-2020-076 | 03 - Central | 578530 | FR3HV | 345 | 5.2477 | 5.2491 | 0.0014
GEN-2020-076 | 03 - Central | 583850 | GEN-2014-001 | 345 | 7.3035 | 7.3073 | 0.0038
GEN-2020-076 | 03 - Central | 584900 | GEN-2015-052 | 345 | 13.3903 | 13.4138 | 0.0235
GEN-2020-076 | 03 - Central | 587500 | GEN-2016-073 | 345 | 15.7268 | 15.756 | 0.0292
GEN-2020-076 | 03 - Central | 587880 | GEN-2016-111 | 345 | 6.8043 | 6.8062 | 0.0019
GEN-2020-076 | 03 - Central | 587884 | G16-111-TAP | 345 | 10.2166 | 10.2212 | 0.0046
GEN-2020-076 | 03 - Central | 588360 | GEN-2016-153 | 345 | 7.467 | 7.4702 | 0.0032
GEN-2020-076 | 03 - Central | 588364 | G16-153-TAP | 345 | 7.8289 | 7.8325 | 0.0036
GEN-2020-076 | 03 - Central | 588630 | GEN-2017-018 | 345 | 16.8871 | 16.8981 | 0.011
GEN-2020-076 | 03 - Central | 589060 | GEN-2017-068 | 138 | 29.885 | 29.9372 | 0.0522
GEN-2020-076 | 03 - Central | 589240 | GEN-2017-086 | 345 | 6.5467 | 6.5492 | 0.0025
GEN-2020-076 | 03 - Central | 709500 | GI-95_POI | 345 | 8.3442 | 8.3444 | 0.0002
GEN-2020-076 | 03 - Central | 709501 | GI-95_HV | 345 | 8.3442 | 8.3444 | 0.0002
GEN-2020-076 | 03 - Central | 760284 | GEN-2017-220 | 345 | 21.198 | 21.2519 | 0.0539
GEN-2020-076 | 03 - Central | 760641 | GEN-2017-226 | 138 | 32.7261 | 32.7889 | 0.0628
GEN-2020-076 | 03 - Central | 760809 | GEN-2017-203 | 345 | 8.7657 | 8.7684 | 0.0027
GEN-2020-076 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.67 | 19.6744 | 0.0044
GEN-2020-076 | 03 - Central | 760921 | G17-209-TAP | 345 | 20.1947 | 20.1994 | 0.0047
GEN-2020-076 | 03 - Central | 761271 | GEN-2017-108 | 161 | 7.5441 | 7.5441 | 0
GEN-2020-076 | 03 - Central | 761278 | G17-108-TAP | 161 | 12.4205 | 12.4206 | 0.0001
GEN-2020-076 | 03 - Central | 761838 | GEN-2017-121 | 138 | 9.5084 | 9.5118 | 0.0034
GEN-2020-076 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5.3928 | 5.3931 | 0.0003
GEN-2020-076 | 03 - Central | 762279 | GEN-2017-195 | 345 | 31.0702 | 31.08 | 0.0098
GEN-2020-076 | 03 - Central | 762300 | GEN-2017-196 | 345 | 30.9726 | 30.9823 | 0.0097
GEN-2020-076 | 03 - Central | 762405 | ASG-2018-010 | 161 | 3.3626 | 3.3626 | 0
GEN-2020-076 | 03 - Central | 762680 | GEN-2018-032 | 345 | 12.1398 | 12.1425 | 0.0027
GEN-2020-076 | 03 - Central | 762834 | GEN-2018-049 | 345 | 7.1998 | 7.2017 | 0.0019
GEN-2020-076 | 03 - Central | 762922 | GEN-2018-057 | 138 | 17.8198 | 17.8374 | 0.0176
GEN-2020-076 | 03 - Central | 763065 | GEN-2018-071 | 345 | 13.1456 | 13.1526 | 0.007
GEN-2020-076 | 03 - Central | 763069 | G18-071_TAP | 345 | 13.1952 | 13.2022 | 0.007
GEN-2020-076 | 03 - Central | 763417 | GEN-2018-128 | 345 | 11.0373 | 11.0428 | 0.0055
GEN-2020-076 | 03 - Central | 763421 | G18-128-TAP | 345 | 12.1355 | 12.1422 | 0.0067
GEN-2020-076 | 03 - Central | 763890 | GEN-2019-058 | 345 | 13.1432 | 13.1452 | 0.002
GEN-2020-076 | 03 - Central | 764375 | GEN-2020-058 | 345 | 22.1394 | 22.1428 | 0.0034
GEN-2020-076 | 03 - Central | 764390 | GEN-2020-073 | 161 | 8.3927 | 8.3928 | 0.0001
GEN-2020-076 | 03 - Central | 764400 | G20-073-TAP | 161 | 8.4738 | 8.4738 | 0
GEN-2020-076 | 03 - Central | 765100 | GEN-2020-052 | 345 | 9.9267 | 9.928 | 0.0013
GEN-2020-076 | 03 - Central | 765110 | G20-052-TAP | 345 | 13.1163 | 13.1185 | 0.0022
GEN-2020-076 | 03 - Central | 765115 | GEN-2020-057 | 345 | 22.1395 | 22.1429 | 0.0034
GEN-2020-076 | 03 - Central | 765130 | GEN-2020-071 | 230 | 11.3785 | 11.3791 | 0.0006
GEN-2020-076 | 03 - Central | 765140 | G20-071-TAP | 230 | 11.3785 | 11.3791 | 0.0006
GEN-2020-076 | 03 - Central | 765145 | GEN-2020-076 | 345 | 12.2391 | 12.5518 | 0.3127
GEN-2020-076 | 03 - Central | 765155 | G20-076-TAP | 345 | 12.2468 | 12.5595 | 0.3127
GEN-2020-076 | 03 - Central | 765160 | GEN-2020-086 | 345 | 12.2401 | 12.5524 | 0.3123
GEN-2020-076 | 03 - Central | 765190 | GEN-2020-090 | 345 | 8.7232 | 8.7262 | 0.003
GEN-2020-076 | 03 - Central | 765200 | G20-090-TAP | 345 | 9.9491 | 9.9531 | 0.004
GEN-2020-076 | 03 - Central | 766260 | GEN-2020-007 | 345 | 25.1482 | 25.1555 | 0.0073
GEN-2020-076 | 03 - Central | 766261 | G20-007-TAP | 345 | 27.761 | 27.7699 | 0.0089
GEN-2020-079 | 03 - Central | 300045 | 7MORGAN | 345 | 13.9852 | 13.9925 | 0.0073
GEN-2020-079 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 16.1072 | 16.1277 | 0.0205
GEN-2020-079 | 03 - Central | 300740 | 7SPORTSMAN | 345 | 24.611 | 24.6206 | 0.0096
GEN-2020-079 | 03 - Central | 300741 | 5SPORTSMAN | 161 | 40.9258 | 40.935 | 0.0092
GEN-2020-079 | 03 - Central | 300949 | 7JASPER | 345 | 13.0297 | 13.0411 | 0.0114
GEN-2020-079 | 03 - Central | 300950 | 5JASPER | 161 | 13.0991 | 13.1047 | 0.0056
GEN-2020-079 | 03 - Central | 505486 | NEO SPA5 | 161 | 15.7079 | 15.8028 | 0.0949
GEN-2020-079 | 03 - Central | 505488 | CARTHAG5 | 161 | 16.7852 | 16.9087 | 0.1235
GEN-2020-079 | 03 - Central | 510379 | DELWARE4 | 138 | 11.5206 | 11.5244 | 0.0038
GEN-2020-079 | 03 - Central | 510380 | DELWARE7 | 345 | 12.2114 | 12.2209 | 0.0095
GEN-2020-079 | 03 - Central | 510406 | N.E.S.-7 | 345 | 19.4217 | 19.4283 | 0.0066
GEN-2020-079 | 03 - Central | 510417 | VINTAJC4 | 138 | 5.2245 | 5.231 | 0.0065
GEN-2020-079 | 03 - Central | 512630 | MIAMI 2 | 69 | 12.4589 | 12.4993 | 0.0404
GEN-2020-079 | 03 - Central | 512631 | MIAMI 5 | 161 | 9.6121 | 9.6789 | 0.0668
GEN-2020-079 | 03 - Central | 512632 | AFTON 5 | 161 | 8.5488 | 8.5761 | 0.0273
GEN-2020-079 | 03 - Central | 512650 | GRDA1 7 | 345 | 26.9716 | 26.9828 | 0.0112
GEN-2020-079 | 03 - Central | 513020 | MIAMI1 2 | 69 | 10.6677 | 10.6974 | 0.0297
GEN-2020-079 | 03 - Central | 513022 | MIAMI4 2 | 69 | 9.0786 | 9.1001 | 0.0215
GEN-2020-079 | 03 - Central | 513026 | COMMTP 2 | 69 | 9.5226 | 9.5463 | 0.0237
GEN-2020-079 | 03 - Central | 532777 | G17-009-TAP | 345 | 12.0482 | 12.069 | 0.0208
GEN-2020-079 | 03 - Central | 532778 | GEN-2017-009 | 345 | 11.1351 | 11.1528 | 0.0177
GEN-2020-079 | 03 - Central | 532780 | CANEYRV7 | 345 | 9.9364 | 9.9404 | 0.004
GEN-2020-079 | 03 - Central | 532781 | CANEYWF7 | 345 | 9.6556 | 9.6594 | 0.0038
GEN-2020-079 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18.465 | 18.5326 | 0.0676
GEN-2020-079 | 03 - Central | 532797 | WOLFCRK7 | 345 | 22.1308 | 22.1344 | 0.0036
GEN-2020-079 | 03 - Central | 532800 | LATHAMS7 | 345 | 10.5983 | 10.6019 | 0.0036
GEN-2020-079 | 03 - Central | 532801 | ELKRVR17 | 345 | 9.39 | 9.3928 | 0.0028
GEN-2020-079 | 03 - Central | 532926 | BAKER 2 | 69 | 5.1247 | 5.1286 | 0.0039
GEN-2020-079 | 03 - Central | 532934 | MARMTNE5 | 161 | 8.3992 | 8.411 | 0.0118
GEN-2020-079 | 03 - Central | 532935 | MARMTNW5 | 161 | 8.3954 | 8.4072 | 0.0118
GEN-2020-079 | 03 - Central | 532937 | NEOSHO 5 | 161 | 23.7196 | 23.946 | 0.2264
GEN-2020-079 | 03 - Central | 532938 | FRANKLIN5 | 161 | 7.9967 | 8.0194 | 0.0227
GEN-2020-079 | 03 - Central | 533002 | DEARING4 | 138 | 9.6161 | 9.6218 | 0.0057
GEN-2020-079 | 03 - Central | 533003 | LIBERTY4 | 138 | 7.6134 | 7.6188 | 0.0054
GEN-2020-079 | 03 - Central | 533005 | NEPARSN4 | 138 | 13.1207 | 13.1555 | 0.0348
GEN-2020-079 | 03 - Central | 533008 | TV1MNDV4 | 138 | 7.2607 | 7.2674 | 0.0067
GEN-2020-079 | 03 - Central | 533020 | NEOSHOS4 | 138 | 25.3534 | 25.5172 | 0.1638
GEN-2020-079 | 03 - Central | 533021 | NEOSHO 4 | 138 | 25.3966 | 25.5606 | 0.164
GEN-2020-079 | 03 - Central | 533022 | NEOSHON4 | 138 | 25.2779 | 25.4402 | 0.1623
GEN-2020-079 | 03 - Central | 533639 | MARMATN2 | 69 | 9.0282 | 9.0332 | 0.005
GEN-2020-079 | 03 - Central | 533640 | MCKEE 2 | 69 | 4.3631 | 4.3646 | 0.0015
GEN-2020-079 | 03 - Central | 533645 | SE9HIAT2 | 69 | 3.8769 | 3.8781 | 0.0012
GEN-2020-079 | 03 - Central | 533647 | UN1ELSM2 | 69 | 8.1234 | 8.1272 | 0.0038
GEN-2020-079 | 03 - Central | 533650 | UN8HUMB2 | 69 | 4.5621 | 4.5629 | 0.0008
GEN-2020-079 | 03 - Central | 533654 | ZILAJCT2 | 69 | 6.4852 | 6.4868 | 0.0016
GEN-2020-079 | 03 - Central | 533695 | LABETTE2 | 69 | 4.2182 | 4.2203 | 0.0021
GEN-2020-079 | 03 - Central | 533696 | LABETTS2 | 69 | 6.3941 | 6.3991 | 0.005
GEN-2020-079 | 03 - Central | 533697 | LIBERT-2 | 69 | 8.7169 | 8.72 | 0.0031
GEN-2020-079 | 03 - Central | 533702 | ORDNCE 2 | 69 | 6.3281 | 6.333 | 0.0049
GEN-2020-079 | 03 - Central | 533703 | ORDNJCT2 | 69 | 8.7636 | 8.7733 | 0.0097
GEN-2020-079 | 03 - Central | 533704 | PARSONS2 | 69 | 5.0874 | 5.0906 | 0.0032
GEN-2020-079 | 03 - Central | 533758 | CRAWFOR2 | 69 | 7.5652 | 7.5728 | 0.0076
GEN-2020-079 | 03 - Central | 533763 | HUDSON-2 | 69 | 4.8012 | 4.8048 | 0.0036
GEN-2020-079 | 03 - Central | 533768 | NEOSHON2 | 69 | 23.9714 | 24.0451 | 0.0737
GEN-2020-079 | 03 - Central | 533772 | SE1GREE2 | 69 | 6.3079 | 6.3132 | 0.0053
GEN-2020-079 | 03 - Central | 533773 | SOPITT 2 | 69 | 5.7417 | 5.7467 | 0.005
GEN-2020-079 | 03 - Central | 533778 | NEOSHOS2 | 69 | 23.9963 | 24.0702 | 0.0739
GEN-2020-079 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2.6785 | 2.6785 | 0
GEN-2020-079 | 03 - Central | 542965 | W.GRDNR7 | 345 | 31.17 | 31.1725 | 0.0025
GEN-2020-079 | 03 - Central | 542968 | STILWEL7 | 345 | 26.7773 | 26.7794 | 0.0021
GEN-2020-079 | 03 - Central | 542981 | LACYGNE7 | 345 | 28.6033 | 28.609 | 0.0057
GEN-2020-079 | 03 - Central | 543065 | CNTRVIL5 | 161 | 6.2864 | 6.2884 | 0.002
GEN-2020-079 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27.825 | 27.8304 | 0.0054
GEN-2020-079 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27.825 | 27.8304 | 0.0054
GEN-2020-079 | 03 - Central | 543650 | DAKOTA_5 | 161 | 7.2118 | 7.2173 | 0.0055
GEN-2020-079 | 03 - Central | 543651 | PRQN_WIND5 | 161 | 6.1005 | 6.1042 | 0.0037
GEN-2020-079 | 03 - Central | 543659 | LACYGNE2 | 69 | 2.8177 | 2.8177 | 0
GEN-2020-079 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 0.6739 | 0.6739 | 0
GEN-2020-079 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 0.6454 | 0.6454 | 0
GEN-2020-079 | 03 - Central | 547409 | SCAM66 2 | 69 | 2.5485 | 2.5514 | 0.0029
GEN-2020-079 | 03 - Central | 547411 | COL282 2 | 69 | 4.6877 | 4.6981 | 0.0104
GEN-2020-079 | 03 - Central | 547412 | SEK225T2 | 69 | 3.6134 | 3.6193 | 0.0059
GEN-2020-079 | 03 - Central | 547413 | SEK225 2 | 69 | 3.5664 | 3.5722 | 0.0058
GEN-2020-079 | 03 - Central | 547414 | SMN425 2 | 69 | 2.0343 | 2.0362 | 0.0019
GEN-2020-079 | 03 - Central | 547415 | SHR444 2 | 69 | 2.8044 | 2.8078 | 0.0034
GEN-2020-079 | 03 - Central | 547416 | CHE299T2 | 69 | 1.9067 | 1.9082 | 0.0015
GEN-2020-079 | 03 - Central | 547417 | CHE299 2 | 69 | 1.8263 | 1.8277 | 0.0014
GEN-2020-079 | 03 - Central | 547418 | CHE300 2 | 69 | 1.8677 | 1.8692 | 0.0015
GEN-2020-079 | 03 - Central | 547419 | TWN388 2 | 69 | 1.8145 | 1.8159 | 0.0014
GEN-2020-079 | 03 - Central | 547420 | WEL186 2 | 69 | 1.1672 | 1.1677 | 0.0005
GEN-2020-079 | 03 - Central | 547431 | WEB105 2 | 69 | 8.1093 | 8.1295 | 0.0202
GEN-2020-079 | 03 - Central | 547438 | EXP449T2 | 69 | 9.0829 | 9.107 | 0.0241
GEN-2020-079 | 03 - Central | 547439 | EXP4492 | 69 | 7.5374 | 7.5539 | 0.0165
GEN-2020-079 | 03 - Central | 547455 | SCM66T 2 | 69 | 4.5118 | 4.5211 | 0.0093
GEN-2020-079 | 03 - Central | 547459 | WWR477 | 161 | 21.8607 | 22.2791 | 0.4184
GEN-2020-079 | 03 - Central | 547462 | SVRCK469 5 | 161 | 14.2817 | 14.4236 | 0.1419
GEN-2020-079 | 03 - Central | 547466 | ATL109 5 | 161 | 16.3705 | 16.5632 | 0.1927
GEN-2020-079 | 03 - Central | 547467 | ORO110 5 | 161 | 19.7237 | 20.0777 | 0.354
GEN-2020-079 | 03 - Central | 547469 | RIV4525 | 161 | 23.8141 | 24.8094 | 0.9953
GEN-2020-079 | 03 - Central | 547470 | JOP145 5 | 161 | 18.833 | 19.1474 | 0.3144
GEN-2020-079 | 03 - Central | 547472 | TIP292 5 | 161 | 17.5997 | 17.777 | 0.1773
GEN-2020-079 | 03 - Central | 547476 | ASB349 5 | 161 | 11.2541 | 11.3142 | 0.0601
GEN-2020-079 | 03 - Central | 547477 | CJ 366 5 | 161 | 12.5922 | 12.7105 | 0.1183
GEN-2020-079 | 03 - Central | 547480 | MON383 5 | 161 | 12.1804 | 12.2093 | 0.0289
GEN-2020-079 | 03 - Central | 547483 | JOP389 5 | 161 | 19.7971 | 20.0887 | 0.2916
GEN-2020-079 | 03 - Central | 547486 | HOC404 4 | 138 | 6.7277 | 6.7604 | 0.0327
GEN-2020-079 | 03 - Central | 547487 | HOC404 5 | 161 | 13.3837 | 13.5889 | 0.2052
GEN-2020-079 | 03 - Central | 547490 | FIR417 5 | 161 | 14.4762 | 14.6466 | 0.1704
GEN-2020-079 | 03 - Central | 547494 | OAK432 5 | 161 | 17.9165 | 18.1868 | 0.2703
GEN-2020-079 | 03 - Central | 547498 | STL439 5 | 161 | 23.8483 | 24.3471 | 0.4988
GEN-2020-079 | 03 - Central | 547500 | RNM393 5 | 161 | 14.3602 | 14.4879 | 0.1277
GEN-2020-079 | 03 - Central | 547501 | RIV453 5 | 161 | 22.5354 | 23.3993 | 0.8639
GEN-2020-079 | 03 - Central | 547502 | RIV167 5 | 161 | 22.1199 | 22.968 | 0.8481
GEN-2020-079 | 03 - Central | 547503 | RIV452T 5 | 161 | 23.385 | 24.335 | 0.95
GEN-2020-079 | 03 - Central | 547525 | JOP 59 2 | 69 | 19.8261 | 19.9658 | 0.1397
GEN-2020-079 | 03 - Central | 547526 | JOP 64 2 | 69 | 19.4693 | 19.6039 | 0.1346
GEN-2020-079 | 03 - Central | 547527 | WEB436 2 | 69 | 9.6753 | 9.7038 | 0.0285
GEN-2020-079 | 03 - Central | 547530 | COL 94 2 | 69 | 6.5695 | 6.5895 | 0.02
GEN-2020-079 | 03 - Central | 547532 | CAR108 2 | 69 | 8.4934 | 8.5107 | 0.0173
GEN-2020-079 | 03 - Central | 547533 | ATL109 2 | 69 | 21.0358 | 21.1739 | 0.1381
GEN-2020-079 | 03 - Central | 547534 | ORO110 2 | 69 | 18.1544 | 18.2668 | 0.1124
GEN-2020-079 | 03 - Central | 547539 | JOP145 2 | 69 | 21.0979 | 21.2624 | 0.1645
GEN-2020-079 | 03 - Central | 547541 | RIV167 2 | 69 | 17.8254 | 17.9864 | 0.161
GEN-2020-079 | 03 - Central | 547551 | GAT258 2 | 69 | 14.6099 | 14.6783 | 0.0684
GEN-2020-079 | 03 - Central | 547554 | BAX271 2 | 69 | 9.6643 | 9.7076 | 0.0433
GEN-2020-079 | 03 - Central | 547555 | GAL278 2 | 69 | 13.2592 | 13.329 | 0.0698
GEN-2020-079 | 03 - Central | 547556 | OAK280 2 | 69 | 16.0941 | 16.1797 | 0.0856
GEN-2020-079 | 03 - Central | 547557 | JOP284 2 | 69 | 16.8702 | 16.9696 | 0.0994
GEN-2020-079 | 03 - Central | 547574 | JOP341 2 | 69 | 18.3002 | 18.4213 | 0.1211
GEN-2020-079 | 03 - Central | 547590 | QUA377 2 | 69 | 7.3279 | 7.3504 | 0.0225
GEN-2020-079 | 03 - Central | 547592 | JOP389 2 | 69 | 15.4988 | 15.5762 | 0.0774
GEN-2020-079 | 03 - Central | 547601 | HOC404 2 | 69 | 9.7833 | 9.8264 | 0.0431
GEN-2020-079 | 03 - Central | 547602 | RIV406 2 | 69 | 15.8377 | 15.9643 | 0.1266
GEN-2020-079 | 03 - Central | 547607 | JOP422 5 | 161 | 13.3043 | 13.4218 | 0.1175
GEN-2020-079 | 03 - Central | 547608 | JOP430 2 | 69 | 16.0023 | 16.0904 | 0.0881
GEN-2020-079 | 03 - Central | 547685 | PLB447 2 | 69 | 14.566 | 14.6328 | 0.0668
GEN-2020-079 | 03 - Central | 547690 | GLF339 2 | 69 | 12.0564 | 12.1232 | 0.0668
GEN-2020-079 | 03 - Central | 547728 | GAL278T | 69 | 13.5498 | 13.6227 | 0.0729
GEN-2020-079 | 03 - Central | 547729 | BAX488 5 | 161 | 14.9773 | 15.2752 | 0.2979
GEN-2020-079 | 03 - Central | 588500 | GEN-2017-005 | 161 | 6.9618 | 6.9722 | 0.0104
GEN-2020-079 | 03 - Central | 588504 | G17-005-TAP | 161 | 7.0469 | 7.0576 | 0.0107
GEN-2020-079 | 03 - Central | 588660 | GEN-2017-022 | 138 | 8.9095 | 8.917 | 0.0075
GEN-2020-079 | 03 - Central | 588664 | G17-022-TAP | 138 | 9.2763 | 9.2844 | 0.0081
GEN-2020-079 | 03 - Central | 589200 | GEN-2017-082 | 161 | 7.6539 | 7.6802 | 0.0263
GEN-2020-079 | 03 - Central | 709500 | GI-95_POI | 345 | 8.3419 | 8.3444 | 0.0025
GEN-2020-079 | 03 - Central | 709501 | GI-95_HV | 345 | 8.3419 | 8.3444 | 0.0025
GEN-2020-079 | 03 - Central | 760242 | GEN-2017-188 | 161 | 2.0287 | 2.0299 | 0.0012
GEN-2020-079 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.6693 | 19.6744 | 0.0051
GEN-2020-079 | 03 - Central | 760921 | G17-209-TAP | 345 | 20.194 | 20.1994 | 0.0054
GEN-2020-079 | 03 - Central | 762279 | GEN-2017-195 | 345 | 31.0775 | 31.08 | 0.0025
GEN-2020-079 | 03 - Central | 762300 | GEN-2017-196 | 345 | 30.9798 | 30.9823 | 0.0025
GEN-2020-079 | 03 - Central | 762680 | GEN-2018-032 | 345 | 12.1134 | 12.1425 | 0.0291
GEN-2020-079 | 03 - Central | 764300 | GEN-2020-079 | 161 | 13.9911 | 15.4113 | 1.4202
GEN-2020-079 | 03 - Central | 764310 | G20-079-TAP | 161 | 17.2128 | 18.6071 | 1.3943
GEN-2020-079 | 03 - Central | 765100 | GEN-2020-052 | 345 | 9.9147 | 9.928 | 0.0133
GEN-2020-079 | 03 - Central | 765110 | G20-052-TAP | 345 | 13.0949 | 13.1185 | 0.0236
GEN-2020-079 | 03 - Central | 765175 | GEN-2020-089 | 161 | 4.2626 | 4.2644 | 0.0018
GEN-2020-079 | 03 - Central | 765190 | GEN-2020-090 | 345 | 8.7231 | 8.7262 | 0.0031
GEN-2020-079 | 03 - Central | 765200 | G20-090-TAP | 345 | 9.949 | 9.9531 | 0.0041
GEN-2020-079 | 03 - Central | 766260 | GEN-2020-007 | 345 | 25.1511 | 25.1555 | 0.0044
GEN-2020-079 | 03 - Central | 766261 | G20-007-TAP | 345 | 27.7645 | 27.7699 | 0.0054
GEN-2020-086 | 03 - Central | 300045 | 7MORGAN | 345 | 13.9919 | 13.9925 | 0.0006
GEN-2020-086 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 16.1226 | 16.1277 | 0.0051
GEN-2020-086 | 03 - Central | 300740 | 7SPORTSMAN | 345 | 24.6198 | 24.6206 | 0.0008
GEN-2020-086 | 03 - Central | 300741 | 5SPORTSMAN | 161 | 40.9344 | 40.935 | 0.0006
GEN-2020-086 | 03 - Central | 300949 | 7JASPER | 345 | 13.0388 | 13.0411 | 0.0023
GEN-2020-086 | 03 - Central | 300950 | 5JASPER | 161 | 13.1038 | 13.1047 | 0.0009
GEN-2020-086 | 03 - Central | 512650 | GRDA1 7 | 345 | 26.9819 | 26.9828 | 0.0009
GEN-2020-086 | 03 - Central | 514825 | KAYWIND7 | 345 | 12.6161 | 12.6287 | 0.0126
GEN-2020-086 | 03 - Central | 515543 | RENFROW7 | 345 | 12.2806 | 12.2871 | 0.0065
GEN-2020-086 | 03 - Central | 515576 | RANCHRD7 | 345 | 13.5948 | 13.6043 | 0.0095
GEN-2020-086 | 03 - Central | 515621 | OPENSKY7 | 345 | 12.6493 | 12.662 | 0.0127
GEN-2020-086 | 03 - Central | 515646 | GRNTWD 7 | 345 | 10.8882 | 10.8933 | 0.0051
GEN-2020-086 | 03 - Central | 515688 | FRNTWND7 | 345 | 10.7722 | 10.7781 | 0.0059
GEN-2020-086 | 03 - Central | 515852 | DGRASSE7 | 345 | 14.6033 | 14.6079 | 0.0046
GEN-2020-086 | 03 - Central | 516066 | FRNT2WD7 | 345 | 10.545 | 10.5507 | 0.0057
GEN-2020-086 | 03 - Central | 529200 | OMCDLEC7 | 345 | 13.5742 | 13.5837 | 0.0095
GEN-2020-086 | 03 - Central | 532768 | EMPEC 7 | 345 | 16.8256 | 16.8308 | 0.0052
GEN-2020-086 | 03 - Central | 532769 | LANG 7 | 345 | 16.64 | 16.6452 | 0.0052
GEN-2020-086 | 03 - Central | 532770 | MORRIS 7 | 345 | 12.9075 | 12.9096 | 0.0021
GEN-2020-086 | 03 - Central | 532771 | RENO 7 | 345 | 11.5893 | 11.6004 | 0.0111
GEN-2020-086 | 03 - Central | 532773 | SUMMIT 7 | 345 | 11.3614 | 11.3648 | 0.0034
GEN-2020-086 | 03 - Central | 532774 | SWISVAL7 | 345 | 17.6312 | 17.6348 | 0.0036
GEN-2020-086 | 03 - Central | 532775 | 87TH 7 | 345 | 21.5416 | 21.5435 | 0.0019
GEN-2020-086 | 03 - Central | 532776 | READWF 7 | 345 | 14.0642 | 14.0678 | 0.0036
GEN-2020-086 | 03 - Central | 532777 | G17-009-TAP | 345 | 12.0625 | 12.069 | 0.0065
GEN-2020-086 | 03 - Central | 532778 | GEN-2017-009 | 345 | 11.1473 | 11.1528 | 0.0055
GEN-2020-086 | 03 - Central | 532780 | CANEYRV7 | 345 | 9.9236 | 9.9404 | 0.0168
GEN-2020-086 | 03 - Central | 532781 | CANEYWF7 | 345 | 9.6436 | 9.6594 | 0.0158
GEN-2020-086 | 03 - Central | 532782 | BUFFALO7 | 345 | 21.2966 | 21.3663 | 0.0697
GEN-2020-086 | 03 - Central | 532783 | KINGMAN7 | 345 | 7.1862 | 7.1921 | 0.0059
GEN-2020-086 | 03 - Central | 532784 | NINN1WF7 | 345 | 6.0036 | 6.0075 | 0.0039
GEN-2020-086 | 03 - Central | 532785 | PRATTWF7 | 345 | 5.0119 | 5.0145 | 0.0026
GEN-2020-086 | 03 - Central | 532791 | BENTON 7 | 345 | 20.0074 | 20.2629 | 0.2555
GEN-2020-086 | 03 - Central | 532792 | FR2EAST7 | 345 | 7.1001 | 7.1037 | 0.0036
GEN-2020-086 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18.5245 | 18.5326 | 0.0081
GEN-2020-086 | 03 - Central | 532794 | ROSEHIL7 | 345 | 19.5521 | 19.6793 | 0.1272
GEN-2020-086 | 03 - Central | 532795 | FR2WEST7 | 345 | 5.7144 | 5.7166 | 0.0022
GEN-2020-086 | 03 - Central | 532796 | WICHITA7 | 345 | 24.3949 | 24.5073 | 0.1124
GEN-2020-086 | 03 - Central | 532797 | WOLFCRK7 | 345 | 22.0626 | 22.1344 | 0.0718
GEN-2020-086 | 03 - Central | 532798 | VIOLA 7 | 345 | 14.3016 | 14.3211 | 0.0195
GEN-2020-086 | 03 - Central | 532799 | WAVERLY7 | 345 | 18.5703 | 18.6143 | 0.044
GEN-2020-086 | 03 - Central | 532800 | LATHAMS7 | 345 | 10.5797 | 10.6019 | 0.0222
GEN-2020-086 | 03 - Central | 532801 | ELKRVR17 | 345 | 9.3755 | 9.3928 | 0.0173
GEN-2020-086 | 03 - Central | 532802 | WAVERTX7 | 345 | 15.1595 | 15.1886 | 0.0291
GEN-2020-086 | 03 - Central | 532851 | AUBURN 6 | 230 | 13.7394 | 13.7402 | 0.0008
GEN-2020-086 | 03 - Central | 532853 | LAWHILL6 | 230 | 14.1382 | 14.1387 | 0.0005
GEN-2020-086 | 03 - Central | 532854 | LEC U5 6 | 230 | 14.0051 | 14.0056 | 0.0005
GEN-2020-086 | 03 - Central | 532856 | SWISVAL6 | 230 | 22.5969 | 22.5998 | 0.0029
GEN-2020-086 | 03 - Central | 532857 | TECHILL6 | 230 | 11.1784 | 11.179 | 0.0006
GEN-2020-086 | 03 - Central | 532937 | NEOSHO 5 | 161 | 23.9417 | 23.946 | 0.0043
GEN-2020-086 | 03 - Central | 532984 | SUMNER 4 | 138 | 12.6093 | 12.6174 | 0.0081
GEN-2020-086 | 03 - Central | 532986 | BENTON 4 | 138 | 29.0098 | 29.159 | 0.1492
GEN-2020-086 | 03 - Central | 532987 | BUTLER 4 | 138 | 11.3295 | 11.3447 | 0.0152
GEN-2020-086 | 03 - Central | 532988 | BELAIRE4 | 138 | 19.5725 | 19.6358 | 0.0633
GEN-2020-086 | 03 - Central | 532989 | BUTLERS4 | 138 | 11.3221 | 11.3374 | 0.0153
GEN-2020-086 | 03 - Central | 532990 | MIDIAN 4 | 138 | 11.3851 | 11.4017 | 0.0166
GEN-2020-086 | 03 - Central | 532991 | WEAVER 4 | 138 | 22.9037 | 22.9679 | 0.0642
GEN-2020-086 | 03 - Central | 532993 | TALLGRS4 | 138 | 10.7942 | 10.8082 | 0.014
GEN-2020-086 | 03 - Central | 532994 | TCBURNS4 | 138 | 4.1512 | 4.1534 | 0.0022
GEN-2020-086 | 03 - Central | 532996 | TIOGA 4 | 138 | 5.7118 | 5.712 | 0.0002
GEN-2020-086 | 03 - Central | 532997 | OTTRCRK4 | 138 | 5.7448 | 5.7465 | 0.0017
GEN-2020-086 | 03 - Central | 533015 | BENTLEY4 | 138 | 11.0987 | 11.1069 | 0.0082
GEN-2020-086 | 03 - Central | 533016 | WWUPLNT4 | 138 | 8.4183 | 8.4231 | 0.0048
GEN-2020-086 | 03 - Central | 533021 | NEOSHO 4 | 138 | 25.5561 | 25.5606 | 0.0045
GEN-2020-086 | 03 - Central | 533024 | 29TH 4 | 138 | 20.2339 | 20.3017 | 0.0678
GEN-2020-086 | 03 - Central | 533026 | ANDOVER4 | 138 | 18.4754 | 18.5212 | 0.0458
GEN-2020-086 | 03 - Central | 533029 | 59TH ST4 | 138 | 17.8799 | 17.9079 | 0.028
GEN-2020-086 | 03 - Central | 533030 | BOEINGE4 | 138 | 17.4498 | 17.4832 | 0.0334
GEN-2020-086 | 03 - Central | 533032 | BU11PON4 | 138 | 15.6163 | 15.6441 | 0.0278
GEN-2020-086 | 03 - Central | 533035 | CHISHLM4 | 138 | 22.0892 | 22.1472 | 0.058
GEN-2020-086 | 03 - Central | 533036 | CLEARWT4 | 138 | 14.6493 | 14.6633 | 0.014
GEN-2020-086 | 03 - Central | 533037 | COMOTAR4 | 138 | 19.2726 | 19.332 | 0.0594
GEN-2020-086 | 03 - Central | 533039 | ELPASO 4 | 138 | 25.7415 | 25.8094 | 0.0679
GEN-2020-086 | 03 - Central | 533040 | EVANS N4 | 138 | 32.8857 | 32.9669 | 0.0812
GEN-2020-086 | 03 - Central | 533041 | EVANS S4 | 138 | 32.8069 | 32.8877 | 0.0808
GEN-2020-086 | 03 - Central | 533047 | GILL 4 | 138 | 22.5844 | 22.6227 | 0.0383
GEN-2020-086 | 03 - Central | 533052 | PARKCTY4 | 138 | 20.8836 | 20.9403 | 0.0567
GEN-2020-086 | 03 - Central | 533053 | LAKERDG4 | 138 | 17.7087 | 17.7334 | 0.0247
GEN-2020-086 | 03 - Central | 533054 | MAIZE 4 | 138 | 21.4856 | 21.5278 | 0.0422
GEN-2020-086 | 03 - Central | 533059 | ELPASOE4 | 138 | 25.698 | 25.7657 | 0.0677
GEN-2020-086 | 03 - Central | 533060 | NOEASTE4 | 138 | 21.1988 | 21.2678 | 0.069
GEN-2020-086 | 03 - Central | 533061 | NOEASTW4 | 138 | 21.1679 | 21.2368 | 0.0689
GEN-2020-086 | 03 - Central | 533062 | ROSEHIL4 | 138 | 32.1543 | 32.2797 | 0.1254
GEN-2020-086 | 03 - Central | 533064 | 17TH 4 | 138 | 18.1833 | 18.2208 | 0.0375
GEN-2020-086 | 03 - Central | 533065 | SG12COL4 | 138 | 19.9428 | 19.9717 | 0.0289
GEN-2020-086 | 03 - Central | 533067 | SPRNGDL4 | 138 | 14.9818 | 15.0083 | 0.0265
GEN-2020-086 | 03 - Central | 533068 | STEARMN4 | 138 | 20.1536 | 20.1982 | 0.0446
GEN-2020-086 | 03 - Central | 533074 | 45TH ST4 | 138 | 24.2716 | 24.3161 | 0.0445
GEN-2020-086 | 03 - Central | 533075 | VIOLA 4 | 138 | 24.9061 | 24.9343 | 0.0282
GEN-2020-086 | 03 - Central | 533413 | CIRCLE 3 | 115 | 19.2255 | 19.2321 | 0.0066
GEN-2020-086 | 03 - Central | 533415 | DAVIS 3 | 115 | 8.4254 | 8.4268 | 0.0014
GEN-2020-086 | 03 - Central | 533416 | RENO 3 | 115 | 23.1921 | 23.2037 | 0.0116
GEN-2020-086 | 03 - Central | 533429 | MOUNDRG3 | 115 | 8.8163 | 8.8189 | 0.0026
GEN-2020-086 | 03 - Central | 533430 | MNDRGCT3 | 115 | 6.7998 | 6.8013 | 0.0015
GEN-2020-086 | 03 - Central | 533438 | WMCPHER3 | 115 | 11.4228 | 11.4242 | 0.0014
GEN-2020-086 | 03 - Central | 533583 | BUTLERN2 | 69 | 14.3028 | 14.315 | 0.0122
GEN-2020-086 | 03 - Central | 533584 | BU6DEGR2 | 69 | 2.6154 | 2.6158 | 0.0004
GEN-2020-086 | 03 - Central | 533589 | CHESNEY2 | 69 | 9.4611 | 9.4665 | 0.0054
GEN-2020-086 | 03 - Central | 533597 | MIDIANW2 | 69 | 14.6874 | 14.7003 | 0.0129
GEN-2020-086 | 03 - Central | 533599 | PEABODY2 | 69 | 1.819 | 1.8192 | 0.0002
GEN-2020-086 | 03 - Central | 533601 | POTWIN 2 | 69 | 3.7119 | 3.7127 | 0.0008
GEN-2020-086 | 03 - Central | 533603 | THUNBRD2 | 69 | 8.5779 | 8.5823 | 0.0044
GEN-2020-086 | 03 - Central | 533604 | WEAVER 2 | 69 | 12.3883 | 12.3965 | 0.0082
GEN-2020-086 | 03 - Central | 533610 | MIDIANE2 | 69 | 14.6826 | 14.6956 | 0.013
GEN-2020-086 | 03 - Central | 533624 | BURLING2 | 69 | 3.5604 | 3.5606 | 0.0002
GEN-2020-086 | 03 - Central | 533625 | BURLIND2 | 69 | 3.1728 | 3.173 | 0.0002
GEN-2020-086 | 03 - Central | 533626 | BURLJCT2 | 69 | 5.1829 | 5.1833 | 0.0004
GEN-2020-086 | 03 - Central | 533628 | CC1BURL2 | 69 | 3.5589 | 3.5591 | 0.0002
GEN-2020-086 | 03 - Central | 533629 | CC2SHAR2 | 69 | 4.8473 | 4.8477 | 0.0004
GEN-2020-086 | 03 - Central | 533630 | CC3WEST2 | 69 | 4.7832 | 4.7836 | 0.0004
GEN-2020-086 | 03 - Central | 533636 | GREEN 2 | 69 | 4.2408 | 4.241 | 0.0002
GEN-2020-086 | 03 - Central | 533653 | WOLFCRK2 | 69 | 6.2773 | 6.2781 | 0.0008
GEN-2020-086 | 03 - Central | 533786 | CHISHLM2 | 69 | 20.5677 | 20.5911 | 0.0234
GEN-2020-086 | 03 - Central | 533823 | NOEASTE2 | 69 | 26.3311 | 26.3769 | 0.0458
GEN-2020-086 | 03 - Central | 539008 | MILAN_GOAB | 138 | 12.1621 | 12.1687 | 0.0066
GEN-2020-086 | 03 - Central | 539009 | CONWAY | 138 | 11.6791 | 11.6848 | 0.0057
GEN-2020-086 | 03 - Central | 539676 | MILAN 4 | 138 | 10.8069 | 10.812 | 0.0051
GEN-2020-086 | 03 - Central | 539800 | CLARKCOUNTY7 | 345 | 13.4139 | 13.4165 | 0.0026
GEN-2020-086 | 03 - Central | 539801 | THISTLE7 | 345 | 16.8841 | 16.8981 | 0.014
GEN-2020-086 | 03 - Central | 539804 | THISTLE4 | 138 | 18.2012 | 18.2076 | 0.0064
GEN-2020-086 | 03 - Central | 539813 | TRANSFORMER | 345 | 11.2107 | 11.2125 | 0.0018
GEN-2020-086 | 03 - Central | 539840 | GEN-2011-008 | 345 | 11.081 | 11.0827 | 0.0017
GEN-2020-086 | 03 - Central | 539841 | G-2011-008-1 | 345 | 11.081 | 11.0827 | 0.0017
GEN-2020-086 | 03 - Central | 539855 | G-2011-008-2 | 345 | 9.2744 | 9.2755 | 0.0011
GEN-2020-086 | 03 - Central | 539857 | G-2011-008-3 | 345 | 8.683 | 8.684 | 0.001
GEN-2020-086 | 03 - Central | 541198 | PECULR 7 | 345 | 21.2306 | 21.2331 | 0.0025
GEN-2020-086 | 03 - Central | 541200 | PHILL 7 | 345 | 19.1431 | 19.1445 | 0.0014
GEN-2020-086 | 03 - Central | 541341 | S.HARP 5 | 161 | 21.2781 | 21.2789 | 0.0008
GEN-2020-086 | 03 - Central | 541342 | PECULR 5 | 161 | 23.4206 | 23.4216 | 0.001
GEN-2020-086 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2.6785 | 2.6785 | 0
GEN-2020-086 | 03 - Central | 542940 | ATLNTIC7 | 345 | 22.1836 | 22.188 | 0.0044
GEN-2020-086 | 03 - Central | 542945 | CRAIG_CAP 5 | 161 | 35.317 | 35.3191 | 0.0021
GEN-2020-086 | 03 - Central | 542965 | W.GRDNR7 | 345 | 31.1599 | 31.1725 | 0.0126
GEN-2020-086 | 03 - Central | 542966 | WGARDNR5 | 161 | 30.8129 | 30.8153 | 0.0024
GEN-2020-086 | 03 - Central | 542968 | STILWEL7 | 345 | 26.7737 | 26.7794 | 0.0057
GEN-2020-086 | 03 - Central | 542969 | STILWEL5 | 161 | 41.6799 | 41.684 | 0.0041
GEN-2020-086 | 03 - Central | 542977 | CRAIG 7 | 345 | 22.7828 | 22.7852 | 0.0024
GEN-2020-086 | 03 - Central | 542978 | CRAIG 5 | 161 | 44.3874 | 44.3908 | 0.0034
GEN-2020-086 | 03 - Central | 542981 | LACYGNE7 | 345 | 28.5973 | 28.609 | 0.0117
GEN-2020-086 | 03 - Central | 542994 | HICKMAN5 | 161 | 20.1229 | 20.1235 | 0.0006
GEN-2020-086 | 03 - Central | 543031 | SHWNMSN5 | 161 | 37.2372 | 37.2389 | 0.0017
GEN-2020-086 | 03 - Central | 543044 | MOONLT 5 | 161 | 18.082 | 18.0827 | 0.0007
GEN-2020-086 | 03 - Central | 543049 | CEDRCRK5 | 161 | 31.3507 | 31.3524 | 0.0017
GEN-2020-086 | 03 - Central | 543050 | ANTIOCH5 | 161 | 23.51 | 23.5112 | 0.0012
GEN-2020-086 | 03 - Central | 543053 | REDEL 5 | 161 | 25.3387 | 25.3399 | 0.0012
GEN-2020-086 | 03 - Central | 543054 | CEDARNL5 | 161 | 10.9409 | 10.9412 | 0.0003
GEN-2020-086 | 03 - Central | 543056 | GARDNER5 | 161 | 16.8186 | 16.8192 | 0.0006
GEN-2020-086 | 03 - Central | 543057 | BUCYRUS5 | 161 | 21.2222 | 21.2232 | 0.001
GEN-2020-086 | 03 - Central | 543058 | NLOUISB5 | 161 | 9.3692 | 9.3694 | 0.0002
GEN-2020-086 | 03 - Central | 543077 | PLSTVAL5 | 161 | 10.6968 | 10.6971 | 0.0003
GEN-2020-086 | 03 - Central | 543105 | BULLCRK5 | 161 | 29.7856 | 29.7878 | 0.0022
GEN-2020-086 | 03 - Central | 543126 | LACKMAN5 | 161 | 13.9425 | 13.9429 | 0.0004
GEN-2020-086 | 03 - Central | 543132 | BNSF 5 | 161 | 22.5516 | 22.5528 | 0.0012
GEN-2020-086 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27.8194 | 27.8304 | 0.011
GEN-2020-086 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27.8194 | 27.8304 | 0.011
GEN-2020-086 | 03 - Central | 543659 | LACYGNE2 | 69 | 2.8177 | 2.8177 | 0
GEN-2020-086 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 0.6739 | 0.6739 | 0
GEN-2020-086 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 0.6454 | 0.6454 | 0
GEN-2020-086 | 03 - Central | 560053 | G15-052T | 345 | 13.4336 | 13.4639 | 0.0303
GEN-2020-086 | 03 - Central | 562476 | G14-001-TAP | 345 | 10.8306 | 10.8417 | 0.0111
GEN-2020-086 | 03 - Central | 578530 | FR3HV | 345 | 5.2473 | 5.2491 | 0.0018
GEN-2020-086 | 03 - Central | 583850 | GEN-2014-001 | 345 | 7.3025 | 7.3073 | 0.0048
GEN-2020-086 | 03 - Central | 584900 | GEN-2015-052 | 345 | 13.3838 | 13.4138 | 0.03
GEN-2020-086 | 03 - Central | 587500 | GEN-2016-073 | 345 | 15.7187 | 15.756 | 0.0373
GEN-2020-086 | 03 - Central | 587880 | GEN-2016-111 | 345 | 6.8037 | 6.8062 | 0.0025
GEN-2020-086 | 03 - Central | 587884 | G16-111-TAP | 345 | 10.2153 | 10.2212 | 0.0059
GEN-2020-086 | 03 - Central | 588360 | GEN-2016-153 | 345 | 7.466 | 7.4702 | 0.0042
GEN-2020-086 | 03 - Central | 588364 | G16-153-TAP | 345 | 7.8279 | 7.8325 | 0.0046
GEN-2020-086 | 03 - Central | 588630 | GEN-2017-018 | 345 | 16.8841 | 16.8981 | 0.014
GEN-2020-086 | 03 - Central | 589060 | GEN-2017-068 | 138 | 29.8705 | 29.9372 | 0.0667
GEN-2020-086 | 03 - Central | 589240 | GEN-2017-086 | 345 | 6.546 | 6.5492 | 0.0032
GEN-2020-086 | 03 - Central | 709500 | GI-95_POI | 345 | 8.3442 | 8.3444 | 0.0002
GEN-2020-086 | 03 - Central | 709501 | GI-95_HV | 345 | 8.3442 | 8.3444 | 0.0002
GEN-2020-086 | 03 - Central | 760284 | GEN-2017-220 | 345 | 21.183 | 21.2519 | 0.0689
GEN-2020-086 | 03 - Central | 760641 | GEN-2017-226 | 138 | 32.7086 | 32.7889 | 0.0803
GEN-2020-086 | 03 - Central | 760809 | GEN-2017-203 | 345 | 8.765 | 8.7684 | 0.0034
GEN-2020-086 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.6688 | 19.6744 | 0.0056
GEN-2020-086 | 03 - Central | 760921 | G17-209-TAP | 345 | 20.1934 | 20.1994 | 0.006
GEN-2020-086 | 03 - Central | 761271 | GEN-2017-108 | 161 | 7.544 | 7.5441 | 0.0001
GEN-2020-086 | 03 - Central | 761278 | G17-108-TAP | 161 | 12.4204 | 12.4206 | 0.0002
GEN-2020-086 | 03 - Central | 761838 | GEN-2017-121 | 138 | 9.5075 | 9.5118 | 0.0043
GEN-2020-086 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5.3928 | 5.3931 | 0.0003
GEN-2020-086 | 03 - Central | 762279 | GEN-2017-195 | 345 | 31.0675 | 31.08 | 0.0125
GEN-2020-086 | 03 - Central | 762300 | GEN-2017-196 | 345 | 30.9699 | 30.9823 | 0.0124
GEN-2020-086 | 03 - Central | 762405 | ASG-2018-010 | 161 | 3.3626 | 3.3626 | 0
GEN-2020-086 | 03 - Central | 762680 | GEN-2018-032 | 345 | 12.139 | 12.1425 | 0.0035
GEN-2020-086 | 03 - Central | 762834 | GEN-2018-049 | 345 | 7.1992 | 7.2017 | 0.0025
GEN-2020-086 | 03 - Central | 762922 | GEN-2018-057 | 138 | 17.8149 | 17.8374 | 0.0225
GEN-2020-086 | 03 - Central | 763065 | GEN-2018-071 | 345 | 13.1437 | 13.1526 | 0.0089
GEN-2020-086 | 03 - Central | 763069 | G18-071_TAP | 345 | 13.1932 | 13.2022 | 0.009
GEN-2020-086 | 03 - Central | 763417 | GEN-2018-128 | 345 | 11.0357 | 11.0428 | 0.0071
GEN-2020-086 | 03 - Central | 763421 | G18-128-TAP | 345 | 12.1336 | 12.1422 | 0.0086
GEN-2020-086 | 03 - Central | 763890 | GEN-2019-058 | 345 | 13.1427 | 13.1452 | 0.0025
GEN-2020-086 | 03 - Central | 764375 | GEN-2020-058 | 345 | 22.1385 | 22.1428 | 0.0043
GEN-2020-086 | 03 - Central | 764390 | GEN-2020-073 | 161 | 8.3927 | 8.3928 | 0.0001
GEN-2020-086 | 03 - Central | 764400 | G20-073-TAP | 161 | 8.4737 | 8.4738 | 0.0001
GEN-2020-086 | 03 - Central | 765100 | GEN-2020-052 | 345 | 9.9263 | 9.928 | 0.0017
GEN-2020-086 | 03 - Central | 765110 | G20-052-TAP | 345 | 13.1156 | 13.1185 | 0.0029
GEN-2020-086 | 03 - Central | 765115 | GEN-2020-057 | 345 | 22.1386 | 22.1429 | 0.0043
GEN-2020-086 | 03 - Central | 765130 | GEN-2020-071 | 230 | 11.3783 | 11.3791 | 0.0008
GEN-2020-086 | 03 - Central | 765140 | G20-071-TAP | 230 | 11.3783 | 11.3791 | 0.0008
GEN-2020-086 | 03 - Central | 765145 | GEN-2020-076 | 345 | 12.1551 | 12.5518 | 0.3967
GEN-2020-086 | 03 - Central | 765155 | G20-076-TAP | 345 | 12.1623 | 12.5595 | 0.3972
GEN-2020-086 | 03 - Central | 765160 | GEN-2020-086 | 345 | 12.1552 | 12.5524 | 0.3972
GEN-2020-086 | 03 - Central | 765190 | GEN-2020-090 | 345 | 8.7223 | 8.7262 | 0.0039
GEN-2020-086 | 03 - Central | 765200 | G20-090-TAP | 345 | 9.948 | 9.9531 | 0.0051
GEN-2020-086 | 03 - Central | 766260 | GEN-2020-007 | 345 | 25.1462 | 25.1555 | 0.0093
GEN-2020-086 | 03 - Central | 766261 | G20-007-TAP | 345 | 27.7585 | 27.7699 | 0.0114
GEN-2020-088 | 03 - Central | 300042 | 7HUBEN | 345 | 10.5756 | 10.5775 | 0.0019
GEN-2020-088 | 03 - Central | 300045 | 7MORGAN | 345 | 13.9852 | 13.9925 | 0.0073
GEN-2020-088 | 03 - Central | 300081 | 5GAINES | 161 | 5.9475 | 5.9478 | 0.0003
GEN-2020-088 | 03 - Central | 300089 | 5JAMESV | 161 | 16.1229 | 16.1344 | 0.0115
GEN-2020-088 | 03 - Central | 300095 | 5MANSFDMN | 161 | 9.15 | 9.151 | 0.001
GEN-2020-088 | 03 - Central | 300101 | 5MORGAN | 161 | 19.7356 | 19.749 | 0.0134
GEN-2020-088 | 03 - Central | 300118 | 5STKAEC | 161 | 9.3374 | 9.3391 | 0.0017
GEN-2020-088 | 03 - Central | 300348 | 5BTLFD | 161 | 21.9484 | 21.9669 | 0.0185
GEN-2020-088 | 03 - Central | 300646 | 2BELLAMY | 69 | 2.6487 | 2.6488 | 0.0001
GEN-2020-088 | 03 - Central | 300647 | 2BLLMYTP | 69 | 5.3226 | 5.3229 | 0.0003
GEN-2020-088 | 03 - Central | 300649 | 2JASPER | 69 | 4.9486 | 4.9501 | 0.0015
GEN-2020-088 | 03 - Central | 300651 | 2LAMR | 69 | 10.1501 | 10.1521 | 0.002
GEN-2020-088 | 03 - Central | 300652 | 2LAMRCTS | 69 | 3.9485 | 3.9487 | 0.0002
GEN-2020-088 | 03 - Central | 300653 | 2MEDOC | 69 | 2.4929 | 2.4932 | 0.0003
GEN-2020-088 | 03 - Central | 300656 | 2JACK ST | 69 | 7.593 | 7.5943 | 0.0013
GEN-2020-088 | 03 - Central | 300657 | 2ASHGRV | 69 | 4.052 | 4.0523 | 0.0003
GEN-2020-088 | 03 - Central | 300658 | 2BILLNG | 69 | 8.4241 | 8.4285 | 0.0044
GEN-2020-088 | 03 - Central | 300659 | 2BOWRML | 69 | 6.1639 | 6.167 | 0.0031
GEN-2020-088 | 03 - Central | 300660 | 2BRNSPG | 69 | 3.8381 | 3.8392 | 0.0011
GEN-2020-088 | 03 - Central | 300663 | 2CASSIDY | 69 | 6.9522 | 6.9529 | 0.0007
GEN-2020-088 | 03 - Central | 300664 | 2CAVESP | 69 | 2.4071 | 2.4072 | 0.0001
GEN-2020-088 | 03 - Central | 300666 | 2CLRKSN | 69 | 2.851 | 2.8516 | 0.0006
GEN-2020-088 | 03 - Central | 300667 | 2CRANE | 69 | 3.3441 | 3.3451 | 0.001
GEN-2020-088 | 03 - Central | 300668 | 2DADEVL | 69 | 5.8584 | 5.8591 | 0.0007
GEN-2020-088 | 03 - Central | 300669 | 2ELWOOD | 69 | 5.4281 | 5.4286 | 0.0005
GEN-2020-088 | 03 - Central | 300670 | 2EPURDY | 69 | 3.6333 | 3.6347 | 0.0014
GEN-2020-088 | 03 - Central | 300673 | 2JAMESV | 69 | 12.2143 | 12.217 | 0.0027
GEN-2020-088 | 03 - Central | 300677 | 2MTVRN | 69 | 9.0944 | 9.1004 | 0.006
GEN-2020-088 | 03 - Central | 300678 | 5NIXA-1 | 161 | 19.3957 | 19.4132 | 0.0175
GEN-2020-088 | 03 - Central | 300679 | 2PRDYTP | 69 | 5.17 | 5.1728 | 0.0028
GEN-2020-088 | 03 - Central | 300680 | 2VERONA | 69 | 6.5897 | 6.5956 | 0.0059
GEN-2020-088 | 03 - Central | 300681 | 2BUTRFLD | 69 | 5.1741 | 5.1762 | 0.0021
GEN-2020-088 | 03 - Central | 300685 | 2LAMARPT | 69 | 8.5681 | 8.5695 | 0.0014
GEN-2020-088 | 03 - Central | 300718 | 5CLEVCOV | 161 | 12.1547 | 12.1598 | 0.0051
GEN-2020-088 | 03 - Central | 300719 | 5COMPTN | 161 | 11.537 | 11.5421 | 0.0051
GEN-2020-088 | 03 - Central | 300723 | 2PARDIS | 69 | 5.1147 | 5.1151 | 0.0004
GEN-2020-088 | 03 - Central | 300726 | 5RIVRDL | 161 | 11.6763 | 11.6822 | 0.0059
GEN-2020-088 | 03 - Central | 300727 | 5ROARK | 161 | 10.172 | 10.176 | 0.004
GEN-2020-088 | 03 - Central | 300735 | 2T.ROCK | 69 | 12.4294 | 12.4323 | 0.0029
GEN-2020-088 | 03 - Central | 300744 | 2DMNDGR | 69 | 2.6046 | 2.6055 | 0.0009
GEN-2020-088 | 03 - Central | 300745 | 2DMNDTP | 69 | 5.5946 | 5.599 | 0.0044
GEN-2020-088 | 03 - Central | 300748 | 2NEOSAC | 69 | 10.1938 | 10.2004 | 0.0066
GEN-2020-088 | 03 - Central | 300750 | 2NEOSHO | 69 | 8.6748 | 8.6793 | 0.0045
GEN-2020-088 | 03 - Central | 300751 | 2REEDS | 69 | 6.5636 | 6.5696 | 0.006
GEN-2020-088 | 03 - Central | 300753 | 2SIMS | 69 | 3.7055 | 3.706 | 0.0005
GEN-2020-088 | 03 - Central | 300754 | 2SPGCTP | 69 | 5.6516 | 5.6539 | 0.0023
GEN-2020-088 | 03 - Central | 300755 | 2SPGCTY | 69 | 2.7581 | 2.7587 | 0.0006
GEN-2020-088 | 03 - Central | 300758 | 2SWTWT | 69 | 4.277 | 4.2781 | 0.0011
GEN-2020-088 | 03 - Central | 300762 | 2WNTWRT | 69 | 4.7699 | 4.7727 | 0.0028
GEN-2020-088 | 03 - Central | 300763 | 2WASHBRN | 69 | 6.7977 | 6.7995 | 0.0018
GEN-2020-088 | 03 - Central | 300764 | 2SPURGNTP | 69 | 3.1949 | 3.1956 | 0.0007
GEN-2020-088 | 03 - Central | 300765 | 2SPURGN | 69 | 2.9215 | 2.9221 | 0.0006
GEN-2020-088 | 03 - Central | 300774 | 2EUDORA | 69 | 6.1729 | 6.1735 | 0.0006
GEN-2020-088 | 03 - Central | 300782 | 2MORGAN | 69 | 7.1193 | 7.1202 | 0.0009
GEN-2020-088 | 03 - Central | 300788 | 2SLAGLE | 69 | 6.2374 | 6.2379 | 0.0005
GEN-2020-088 | 03 - Central | 300794 | 5LAMAR | 161 | 8.9438 | 8.9451 | 0.0013
GEN-2020-088 | 03 - Central | 300800 | 2BONA | 69 | 3.4954 | 3.4957 | 0.0003
GEN-2020-088 | 03 - Central | 300805 | 5RIVERSIDE | 161 | 11.0746 | 11.0799 | 0.0053
GEN-2020-088 | 03 - Central | 300816 | 5COLLINS | 161 | 6.7878 | 6.7884 | 0.0006
GEN-2020-088 | 03 - Central | 300824 | 2SELIGM | 69 | 6.1872 | 6.1888 | 0.0016
GEN-2020-088 | 03 - Central | 300949 | 7JASPER | 345 | 13.038 | 13.0411 | 0.0031
GEN-2020-088 | 03 - Central | 301057 | 5GRVSPG | 161 | 7.0396 | 7.04 | 0.0004
GEN-2020-088 | 03 - Central | 301058 | 2HARTVL | 69 | 3.3811 | 3.3812 | 0.0001
GEN-2020-088 | 03 - Central | 301128 | 5MTNGRV | 161 | 6.1392 | 6.1395 | 0.0003
GEN-2020-088 | 03 - Central | 301161 | 5LOGAN | 161 | 13.7036 | 13.7099 | 0.0063
GEN-2020-088 | 03 - Central | 301168 | 2MANSFL | 69 | 10.6656 | 10.6663 | 0.0007
GEN-2020-088 | 03 - Central | 301360 | 2T.ROCKSW | 69 | 12.7071 | 12.7102 | 0.0031
GEN-2020-088 | 03 - Central | 301393 | 2ROUNDGROVE | 69 | 4.3108 | 4.3117 | 0.0009
GEN-2020-088 | 03 - Central | 301395 | 2ROUNDGRVETP | 69 | 4.4837 | 4.4847 | 0.001
GEN-2020-088 | 03 - Central | 301521 | 5REEDSP | 161 | 8.6352 | 8.642 | 0.0068
GEN-2020-088 | 03 - Central | 301547 | 5MANSFDTF | 161 | 9.1279 | 9.1289 | 0.001
GEN-2020-088 | 03 - Central | 301622 | 5MORGANXF2 | 161 | 19.7343 | 19.7477 | 0.0134
GEN-2020-088 | 03 - Central | 338099 | 5GRANDVIEW% | 161 | 9.7497 | 9.7524 | 0.0027
GEN-2020-088 | 03 - Central | 338120 | 5S.LEAD HILL | 161 | 6.6076 | 6.6084 | 0.0008
GEN-2020-088 | 03 - Central | 338554 | 2OSAGE CRK-1 | 69 | 4.6805 | 4.6808 | 0.0003
GEN-2020-088 | 03 - Central | 338556 | 2OSAGE CRK-2 | 69 | 4.2165 | 4.2167 | 0.0002
GEN-2020-088 | 03 - Central | 338682 | 5OSAGE CRK#! | 161 | 9.8089 | 9.8114 | 0.0025
GEN-2020-088 | 03 - Central | 503508 | 2LAMRLNDFL | 69 | 3.3631 | 3.3633 | 0.0002
GEN-2020-088 | 03 - Central | 504000 | AVOCA 5 | 161 | 9.4228 | 9.4245 | 0.0017
GEN-2020-088 | 03 - Central | 504001 | AVOCA_1 2 | 69 | 6.735 | 6.7354 | 0.0004
GEN-2020-088 | 03 - Central | 505472 | TABLE R5 | 161 | 15.1077 | 15.1161 | 0.0084
GEN-2020-088 | 03 - Central | 505474 | TABLE R2 | 69 | 13.7095 | 13.7131 | 0.0036
GEN-2020-088 | 03 - Central | 505480 | BEAVER 5 | 161 | 11.2996 | 11.3035 | 0.0039
GEN-2020-088 | 03 - Central | 505485 | WASHBURN5 | 161 | 8.3452 | 8.3493 | 0.0041
GEN-2020-088 | 03 - Central | 505486 | NEO SPA5 | 161 | 15.7599 | 15.8028 | 0.0429
GEN-2020-088 | 03 - Central | 505488 | CARTHAG5 | 161 | 16.7537 | 16.9087 | 0.155
GEN-2020-088 | 03 - Central | 505490 | CARTHG 2 | 69 | 14.0603 | 14.0947 | 0.0344
GEN-2020-088 | 03 - Central | 505492 | SPRGFLD5 | 161 | 27.3988 | 27.4351 | 0.0363
GEN-2020-088 | 03 - Central | 505494 | SPRGFLD2 | 69 | 16.188 | 16.1934 | 0.0054
GEN-2020-088 | 03 - Central | 505496 | NIXA 5 | 161 | 12.7234 | 12.7307 | 0.0073
GEN-2020-088 | 03 - Central | 505498 | STOCKTN5 | 161 | 10.0698 | 10.0717 | 0.0019
GEN-2020-088 | 03 - Central | 505501 | NIXA 2 | 69 | 12.4887 | 12.4916 | 0.0029
GEN-2020-088 | 03 - Central | 505541 | NIXA DT2 | 69 | 10.9284 | 10.9306 | 0.0022
GEN-2020-088 | 03 - Central | 505543 | NX ESPY2 | 69 | 11.3659 | 11.3683 | 0.0024
GEN-2020-088 | 03 - Central | 505545 | NIX_SLR_U1_2 | 69 | 8.8078 | 8.8093 | 0.0015
GEN-2020-088 | 03 - Central | 506932 | EUREKA 5 | 161 | 10.4999 | 10.503 | 0.0031
GEN-2020-088 | 03 - Central | 506934 | FLINTCR5 | 161 | 34.4838 | 34.4901 | 0.0063
GEN-2020-088 | 03 - Central | 506935 | FLINTCR7 | 345 | 15.7205 | 15.7233 | 0.0028
GEN-2020-088 | 03 - Central | 506979 | SHIPERD7 | 345 | 10.5701 | 10.5714 | 0.0013
GEN-2020-088 | 03 - Central | 510411 | GROVE 5 | 161 | 5.9739 | 5.9753 | 0.0014
GEN-2020-088 | 03 - Central | 512750 | TONECE7 | 345 | 15.4925 | 15.4951 | 0.0026
GEN-2020-088 | 03 - Central | 532932 | LITCH 5 | 161 | 9.1889 | 9.201 | 0.0121
GEN-2020-088 | 03 - Central | 547400 | MON376J2 | 69 | 4.1267 | 4.13 | 0.0033
GEN-2020-088 | 03 - Central | 547401 | MON376 2 | 69 | 6.6941 | 6.7028 | 0.0087
GEN-2020-088 | 03 - Central | 547402 | MON416J2 | 69 | 3.6345 | 3.637 | 0.0025
GEN-2020-088 | 03 - Central | 547403 | MON416 2 | 69 | 3.5401 | 3.5425 | 0.0024
GEN-2020-088 | 03 - Central | 547404 | PUR390 2 | 69 | 1.7994 | 1.7999 | 0.0005
GEN-2020-088 | 03 - Central | 547405 | MON352J2 | 69 | 7.9194 | 7.9316 | 0.0122
GEN-2020-088 | 03 - Central | 547406 | MON352 2 | 69 | 7.6077 | 7.619 | 0.0113
GEN-2020-088 | 03 - Central | 547407 | MON311J2 | 69 | 6.779 | 6.7879 | 0.0089
GEN-2020-088 | 03 - Central | 547408 | MON311 2 | 69 | 6.6941 | 6.7028 | 0.0087
GEN-2020-088 | 03 - Central | 547424 | RES364 2 | 69 | 4.0689 | 4.0702 | 0.0013
GEN-2020-088 | 03 - Central | 547428 | SWC414 2 | 69 | 3.8235 | 3.8238 | 0.0003
GEN-2020-088 | 03 - Central | 547430 | SAR362 2 | 69 | 2.0301 | 2.0307 | 0.0006
GEN-2020-088 | 03 - Central | 547431 | WEB105 2 | 69 | 8.1249 | 8.1295 | 0.0046
GEN-2020-088 | 03 - Central | 547438 | EXP449T2 | 69 | 9.1021 | 9.107 | 0.0049
GEN-2020-088 | 03 - Central | 547439 | EXP4492 | 69 | 7.5505 | 7.5539 | 0.0034
GEN-2020-088 | 03 - Central | 547449 | PRC460 2 | 69 | 5.7532 | 5.7586 | 0.0054
GEN-2020-088 | 03 - Central | 547450 | JAS344T2 | 69 | 5.1093 | 5.1105 | 0.0012
GEN-2020-088 | 03 - Central | 547451 | JAS344 | 69 | 4.4452 | 4.4461 | 0.0009
GEN-2020-088 | 03 - Central | 547459 | WWR477 | 161 | 22.2261 | 22.2791 | 0.053
GEN-2020-088 | 03 - Central | 547462 | SVRCK469 5 | 161 | 14.3938 | 14.4236 | 0.0298
GEN-2020-088 | 03 - Central | 547463 | KOD471 2 | 69 | 12.2332 | 12.245 | 0.0118
GEN-2020-088 | 03 - Central | 547466 | ATL109 5 | 161 | 16.4874 | 16.5632 | 0.0758
GEN-2020-088 | 03 - Central | 547467 | ORO110 5 | 161 | 20.0067 | 20.0777 | 0.071
GEN-2020-088 | 03 - Central | 547468 | AUR124 5 | 161 | 10.7816 | 10.82 | 0.0384
GEN-2020-088 | 03 - Central | 547469 | RIV4525 | 161 | 24.7577 | 24.8094 | 0.0517
GEN-2020-088 | 03 - Central | 547470 | JOP145 5 | 161 | 19.0984 | 19.1474 | 0.049
GEN-2020-088 | 03 - Central | 547471 | NEO184 5 | 161 | 14.5396 | 14.5735 | 0.0339
GEN-2020-088 | 03 - Central | 547472 | TIP292 5 | 161 | 17.7226 | 17.777 | 0.0544
GEN-2020-088 | 03 - Central | 547473 | RDS295 5 | 161 | 8.0627 | 8.0699 | 0.0072
GEN-2020-088 | 03 - Central | 547476 | ASB349 5 | 161 | 11.2901 | 11.3142 | 0.0241
GEN-2020-088 | 03 - Central | 547477 | CJ 366 5 | 161 | 12.6814 | 12.7105 | 0.0291
GEN-2020-088 | 03 - Central | 547478 | DAD368 5 | 161 | 18.6454 | 18.6582 | 0.0128
GEN-2020-088 | 03 - Central | 547479 | LAR382 5 | 161 | 15.1939 | 15.6765 | 0.4826
GEN-2020-088 | 03 - Central | 547480 | MON383 5 | 161 | 12.1124 | 12.2093 | 0.0969
GEN-2020-088 | 03 - Central | 547483 | JOP389 5 | 161 | 20.0352 | 20.0887 | 0.0535
GEN-2020-088 | 03 - Central | 547484 | DEC392 5 | 161 | 15.7745 | 15.7779 | 0.0034
GEN-2020-088 | 03 - Central | 547485 | CAR395 5 | 161 | 12.4694 | 12.5434 | 0.074
GEN-2020-088 | 03 - Central | 547489 | BRN413 5 | 161 | 10.7286 | 10.7342 | 0.0056
GEN-2020-088 | 03 - Central | 547490 | FIR417 5 | 161 | 14.6083 | 14.6466 | 0.0383
GEN-2020-088 | 03 - Central | 547491 | PUR421 5 | 161 | 9.7407 | 9.7721 | 0.0314
GEN-2020-088 | 03 - Central | 547493 | BOL431 5 | 161 | 6.1356 | 6.1371 | 0.0015
GEN-2020-088 | 03 - Central | 547494 | OAK432 5 | 161 | 18.1181 | 18.1868 | 0.0687
GEN-2020-088 | 03 - Central | 547496 | NOL435 5 | 161 | 10.2067 | 10.212 | 0.0053
GEN-2020-088 | 03 - Central | 547497 | RVS438 5 | 161 | 12.3816 | 12.3883 | 0.0067
GEN-2020-088 | 03 - Central | 547498 | STL439 5 | 161 | 24.2838 | 24.3471 | 0.0633
GEN-2020-088 | 03 - Central | 547499 | CPK446 5 | 161 | 8.7625 | 8.7765 | 0.014
GEN-2020-088 | 03 - Central | 547500 | RNM393 5 | 161 | 14.4538 | 14.4879 | 0.0341
GEN-2020-088 | 03 - Central | 547501 | RIV453 5 | 161 | 23.3546 | 23.3993 | 0.0447
GEN-2020-088 | 03 - Central | 547502 | RIV167 5 | 161 | 22.9241 | 22.968 | 0.0439
GEN-2020-088 | 03 - Central | 547503 | RIV452T 5 | 161 | 24.2857 | 24.335 | 0.0493
GEN-2020-088 | 03 - Central | 547527 | WEB436 2 | 69 | 9.6975 | 9.7038 | 0.0063
GEN-2020-088 | 03 - Central | 547532 | CAR108 2 | 69 | 8.5064 | 8.5107 | 0.0043
GEN-2020-088 | 03 - Central | 547533 | ATL109 2 | 69 | 21.1381 | 21.1739 | 0.0358
GEN-2020-088 | 03 - Central | 547534 | ORO110 2 | 69 | 18.2432 | 18.2668 | 0.0236
GEN-2020-088 | 03 - Central | 547537 | AUR124 2 | 69 | 12.589 | 12.6096 | 0.0206
GEN-2020-088 | 03 - Central | 547540 | MON152 2 | 69 | 10.9836 | 11.0061 | 0.0225
GEN-2020-088 | 03 - Central | 547543 | NEO184 2 | 69 | 12.07 | 12.0789 | 0.0089
GEN-2020-088 | 03 - Central | 547544 | WEN205 2 | 69 | 4.5471 | 4.55 | 0.0029
GEN-2020-088 | 03 - Central | 547546 | BIL221 2 | 69 | 10.0774 | 10.0831 | 0.0057
GEN-2020-088 | 03 - Central | 547553 | ALB262 2 | 69 | 8.7543 | 8.7602 | 0.0059
GEN-2020-088 | 03 - Central | 547556 | OAK280 2 | 69 | 16.1603 | 16.1797 | 0.0194
GEN-2020-088 | 03 - Central | 547559 | TIP292 2 | 69 | 10.089 | 10.0962 | 0.0072
GEN-2020-088 | 03 - Central | 547560 | ROC296 2 | 69 | 9.0324 | 9.0375 | 0.0051
GEN-2020-088 | 03 - Central | 547563 | LIN314 2 | 69 | 10.2595 | 10.266 | 0.0065
GEN-2020-088 | 03 - Central | 547566 | AND322 2 | 69 | 5.7953 | 5.7966 | 0.0013
GEN-2020-088 | 03 - Central | 547578 | AUR355 2 | 69 | 9.5685 | 9.5797 | 0.0112
GEN-2020-088 | 03 - Central | 547581 | JOP360 2 | 69 | 14.3465 | 14.3614 | 0.0149
GEN-2020-088 | 03 - Central | 547582 | SAR362T2 | 69 | 4.4156 | 4.418 | 0.0024
GEN-2020-088 | 03 - Central | 547585 | DAD368 2 | 69 | 9.8798 | 9.8817 | 0.0019
GEN-2020-088 | 03 - Central | 547588 | JOP372 2 | 69 | 15.5132 | 15.5295 | 0.0163
GEN-2020-088 | 03 - Central | 547591 | MON383 2 | 69 | 12.6667 | 12.6978 | 0.0311
GEN-2020-088 | 03 - Central | 547592 | JOP389 2 | 69 | 15.5616 | 15.5762 | 0.0146
GEN-2020-088 | 03 - Central | 547593 | JOP391 5 | 161 | 13.5734 | 13.6025 | 0.0291
GEN-2020-088 | 03 - Central | 547595 | RNM393 2 | 69 | 19.6659 | 19.6947 | 0.0288
GEN-2020-088 | 03 - Central | 547604 | BHJ415 2 | 69 | 11.204 | 11.2064 | 0.0024
GEN-2020-088 | 03 - Central | 547606 | MTV420 2 | 69 | 7.1246 | 7.1294 | 0.0048
GEN-2020-088 | 03 - Central | 547607 | JOP422 5 | 161 | 13.3947 | 13.4218 | 0.0271
GEN-2020-088 | 03 - Central | 547608 | JOP430 2 | 69 | 16.0744 | 16.0904 | 0.016
GEN-2020-088 | 03 - Central | 547610 | NOL435 2 | 69 | 8.5506 | 8.5524 | 0.0018
GEN-2020-088 | 03 - Central | 547611 | MAR437 2 | 69 | 6.0188 | 6.0222 | 0.0034
GEN-2020-088 | 03 - Central | 547618 | CPK446 2 | 69 | 10.4965 | 10.5044 | 0.0079
GEN-2020-088 | 03 - Central | 547626 | HOL478_5 | 161 | 10.4475 | 10.4523 | 0.0048
GEN-2020-088 | 03 - Central | 547685 | PLB447 2 | 69 | 14.6182 | 14.6328 | 0.0146
GEN-2020-088 | 03 - Central | 549903 | JRPS 69B-2 2 | 69 | 19.5341 | 19.5406 | 0.0065
GEN-2020-088 | 03 - Central | 549904 | JAMES RIVER2 | 69 | 16.1067 | 16.1107 | 0.004
GEN-2020-088 | 03 - Central | 549905 | PLAINVIEW 2 | 69 | 14.3424 | 14.346 | 0.0036
GEN-2020-088 | 03 - Central | 549910 | COX 2 | 69 | 14.1649 | 14.1686 | 0.0037
GEN-2020-088 | 03 - Central | 549911 | GOLDEN 2 | 69 | 20.5782 | 20.5866 | 0.0084
GEN-2020-088 | 03 - Central | 549913 | DAYTON 2 | 69 | 19.4926 | 19.5 | 0.0074
GEN-2020-088 | 03 - Central | 549914 | FORT 2 | 69 | 17.7299 | 17.7356 | 0.0057
GEN-2020-088 | 03 - Central | 549916 | BLACKMAN 2 | 69 | 18.3385 | 18.3438 | 0.0053
GEN-2020-088 | 03 - Central | 549917 | INGRAM 2 | 69 | 17.0734 | 17.0779 | 0.0045
GEN-2020-088 | 03 - Central | 549918 | MILL 2 | 69 | 22.5289 | 22.5369 | 0.008
GEN-2020-088 | 03 - Central | 549919 | CHAD 2 | 69 | 15.9863 | 15.9906 | 0.0043
GEN-2020-088 | 03 - Central | 549920 | HARGISS 2 | 69 | 18.1678 | 18.1735 | 0.0057
GEN-2020-088 | 03 - Central | 549921 | MAIN STREET2 | 69 | 25.9857 | 25.9979 | 0.0122
GEN-2020-088 | 03 - Central | 549922 | GRAND 2 | 69 | 19.1207 | 19.1271 | 0.0064
GEN-2020-088 | 03 - Central | 549924 | LAUREL 2 | 69 | 18.2738 | 18.2811 | 0.0073
GEN-2020-088 | 03 - Central | 549925 | NICHOLS 2 | 69 | 24.1451 | 24.1589 | 0.0138
GEN-2020-088 | 03 - Central | 549929 | WASHINGTON 2 | 69 | 19.5381 | 19.545 | 0.0069
GEN-2020-088 | 03 - Central | 549932 | PACKER 2 | 69 | 14.8274 | 14.8309 | 0.0035
GEN-2020-088 | 03 - Central | 549954 | JTEC 5 | 161 | 26.9857 | 27.0134 | 0.0277
GEN-2020-088 | 03 - Central | 549955 | JUNCTION 5 | 161 | 20.9966 | 21.0147 | 0.0181
GEN-2020-088 | 03 - Central | 549956 | NICHOLS 5 | 161 | 19.147 | 19.1629 | 0.0159
GEN-2020-088 | 03 - Central | 549957 | WEST BELT 5 | 161 | 18.876 | 18.8916 | 0.0156
GEN-2020-088 | 03 - Central | 549958 | MAIN STREET5 | 161 | 19.1026 | 19.1187 | 0.0161
GEN-2020-088 | 03 - Central | 549959 | BATTLEFIELD5 | 161 | 26.7449 | 26.7786 | 0.0337
GEN-2020-088 | 03 - Central | 549960 | SW DISP PLT5 | 161 | 25.7046 | 25.7307 | 0.0261
GEN-2020-088 | 03 - Central | 549961 | JAMES RIVER5 | 161 | 15.8546 | 15.8626 | 0.008
GEN-2020-088 | 03 - Central | 549962 | MILL 5 | 161 | 16.0261 | 16.0346 | 0.0085
GEN-2020-088 | 03 - Central | 549963 | MENTOR 5 | 161 | 15.0403 | 15.0481 | 0.0078
GEN-2020-088 | 03 - Central | 549966 | SUMMIT 5 | 161 | 13.3899 | 13.3962 | 0.0063
GEN-2020-088 | 03 - Central | 549968 | MC CARTNEY 5 | 161 | 15.21 | 15.2166 | 0.0066
GEN-2020-088 | 03 - Central | 549969 | BROOKLINE 5 | 161 | 28.4572 | 28.4898 | 0.0326
GEN-2020-088 | 03 - Central | 549970 | CLAY 5 | 161 | 18.7935 | 18.8062 | 0.0127
GEN-2020-088 | 03 - Central | 549971 | PIC WEST 5 | 161 | 17.2849 | 17.2968 | 0.0119
GEN-2020-088 | 03 - Central | 549979 | BATTLEFIELD2 | 69 | 20.8675 | 20.8761 | 0.0086
GEN-2020-088 | 03 - Central | 549984 | BROOKLINE 7 | 345 | 11.9492 | 11.9564 | 0.0072
GEN-2020-088 | 03 - Central | 588980 | GEN-2017-060 | 161 | 6.1738 | 6.2434 | 0.0696
GEN-2020-088 | 03 - Central | 589200 | GEN-2017-082 | 161 | 7.6697 | 7.6802 | 0.0105
GEN-2020-088 | 03 - Central | 709500 | GI-95_POI | 345 | 8.3419 | 8.3444 | 0.0025
GEN-2020-088 | 03 - Central | 709501 | GI-95_HV | 345 | 8.3419 | 8.3444 | 0.0025
GEN-2020-088 | 03 - Central | 760242 | GEN-2017-188 | 161 | 2.0294 | 2.0299 | 0.0005
GEN-2020-088 | 03 - Central | 763560 | GEN-2019-016 | 161 | 18.336 | 18.3484 | 0.0124
GEN-2020-088 | 03 - Central | 763692 | GEN-2019-035 | 161 | 7.8603 | 7.8727 | 0.0124
GEN-2020-088 | 03 - Central | 763696 | G19-035-TAP | 161 | 7.8779 | 7.8903 | 0.0124
GEN-2020-088 | 03 - Central | 764315 | GEN-2020-088 | 161 | 14.7196 | 15.2024 | 0.4828
GEN-2020-089 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 16.1241 | 16.1277 | 0.0036
GEN-2020-089 | 03 - Central | 532777 | G17-009-TAP | 345 | 12.0649 | 12.069 | 0.0041
GEN-2020-089 | 03 - Central | 532778 | GEN-2017-009 | 345 | 11.1493 | 11.1528 | 0.0035
GEN-2020-089 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18.5196 | 18.5326 | 0.013
GEN-2020-089 | 03 - Central | 532932 | LITCH 5 | 161 | 9.1721 | 9.201 | 0.0289
GEN-2020-089 | 03 - Central | 532934 | MARMTNE5 | 161 | 8.1941 | 8.411 | 0.2169
GEN-2020-089 | 03 - Central | 532935 | MARMTNW5 | 161 | 8.1909 | 8.4072 | 0.2163
GEN-2020-089 | 03 - Central | 532937 | NEOSHO 5 | 161 | 23.9058 | 23.946 | 0.0402
GEN-2020-089 | 03 - Central | 532938 | FRANKLIN5 | 161 | 7.9843 | 8.0194 | 0.0351
GEN-2020-089 | 03 - Central | 533008 | TV1MNDV4 | 138 | 7.266 | 7.2674 | 0.0014
GEN-2020-089 | 03 - Central | 533020 | NEOSHOS4 | 138 | 25.4848 | 25.5172 | 0.0324
GEN-2020-089 | 03 - Central | 533021 | NEOSHO 4 | 138 | 25.5282 | 25.5606 | 0.0324
GEN-2020-089 | 03 - Central | 533022 | NEOSHON4 | 138 | 25.4081 | 25.4402 | 0.0321
GEN-2020-089 | 03 - Central | 533639 | MARMATN2 | 69 | 8.9679 | 9.0332 | 0.0653
GEN-2020-089 | 03 - Central | 533640 | MCKEE 2 | 69 | 4.3524 | 4.3646 | 0.0122
GEN-2020-089 | 03 - Central | 533645 | SE9HIAT2 | 69 | 3.8694 | 3.8781 | 0.0087
GEN-2020-089 | 03 - Central | 533647 | UN1ELSM2 | 69 | 8.0794 | 8.1272 | 0.0478
GEN-2020-089 | 03 - Central | 533650 | UN8HUMB2 | 69 | 4.5549 | 4.5629 | 0.008
GEN-2020-089 | 03 - Central | 533654 | ZILAJCT2 | 69 | 6.471 | 6.4868 | 0.0158
GEN-2020-089 | 03 - Central | 533761 | GIRARD 2 | 69 | 4.676 | 4.679 | 0.003
GEN-2020-089 | 03 - Central | 533762 | GIR JCT2 | 69 | 6.6768 | 6.6831 | 0.0063
GEN-2020-089 | 03 - Central | 533765 | LITCH N2 | 69 | 13.0713 | 13.0972 | 0.0259
GEN-2020-089 | 03 - Central | 533766 | LITCH S2 | 69 | 13.0721 | 13.098 | 0.0259
GEN-2020-089 | 03 - Central | 533767 | MULBERY2 | 69 | 8.3853 | 8.3974 | 0.0121
GEN-2020-089 | 03 - Central | 533774 | SHEFFLD2 | 69 | 4.4124 | 4.4182 | 0.0058
GEN-2020-089 | 03 - Central | 533775 | FRONTEN2 | 69 | 8.8227 | 8.8356 | 0.0129
GEN-2020-089 | 03 - Central | 533778 | NEOSHOS2 | 69 | 24.0517 | 24.0702 | 0.0185
GEN-2020-089 | 03 - Central | 533876 | FRANKLIN2 | 69 | 11.4219 | 11.4467 | 0.0248
GEN-2020-089 | 03 - Central | 543055 | SEOTTWA5 | 161 | 8.2383 | 8.2466 | 0.0083
GEN-2020-089 | 03 - Central | 543057 | BUCYRUS5 | 161 | 21.2052 | 21.2232 | 0.018
GEN-2020-089 | 03 - Central | 543058 | NLOUISB5 | 161 | 9.3659 | 9.3694 | 0.0035
GEN-2020-089 | 03 - Central | 543065 | CNTRVIL5 | 161 | 6.1623 | 6.2884 | 0.1261
GEN-2020-089 | 03 - Central | 543066 | S.OTTWA5 | 161 | 8.0727 | 8.0822 | 0.0095
GEN-2020-089 | 03 - Central | 543067 | CENTENL5 | 161 | 10.8323 | 10.8747 | 0.0424
GEN-2020-089 | 03 - Central | 543068 | WAGSTAF5 | 161 | 14.5734 | 14.5945 | 0.0211
GEN-2020-089 | 03 - Central | 543069 | PAOLA 5 | 161 | 10.9167 | 10.9709 | 0.0542
GEN-2020-089 | 03 - Central | 543112 | OSAWAT 5 | 161 | 10.8211 | 10.8742 | 0.0531
GEN-2020-089 | 03 - Central | 543135 | OSAWTM_CAP5 | 161 | 10.1832 | 10.2302 | 0.047
GEN-2020-089 | 03 - Central | 543166 | NEASTOTTW5 | 161 | 7.0161 | 7.0221 | 0.006
GEN-2020-089 | 03 - Central | 543650 | DAKOTA_5 | 161 | 6.874 | 7.2173 | 0.3433
GEN-2020-089 | 03 - Central | 543651 | PRQN_WIND5 | 161 | 5.8665 | 6.1042 | 0.2377
GEN-2020-089 | 03 - Central | 547469 | RIV4525 | 161 | 24.7971 | 24.8094 | 0.0123
GEN-2020-089 | 03 - Central | 547476 | ASB349 5 | 161 | 11.2919 | 11.3142 | 0.0223
GEN-2020-089 | 03 - Central | 547502 | RIV167 5 | 161 | 22.9576 | 22.968 | 0.0104
GEN-2020-089 | 03 - Central | 547503 | RIV452T 5 | 161 | 24.3233 | 24.335 | 0.0117
GEN-2020-089 | 03 - Central | 588500 | GEN-2017-005 | 161 | 6.8907 | 6.9722 | 0.0815
GEN-2020-089 | 03 - Central | 588504 | G17-005-TAP | 161 | 6.9739 | 7.0576 | 0.0837
GEN-2020-089 | 03 - Central | 589200 | GEN-2017-082 | 161 | 7.6705 | 7.6802 | 0.0097
GEN-2020-089 | 03 - Central | 760242 | GEN-2017-188 | 161 | 2.0295 | 2.0299 | 0.0004
GEN-2020-089 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.6719 | 19.6744 | 0.0025
GEN-2020-089 | 03 - Central | 760921 | G17-209-TAP | 345 | 20.1967 | 20.1994 | 0.0027
GEN-2020-089 | 03 - Central | 762416 | ASG-2018-011 | 161 | 3.0633 | 3.0646 | 0.0013
GEN-2020-089 | 03 - Central | 762680 | GEN-2018-032 | 345 | 12.1369 | 12.1425 | 0.0056
GEN-2020-089 | 03 - Central | 764300 | GEN-2020-079 | 161 | 15.4055 | 15.4113 | 0.0058
GEN-2020-089 | 03 - Central | 764310 | G20-079-TAP | 161 | 18.5983 | 18.6071 | 0.0088
GEN-2020-089 | 03 - Central | 764390 | GEN-2020-073 | 161 | 8.3855 | 8.3928 | 0.0073
GEN-2020-089 | 03 - Central | 764400 | G20-073-TAP | 161 | 8.4663 | 8.4738 | 0.0075
GEN-2020-089 | 03 - Central | 765100 | GEN-2020-052 | 345 | 9.9254 | 9.928 | 0.0026
GEN-2020-089 | 03 - Central | 765110 | G20-052-TAP | 345 | 13.1141 | 13.1185 | 0.0044
GEN-2020-089 | 03 - Central | 765175 | GEN-2020-089 | 161 | 3.9063 | 4.2644 | 0.3581
GEN-2020-090 | 03 - Central | 300042 | 7HUBEN | 345 | 10.5741 | 10.5775 | 0.0034
GEN-2020-090 | 03 - Central | 300045 | 7MORGAN | 345 | 13.9749 | 13.9925 | 0.0176
GEN-2020-090 | 03 - Central | 300051 | 7FRANKSRCTP | 345 | 16.1333 | 16.1346 | 0.0013
GEN-2020-090 | 03 - Central | 300069 | 5CHOTEAU1 | 161 | 42.5527 | 42.56 | 0.0073
GEN-2020-090 | 03 - Central | 300070 | 5CLARK | 161 | 8.1881 | 8.1909 | 0.0028
GEN-2020-090 | 03 - Central | 300088 | 5HUBEN | 161 | 15.9237 | 15.9261 | 0.0024
GEN-2020-090 | 03 - Central | 300101 | 5MORGAN | 161 | 19.7392 | 19.749 | 0.0098
GEN-2020-090 | 03 - Central | 300651 | 2LAMR | 69 | 10.1498 | 10.1521 | 0.0023
GEN-2020-090 | 03 - Central | 300652 | 2LAMRCTS | 69 | 3.9484 | 3.9487 | 0.0003
GEN-2020-090 | 03 - Central | 300685 | 2LAMARPT | 69 | 8.5678 | 8.5695 | 0.0017
GEN-2020-090 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 15.972 | 16.1277 | 0.1557
GEN-2020-090 | 03 - Central | 300740 | 7SPORTSMAN | 345 | 24.609 | 24.6206 | 0.0116
GEN-2020-090 | 03 - Central | 300741 | 5SPORTSMAN | 161 | 40.9267 | 40.935 | 0.0083
GEN-2020-090 | 03 - Central | 300794 | 5LAMAR | 161 | 8.9378 | 8.9451 | 0.0073
GEN-2020-090 | 03 - Central | 300949 | 7JASPER | 345 | 12.9726 | 13.0411 | 0.0685
GEN-2020-090 | 03 - Central | 300950 | 5JASPER | 161 | 13.0793 | 13.1047 | 0.0254
GEN-2020-090 | 03 - Central | 301348 | 5CHOTEAU2 | 161 | 42.5527 | 42.56 | 0.0073
GEN-2020-090 | 03 - Central | 301554 | 7FRANKSRCT | 345 | 16.0888 | 16.0901 | 0.0013
GEN-2020-090 | 03 - Central | 301622 | 5MORGANXF2 | 161 | 19.7379 | 19.7477 | 0.0098
GEN-2020-090 | 03 - Central | 506935 | FLINTCR7 | 345 | 15.7208 | 15.7233 | 0.0025
GEN-2020-090 | 03 - Central | 510379 | DELWARE4 | 138 | 11.5224 | 11.5244 | 0.002
GEN-2020-090 | 03 - Central | 510380 | DELWARE7 | 345 | 12.2145 | 12.2209 | 0.0064
GEN-2020-090 | 03 - Central | 510406 | N.E.S.-7 | 345 | 19.4241 | 19.4283 | 0.0042
GEN-2020-090 | 03 - Central | 512648 | MAID 5 | 161 | 44.7866 | 44.7942 | 0.0076
GEN-2020-090 | 03 - Central | 512650 | GRDA1 7 | 345 | 26.9718 | 26.9828 | 0.011
GEN-2020-090 | 03 - Central | 512651 | CLARMR 5 | 161 | 13.1803 | 13.1807 | 0.0004
GEN-2020-090 | 03 - Central | 512656 | GRDA1 5 | 161 | 44.3133 | 44.321 | 0.0077
GEN-2020-090 | 03 - Central | 512700 | WAGNOR 5 | 161 | 9.945 | 9.9452 | 0.0002
GEN-2020-090 | 03 - Central | 512727 | GRDA1 2 | 69 | 12.553 | 12.5532 | 0.0002
GEN-2020-090 | 03 - Central | 512728 | ARKLIN2 | 69 | 3.837 | 3.837 | 0
GEN-2020-090 | 03 - Central | 512742 | WMAIN ST5 | 161 | 28.1839 | 28.187 | 0.0031
GEN-2020-090 | 03 - Central | 512745 | SSLINC2 | 69 | 2.8862 | 2.8862 | 0
GEN-2020-090 | 03 - Central | 512746 | SSNORT2 | 69 | 2.9423 | 2.9423 | 0
GEN-2020-090 | 03 - Central | 512747 | SSNEWN2 | 69 | 3.1914 | 3.1914 | 0
GEN-2020-090 | 03 - Central | 512750 | TONECE7 | 345 | 15.4926 | 15.4951 | 0.0025
GEN-2020-090 | 03 - Central | 512751 | TONECE5 | 161 | 15.5496 | 15.5505 | 0.0009
GEN-2020-090 | 03 - Central | 512753 | TONNEC2 | 69 | 4.9591 | 4.9591 | 0
GEN-2020-090 | 03 - Central | 512756 | TONECESTR2 | 69 | 3.9509 | 3.9509 | 0
GEN-2020-090 | 03 - Central | 512865 | GREC TAP5 | 345 | 25.7898 | 25.7994 | 0.0096
GEN-2020-090 | 03 - Central | 513590 | CUSTDAY1 5 | 161 | 16.8387 | 16.8404 | 0.0017
GEN-2020-090 | 03 - Central | 513591 | HERRON 5 | 161 | 17.2558 | 17.2577 | 0.0019
GEN-2020-090 | 03 - Central | 513593 | IGLOOV1 5 | 161 | 17.4527 | 17.4547 | 0.002
GEN-2020-090 | 03 - Central | 513595 | IGLOOV2 5 | 161 | 17.4527 | 17.4547 | 0.002
GEN-2020-090 | 03 - Central | 513596 | IGLOOV 7 | 345 | 20.5094 | 20.5151 | 0.0057
GEN-2020-090 | 03 - Central | 514825 | KAYWIND7 | 345 | 12.6273 | 12.6287 | 0.0014
GEN-2020-090 | 03 - Central | 515576 | RANCHRD7 | 345 | 13.6032 | 13.6043 | 0.0011
GEN-2020-090 | 03 - Central | 515621 | OPENSKY7 | 345 | 12.6606 | 12.662 | 0.0014
GEN-2020-090 | 03 - Central | 515688 | FRNTWND7 | 345 | 10.7774 | 10.7781 | 0.0007
GEN-2020-090 | 03 - Central | 516066 | FRNT2WD7 | 345 | 10.55 | 10.5507 | 0.0007
GEN-2020-090 | 03 - Central | 529200 | OMCDLEC7 | 345 | 13.5825 | 13.5837 | 0.0012
GEN-2020-090 | 03 - Central | 532768 | EMPEC 7 | 345 | 16.8299 | 16.8308 | 0.0009
GEN-2020-090 | 03 - Central | 532769 | LANG 7 | 345 | 16.6443 | 16.6452 | 0.0009
GEN-2020-090 | 03 - Central | 532770 | MORRIS 7 | 345 | 12.9092 | 12.9096 | 0.0004
GEN-2020-090 | 03 - Central | 532771 | RENO 7 | 345 | 11.5998 | 11.6004 | 0.0006
GEN-2020-090 | 03 - Central | 532774 | SWISVAL7 | 345 | 17.6329 | 17.6348 | 0.0019
GEN-2020-090 | 03 - Central | 532775 | 87TH 7 | 345 | 21.5414 | 21.5435 | 0.0021
GEN-2020-090 | 03 - Central | 532776 | READWF 7 | 345 | 14.0672 | 14.0678 | 0.0006
GEN-2020-090 | 03 - Central | 532777 | G17-009-TAP | 345 | 12.052 | 12.069 | 0.017
GEN-2020-090 | 03 - Central | 532778 | GEN-2017-009 | 345 | 11.1383 | 11.1528 | 0.0145
GEN-2020-090 | 03 - Central | 532780 | CANEYRV7 | 345 | 9.9351 | 9.9404 | 0.0053
GEN-2020-090 | 03 - Central | 532781 | CANEYWF7 | 345 | 9.6544 | 9.6594 | 0.005
GEN-2020-090 | 03 - Central | 532782 | BUFFALO7 | 345 | 21.3631 | 21.3663 | 0.0032
GEN-2020-090 | 03 - Central | 532783 | KINGMAN7 | 345 | 7.1919 | 7.1921 | 0.0002
GEN-2020-090 | 03 - Central | 532784 | NINN1WF7 | 345 | 6.0073 | 6.0075 | 0.0002
GEN-2020-090 | 03 - Central | 532785 | PRATTWF7 | 345 | 5.0143 | 5.0145 | 0.0002
GEN-2020-090 | 03 - Central | 532791 | BENTON 7 | 345 | 20.253 | 20.2629 | 0.0099
GEN-2020-090 | 03 - Central | 532792 | FR2EAST7 | 345 | 7.1035 | 7.1037 | 0.0002
GEN-2020-090 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18.4817 | 18.5326 | 0.0509
GEN-2020-090 | 03 - Central | 532794 | ROSEHIL7 | 345 | 19.6675 | 19.6793 | 0.0118
GEN-2020-090 | 03 - Central | 532795 | FR2WEST7 | 345 | 5.7165 | 5.7166 | 0.0001
GEN-2020-090 | 03 - Central | 532796 | WICHITA7 | 345 | 24.5021 | 24.5073 | 0.0052
GEN-2020-090 | 03 - Central | 532797 | WOLFCRK7 | 345 | 22.0423 | 22.1344 | 0.0921
GEN-2020-090 | 03 - Central | 532798 | VIOLA 7 | 345 | 14.3201 | 14.3211 | 0.001
GEN-2020-090 | 03 - Central | 532799 | WAVERLY7 | 345 | 18.5572 | 18.6143 | 0.0571
GEN-2020-090 | 03 - Central | 532800 | LATHAMS7 | 345 | 10.5965 | 10.6019 | 0.0054
GEN-2020-090 | 03 - Central | 532801 | ELKRVR17 | 345 | 9.3886 | 9.3928 | 0.0042
GEN-2020-090 | 03 - Central | 532802 | WAVERTX7 | 345 | 15.1508 | 15.1886 | 0.0378
GEN-2020-090 | 03 - Central | 532851 | AUBURN 6 | 230 | 13.7399 | 13.7402 | 0.0003
GEN-2020-090 | 03 - Central | 532853 | LAWHILL6 | 230 | 14.1384 | 14.1387 | 0.0003
GEN-2020-090 | 03 - Central | 532854 | LEC U5 6 | 230 | 14.0053 | 14.0056 | 0.0003
GEN-2020-090 | 03 - Central | 532856 | SWISVAL6 | 230 | 22.5985 | 22.5998 | 0.0013
GEN-2020-090 | 03 - Central | 532857 | TECHILL6 | 230 | 11.1787 | 11.179 | 0.0003
GEN-2020-090 | 03 - Central | 532926 | BAKER 2 | 69 | 5.1284 | 5.1286 | 0.0002
GEN-2020-090 | 03 - Central | 532934 | MARMTNE5 | 161 | 8.4102 | 8.411 | 0.0008
GEN-2020-090 | 03 - Central | 532935 | MARMTNW5 | 161 | 8.4064 | 8.4072 | 0.0008
GEN-2020-090 | 03 - Central | 532937 | NEOSHO 5 | 161 | 23.9218 | 23.946 | 0.0242
GEN-2020-090 | 03 - Central | 532986 | BENTON 4 | 138 | 29.152 | 29.159 | 0.007
GEN-2020-090 | 03 - Central | 532988 | BELAIRE4 | 138 | 19.6326 | 19.6358 | 0.0032
GEN-2020-090 | 03 - Central | 532990 | MIDIAN 4 | 138 | 11.4006 | 11.4017 | 0.0011
GEN-2020-090 | 03 - Central | 532991 | WEAVER 4 | 138 | 22.9635 | 22.9679 | 0.0044
GEN-2020-090 | 03 - Central | 532993 | TALLGRS4 | 138 | 10.8072 | 10.8082 | 0.001
GEN-2020-090 | 03 - Central | 532994 | TCBURNS4 | 138 | 4.1533 | 4.1534 | 0.0001
GEN-2020-090 | 03 - Central | 533005 | NEPARSN4 | 138 | 13.1501 | 13.1555 | 0.0054
GEN-2020-090 | 03 - Central | 533008 | TV1MNDV4 | 138 | 7.2662 | 7.2674 | 0.0012
GEN-2020-090 | 03 - Central | 533020 | NEOSHOS4 | 138 | 25.4934 | 25.5172 | 0.0238
GEN-2020-090 | 03 - Central | 533021 | NEOSHO 4 | 138 | 25.5368 | 25.5606 | 0.0238
GEN-2020-090 | 03 - Central | 533022 | NEOSHON4 | 138 | 25.4166 | 25.4402 | 0.0236
GEN-2020-090 | 03 - Central | 533024 | 29TH 4 | 138 | 20.2983 | 20.3017 | 0.0034
GEN-2020-090 | 03 - Central | 533026 | ANDOVER4 | 138 | 18.5184 | 18.5212 | 0.0028
GEN-2020-090 | 03 - Central | 533029 | 59TH ST4 | 138 | 17.9061 | 17.9079 | 0.0018
GEN-2020-090 | 03 - Central | 533030 | BOEINGE4 | 138 | 17.481 | 17.4832 | 0.0022
GEN-2020-090 | 03 - Central | 533032 | BU11PON4 | 138 | 15.6422 | 15.6441 | 0.0019
GEN-2020-090 | 03 - Central | 533039 | ELPASO 4 | 138 | 25.8047 | 25.8094 | 0.0047
GEN-2020-090 | 03 - Central | 533040 | EVANS N4 | 138 | 32.9628 | 32.9669 | 0.0041
GEN-2020-090 | 03 - Central | 533052 | PARKCTY4 | 138 | 20.9374 | 20.9403 | 0.0029
GEN-2020-090 | 03 - Central | 533059 | ELPASOE4 | 138 | 25.7609 | 25.7657 | 0.0048
GEN-2020-090 | 03 - Central | 533062 | ROSEHIL4 | 138 | 32.2697 | 32.2797 | 0.01
GEN-2020-090 | 03 - Central | 533067 | SPRNGDL4 | 138 | 15.0065 | 15.0083 | 0.0018
GEN-2020-090 | 03 - Central | 533068 | STEARMN4 | 138 | 20.1951 | 20.1982 | 0.0031
GEN-2020-090 | 03 - Central | 533604 | WEAVER 2 | 69 | 12.3959 | 12.3965 | 0.0006
GEN-2020-090 | 03 - Central | 533624 | BURLING2 | 69 | 3.5603 | 3.5606 | 0.0003
GEN-2020-090 | 03 - Central | 533625 | BURLIND2 | 69 | 3.1727 | 3.173 | 0.0003
GEN-2020-090 | 03 - Central | 533626 | BURLJCT2 | 69 | 5.1827 | 5.1833 | 0.0006
GEN-2020-090 | 03 - Central | 533628 | CC1BURL2 | 69 | 3.5588 | 3.5591 | 0.0003
GEN-2020-090 | 03 - Central | 533629 | CC2SHAR2 | 69 | 4.8471 | 4.8477 | 0.0006
GEN-2020-090 | 03 - Central | 533630 | CC3WEST2 | 69 | 4.7831 | 4.7836 | 0.0005
GEN-2020-090 | 03 - Central | 533636 | GREEN 2 | 69 | 4.2407 | 4.241 | 0.0003
GEN-2020-090 | 03 - Central | 533639 | MARMATN2 | 69 | 9.0328 | 9.0332 | 0.0004
GEN-2020-090 | 03 - Central | 533653 | WOLFCRK2 | 69 | 6.277 | 6.2781 | 0.0011
GEN-2020-090 | 03 - Central | 533702 | ORDNCE 2 | 69 | 6.3324 | 6.333 | 0.0006
GEN-2020-090 | 03 - Central | 533703 | ORDNJCT2 | 69 | 8.772 | 8.7733 | 0.0013
GEN-2020-090 | 03 - Central | 533758 | CRAWFOR2 | 69 | 7.572 | 7.5728 | 0.0008
GEN-2020-090 | 03 - Central | 533768 | NEOSHON2 | 69 | 24.0354 | 24.0451 | 0.0097
GEN-2020-090 | 03 - Central | 533778 | NEOSHOS2 | 69 | 24.0605 | 24.0702 | 0.0097
GEN-2020-090 | 03 - Central | 541198 | PECULR 7 | 345 | 21.2291 | 21.2331 | 0.004
GEN-2020-090 | 03 - Central | 541200 | PHILL 7 | 345 | 19.1423 | 19.1445 | 0.0022
GEN-2020-090 | 03 - Central | 541341 | S.HARP 5 | 161 | 21.2773 | 21.2789 | 0.0016
GEN-2020-090 | 03 - Central | 541342 | PECULR 5 | 161 | 23.4197 | 23.4216 | 0.0019
GEN-2020-090 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2.6785 | 2.6785 | 0
GEN-2020-090 | 03 - Central | 542940 | ATLNTIC7 | 345 | 22.1826 | 22.188 | 0.0054
GEN-2020-090 | 03 - Central | 542945 | CRAIG_CAP 5 | 161 | 35.3164 | 35.3191 | 0.0027
GEN-2020-090 | 03 - Central | 542965 | W.GRDNR7 | 345 | 31.1568 | 31.1725 | 0.0157
GEN-2020-090 | 03 - Central | 542966 | WGARDNR5 | 161 | 30.8121 | 30.8153 | 0.0032
GEN-2020-090 | 03 - Central | 542968 | STILWEL7 | 345 | 26.7708 | 26.7794 | 0.0086
GEN-2020-090 | 03 - Central | 542969 | STILWEL5 | 161 | 41.6775 | 41.684 | 0.0065
GEN-2020-090 | 03 - Central | 542977 | CRAIG 7 | 345 | 22.7824 | 22.7852 | 0.0028
GEN-2020-090 | 03 - Central | 542978 | CRAIG 5 | 161 | 44.3865 | 44.3908 | 0.0043
GEN-2020-090 | 03 - Central | 542981 | LACYGNE7 | 345 | 28.5883 | 28.609 | 0.0207
GEN-2020-090 | 03 - Central | 542994 | HICKMAN5 | 161 | 20.1226 | 20.1235 | 0.0009
GEN-2020-090 | 03 - Central | 543031 | SHWNMSN5 | 161 | 37.2367 | 37.2389 | 0.0022
GEN-2020-090 | 03 - Central | 543044 | MOONLT 5 | 161 | 18.0817 | 18.0827 | 0.001
GEN-2020-090 | 03 - Central | 543049 | CEDRCRK5 | 161 | 31.3502 | 31.3524 | 0.0022
GEN-2020-090 | 03 - Central | 543050 | ANTIOCH5 | 161 | 23.5094 | 23.5112 | 0.0018
GEN-2020-090 | 03 - Central | 543053 | REDEL 5 | 161 | 25.3379 | 25.3399 | 0.002
GEN-2020-090 | 03 - Central | 543054 | CEDARNL5 | 161 | 10.9408 | 10.9412 | 0.0004
GEN-2020-090 | 03 - Central | 543056 | GARDNER5 | 161 | 16.8184 | 16.8192 | 0.0008
GEN-2020-090 | 03 - Central | 543057 | BUCYRUS5 | 161 | 21.2216 | 21.2232 | 0.0016
GEN-2020-090 | 03 - Central | 543058 | NLOUISB5 | 161 | 9.3691 | 9.3694 | 0.0003
GEN-2020-090 | 03 - Central | 543077 | PLSTVAL5 | 161 | 10.6967 | 10.6971 | 0.0004
GEN-2020-090 | 03 - Central | 543105 | BULLCRK5 | 161 | 29.785 | 29.7878 | 0.0028
GEN-2020-090 | 03 - Central | 543126 | LACKMAN5 | 161 | 13.9423 | 13.9429 | 0.0006
GEN-2020-090 | 03 - Central | 543132 | BNSF 5 | 161 | 22.5512 | 22.5528 | 0.0016
GEN-2020-090 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27.8109 | 27.8304 | 0.0195
GEN-2020-090 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27.8109 | 27.8304 | 0.0195
GEN-2020-090 | 03 - Central | 543659 | LACYGNE2 | 69 | 2.8177 | 2.8177 | 0
GEN-2020-090 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 0.6739 | 0.6739 | 0
GEN-2020-090 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 0.6454 | 0.6454 | 0
GEN-2020-090 | 03 - Central | 547469 | RIV4525 | 161 | 24.8059 | 24.8094 | 0.0035
GEN-2020-090 | 03 - Central | 547501 | RIV453 5 | 161 | 23.3963 | 23.3993 | 0.003
GEN-2020-090 | 03 - Central | 547502 | RIV167 5 | 161 | 22.9651 | 22.968 | 0.0029
GEN-2020-090 | 03 - Central | 547503 | RIV452T 5 | 161 | 24.3317 | 24.335 | 0.0033
GEN-2020-090 | 03 - Central | 549969 | BROOKLINE 5 | 161 | 28.4815 | 28.4898 | 0.0083
GEN-2020-090 | 03 - Central | 549984 | BROOKLINE 7 | 345 | 11.9499 | 11.9564 | 0.0065
GEN-2020-090 | 03 - Central | 560053 | G15-052T | 345 | 13.4609 | 13.4639 | 0.003
GEN-2020-090 | 03 - Central | 562476 | G14-001-TAP | 345 | 10.841 | 10.8417 | 0.0007
GEN-2020-090 | 03 - Central | 578530 | FR3HV | 345 | 5.249 | 5.2491 | 0.0001
GEN-2020-090 | 03 - Central | 583850 | GEN-2014-001 | 345 | 7.307 | 7.3073 | 0.0003
GEN-2020-090 | 03 - Central | 584900 | GEN-2015-052 | 345 | 13.4108 | 13.4138 | 0.003
GEN-2020-090 | 03 - Central | 587500 | GEN-2016-073 | 345 | 15.7543 | 15.756 | 0.0017
GEN-2020-090 | 03 - Central | 588360 | GEN-2016-153 | 345 | 7.47 | 7.4702 | 0.0002
GEN-2020-090 | 03 - Central | 588364 | G16-153-TAP | 345 | 7.8322 | 7.8325 | 0.0003
GEN-2020-090 | 03 - Central | 588990 | GEN-2017-061 | 161 | 22.5903 | 22.5923 | 0.002
GEN-2020-090 | 03 - Central | 589060 | GEN-2017-068 | 138 | 29.9338 | 29.9372 | 0.0034
GEN-2020-090 | 03 - Central | 589240 | GEN-2017-086 | 345 | 6.549 | 6.5492 | 0.0002
GEN-2020-090 | 03 - Central | 709500 | GI-95_POI | 345 | 8.3384 | 8.3444 | 0.006
GEN-2020-090 | 03 - Central | 709501 | GI-95_HV | 345 | 8.3384 | 8.3444 | 0.006
GEN-2020-090 | 03 - Central | 760284 | GEN-2017-220 | 345 | 21.2487 | 21.2519 | 0.0032
GEN-2020-090 | 03 - Central | 760641 | GEN-2017-226 | 138 | 32.7848 | 32.7889 | 0.0041
GEN-2020-090 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19.6623 | 19.6744 | 0.0121
GEN-2020-090 | 03 - Central | 760921 | G17-209-TAP | 345 | 20.1866 | 20.1994 | 0.0128
GEN-2020-090 | 03 - Central | 761271 | GEN-2017-108 | 161 | 7.5439 | 7.5441 | 0.0002
GEN-2020-090 | 03 - Central | 761278 | G17-108-TAP | 161 | 12.4201 | 12.4206 | 0.0005
GEN-2020-090 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5.3929 | 5.3931 | 0.0002
GEN-2020-090 | 03 - Central | 762279 | GEN-2017-195 | 345 | 31.0644 | 31.08 | 0.0156
GEN-2020-090 | 03 - Central | 762300 | GEN-2017-196 | 345 | 30.9668 | 30.9823 | 0.0155
GEN-2020-090 | 03 - Central | 762405 | ASG-2018-010 | 161 | 3.3626 | 3.3626 | 0
GEN-2020-090 | 03 - Central | 762680 | GEN-2018-032 | 345 | 12.1206 | 12.1425 | 0.0219
GEN-2020-090 | 03 - Central | 762922 | GEN-2018-057 | 138 | 17.8363 | 17.8374 | 0.0011
GEN-2020-090 | 03 - Central | 762999 | GEN-2018-064 | 69 | 3.6738 | 3.6739 | 0.0001
GEN-2020-090 | 03 - Central | 763065 | GEN-2018-071 | 345 | 13.1515 | 13.1526 | 0.0011
GEN-2020-090 | 03 - Central | 763069 | G18-071_TAP | 345 | 13.2011 | 13.2022 | 0.0011
GEN-2020-090 | 03 - Central | 763472 | GEN-2019-002 | 161 | 41.5939 | 41.6004 | 0.0065
GEN-2020-090 | 03 - Central | 764300 | GEN-2020-079 | 161 | 15.4092 | 15.4113 | 0.0021
GEN-2020-090 | 03 - Central | 764310 | G20-079-TAP | 161 | 18.6039 | 18.6071 | 0.0032
GEN-2020-090 | 03 - Central | 764375 | GEN-2020-058 | 345 | 22.1375 | 22.1428 | 0.0053
GEN-2020-090 | 03 - Central | 764390 | GEN-2020-073 | 161 | 8.3927 | 8.3928 | 0.0001
GEN-2020-090 | 03 - Central | 764400 | G20-073-TAP | 161 | 8.4737 | 8.4738 | 0.0001
GEN-2020-090 | 03 - Central | 765100 | GEN-2020-052 | 345 | 9.9183 | 9.928 | 0.0097
GEN-2020-090 | 03 - Central | 765110 | G20-052-TAP | 345 | 13.1013 | 13.1185 | 0.0172
GEN-2020-090 | 03 - Central | 765115 | GEN-2020-057 | 345 | 22.1376 | 22.1429 | 0.0053
GEN-2020-090 | 03 - Central | 765130 | GEN-2020-071 | 230 | 11.3788 | 11.3791 | 0.0003
GEN-2020-090 | 03 - Central | 765140 | G20-071-TAP | 230 | 11.3788 | 11.3791 | 0.0003
GEN-2020-090 | 03 - Central | 765145 | GEN-2020-076 | 345 | 12.5451 | 12.5518 | 0.0067
GEN-2020-090 | 03 - Central | 765155 | G20-076-TAP | 345 | 12.5528 | 12.5595 | 0.0067
GEN-2020-090 | 03 - Central | 765160 | GEN-2020-086 | 345 | 12.5458 | 12.5524 | 0.0066
GEN-2020-090 | 03 - Central | 765190 | GEN-2020-090 | 345 | 8.3971 | 8.7262 | 0.3291
GEN-2020-090 | 03 - Central | 765200 | G20-090-TAP | 345 | 9.6256 | 9.9531 | 0.3275
GEN-2020-090 | 03 - Central | 766260 | GEN-2020-007 | 345 | 25.1393 | 25.1555 | 0.0162
GEN-2020-092 | 04 - Southeast | 510366 | MCARBDE4 | 138 | 7.6902 | 7.991 | 0.3008
GEN-2020-092 | 04 - Southeast | 510366 | MCARBDE4 | 138 | 7.6902 | 7.991 | 0.3008
GEN-2020-092 | 04 - Southeast | 510373 | CHOUTEA4 | 138 | 6.965 | 7.1032 | 0.1382
GEN-2020-092 | 04 - Southeast | 510387 | ADAIR--2 | 69 | 5.7906 | 5.8195 | 0.0289
GEN-2020-092 | 04 - Southeast | 510398 | BIRDHOL4 | 138 | 4.8389 | 4.9059 | 0.067
GEN-2020-092 | 04 - Southeast | 510399 | LSTAR--3 | 115 | 10.6978 | 10.8055 | 0.1077
GEN-2020-092 | 04 - Southeast | 510400 | PRY-JCT2 | 69 | 11.1076 | 11.2681 | 0.1605
GEN-2020-092 | 04 - Southeast | 510401 | EXCLART4 | 138 | 7.218 | 7.4006 | 0.1826
GEN-2020-092 | 04 - Southeast | 510402 | GROVE | 138 | 5.2113 | 5.2334 | 0.0221
GEN-2020-092 | 04 - Southeast | 510404 | VINITA-2 | 69 | 6.6856 | 6.6919 | 0.0063
GEN-2020-092 | 04 - Southeast | 510405 | EXPCLAR4 | 138 | 5.0825 | 5.1728 | 0.0903
GEN-2020-092 | 04 - Southeast | 510407 | PRY-JCT3 | 115 | 9.2461 | 9.395 | 0.1489
GEN-2020-092 | 04 - Southeast | 510408 | PCP-TAP2 | 69 | 7.8707 | 7.8991 | 0.0284
GEN-2020-092 | 04 - Southeast | 510411 | GROVE | 161 | 5.7001 | 5.7125 | 0.0124
GEN-2020-092 | 04 - Southeast | 510416 | HUNTAP-2 | 69 | 8.8063 | 8.8297 | 0.0234
GEN-2020-092 | 04 - Southeast | 510418 | VINTAJC2 | 69 | 6.3506 | 6.355 | 0.0044
GEN-2020-092 | 04 - Southeast | 510419 | PRY-JCT4 | 138 | 8.6231 | 9.0176 | 0.3945
GEN-2020-092 | 04 - Southeast | 510421 | JAY | 138 | 4.5767 | 4.6104 | 0.0337
GEN-2020-092 | 04 - Southeast | 510423 | L | 115 | 16.3453 | 16.432 | 0.0867
GEN-2020-092 | 04 - Southeast | 510425 | NEOHOME2 | 69 | 5.6439 | 5.6583 | 0.0144
GEN-2020-092 | 04 - Southeast | 510431 | PRY_CRK4 | 138 | 7.3003 | 7.5142 | 0.2139
GEN-2020-092 | 04 - Southeast | 510437 | ROCKPT-4 | 138 | 8.2779 | 8.3392 | 0.0613
GEN-2020-092 | 04 - Southeast | 512622 | PRYORC32 | 69 | 9.331 | 9.3711 | 0.0401
GEN-2020-092 | 04 - Southeast | 512634 | KERR | 115 | 17.4145 | 17.5008 | 0.0863
GEN-2020-092 | 04 - Southeast | 512639 | PRY0RC22 | 69 | 9.7094 | 9.7453 | 0.0359
GEN-2020-092 | 04 - Southeast | 512680 | ESH | 69 | 6.4215 | 6.4266 | 0.0051
GEN-2020-092 | 04 - Southeast | 512719 | COWSKIN | 138 | 4.4297 | 4.4451 | 0.0154
GEN-2020-092 | 04 - Southeast | 512810 | PRYORC12 | 69 | 9.8566 | 9.9198 | 0.0632
GEN-2020-092 | 04 - Southeast | 589120 | GEN-2017-07 | 138 | 8.5781 | 8.9683 | 0.3902
GEN-2020-092 | 04 - Southeast | 589150 | GEN-2017-07 | 138 | 6.6894 | 6.8436 | 0.1542
GEN-2020-092 | 04 - Southeast | 764150 | GEN-2020-09 | 138 | 8.202 | 8.6226 | 0.4206
GEN-2020-092 | 04 - Southeast | 764160 | G20-092-TAP | 138 | 8.3065 | 8.7268 | 0.4203
GEN-2020-087 | 04 - Southeast | 511409 | TREASILD7 | 345 | 16.8876 | 17.2896 | 0.402
GEN-2020-087 | 04 - Southeast | 511422 | FLETCHR4 | 138 | 8.0194 | 8.0306 | 0.0112
GEN-2020-087 | 04 - Southeast | 511423 | FLE | 138 | 8.7847 | 8.7982 | 0.0135
GEN-2020-087 | 04 - Southeast | 511428 | LG-YEAR4 | 138 | 12.3876 | 12.4343 | 0.0467
GEN-2020-087 | 04 - Southeast | 511431 | LWS | 138 | 11.4642 | 11.5061 | 0.0419
GEN-2020-087 | 04 - Southeast | 511436 | COMANC-2 | 69 | 9.2768 | 9.2847 | 0.0079
GEN-2020-087 | 04 - Southeast | 511437 | COMANC-4 | 138 | 19.0155 | 19.1291 | 0.1136
GEN-2020-087 | 04 - Southeast | 511439 | LWSTAP | 138 | 11.9747 | 12.0203 | 0.0456
GEN-2020-087 | 04 - Southeast | 511451 | CYRIL--2 | 69 | 4.6522 | 4.6539 | 0.0017
GEN-2020-087 | 04 - Southeast | 511453 | DUNCAN-4 | 138 | 6.419 | 6.4264 | 0.0074
GEN-2020-087 | 04 - Southeast | 511456 | O.K.U.-7 | 345 | 7.069 | 7.1171 | 0.0481
GEN-2020-087 | 04 - Southeast | 511461 | FT.SILL2 | 69 | 5.9496 | 5.954 | 0.0044
GEN-2020-087 | 04 - Southeast | 511466 | L.E.S.-2 | 69 | 16.6612 | 16.7009 | 0.0397
GEN-2020-087 | 04 - Southeast | 511467 | L.E.S.-4 | 138 | 26.7864 | 27.0517 | 0.2653
GEN-2020-087 | 04 - Southeast | 511468 | L.E.S.-7 | 345 | 16.8437 | 17.3217 | 0.478
GEN-2020-087 | 04 - Southeast | 511469 | LGORE-N2 | 69 | 8.0249 | 8.0336 | 0.0087
GEN-2020-087 | 04 - Southeast | 511470 | LGORE-S2 | 69 | 6.9524 | 6.9593 | 0.0069
GEN-2020-087 | 04 - Southeast | 511471 | LWS-NTP4 | 138 | 12.1065 | 12.1536 | 0.0471
GEN-2020-087 | 04 - Southeast | 511473 | PO.HILL2 | 69 | 5.8305 | 5.8342 | 0.0037
GEN-2020-087 | 04 - Southeast | 511474 | SHERID4 | 138 | 12.8053 | 12.8605 | 0.0552
GEN-2020-087 | 04 - Southeast | 511477 | S.W.S.-4 | 138 | 32.9941 | 33.0598 | 0.0657
GEN-2020-087 | 04 - Southeast | 511486 | ELGINJT4 | 138 | 10.1348 | 10.1556 | 0.0208
GEN-2020-087 | 04 - Southeast | 511487 | ELGINJT2 | 69 | 8.5382 | 8.5453 | 0.0071
GEN-2020-087 | 04 - Southeast | 511488 | 112GORE4 | 138 | 13.2439 | 13.2972 | 0.0533
GEN-2020-087 | 04 - Southeast | 511494 | COMMTAP4 | 138 | 23.0504 | 23.2383 | 0.1879
GEN-2020-087 | 04 - Southeast | 511503 | LAW | 69 | 4.5369 | 4.5398 | 0.0029
GEN-2020-087 | 04 - Southeast | 511509 | 53CACHE4 | 138 | 12.1408 | 12.1888 | 0.048
GEN-2020-087 | 04 - Southeast | 511510 | LAIRGST4 | 138 | 12.8145 | 12.8638 | 0.0493
GEN-2020-087 | 04 - Southeast | 511512 | RPPAPER4 | 138 | 12.435 | 12.483 | 0.048
GEN-2020-087 | 04 - Southeast | 511524 | L-DISTP2 | 69 | 8.5923 | 8.5989 | 0.0066
GEN-2020-087 | 04 - Southeast | 511537 | ARTVLTP4 | 138 | 12.1611 | 12.2093 | 0.0482
GEN-2020-087 | 04 - Southeast | 511538 | ARTVILL4 | 138 | 8.701 | 8.7257 | 0.0247
GEN-2020-087 | 04 - Southeast | 511553 | CHISHOLM7 | 345 | 13.1887 | 13.2045 | 0.0158
GEN-2020-087 | 04 - Southeast | 511557 | CHISHOLM6 | 230 | 12.556 | 12.5631 | 0.0071
GEN-2020-087 | 04 - Southeast | 511563 | ELSWORTH | 138 | 10.0547 | 10.0746 | 0.0199
GEN-2020-087 | 04 - Southeast | 511565 | OKLAUN | 345 | 7.0418 | 7.0896 | 0.0478
GEN-2020-087 | 04 - Southeast | 511568 | TERRYRD7 | 345 | 11.7758 | 11.8801 | 0.1043
GEN-2020-087 | 04 - Southeast | 511571 | RUSHSPR7 | 345 | 7.3018 | 7.3351 | 0.0333
GEN-2020-087 | 04 - Southeast | 514801 | MINCO | 345 | 26.1812 | 26.2868 | 0.1056
GEN-2020-087 | 04 - Southeast | 514880 | NORTWST7 | 345 | 33.5985 | 33.6247 | 0.0262
GEN-2020-087 | 04 - Southeast | 514898 | CIMARON4 | 138 | 45.9285 | 45.9573 | 0.0288
GEN-2020-087 | 04 - Southeast | 514901 | CIMARON7 | 345 | 36.6207 | 36.6785 | 0.0578
GEN-2020-087 | 04 - Southeast | 514929 | PLVALLY4 | 138 | 56.3264 | 56.3755 | 0.0491
GEN-2020-087 | 04 - Southeast | 514934 | DRAPER | 345 | 31.3757 | 31.4206 | 0.0449
GEN-2020-087 | 04 - Southeast | 515136 | SUNNYSD7 | 345 | 12.5203 | 12.5482 | 0.0279
GEN-2020-087 | 04 - Southeast | 515444 | MCNOWND7 | 345 | 26.0616 | 26.1662 | 0.1046
GEN-2020-087 | 04 - Southeast | 515458 | BORDER | 345 | 8.5439 | 8.5506 | 0.0067
GEN-2020-087 | 04 - Southeast | 515497 | MATHWSN7 | 345 | 33.8813 | 33.9142 | 0.0329
GEN-2020-087 | 04 - Southeast | 515549 | MNCWND37 | 345 | 15.1145 | 15.1479 | 0.0334
GEN-2020-087 | 04 - Southeast | 515610 | FSHRTAP7 | 345 | 16.5118 | 16.5227 | 0.0109
GEN-2020-087 | 04 - Southeast | 515800 | GRACMNT7 | 345 | 20.4668 | 20.7563 | 0.2895
GEN-2020-087 | 04 - Southeast | 515802 | GRACMNT4 | 138 | 32.6967 | 32.7851 | 0.0884
GEN-2020-087 | 04 - Southeast | 515939 | MNCWND47 | 345 | 10.3275 | 10.3425 | 0.015
GEN-2020-087 | 04 - Southeast | 516059 | BECKHAM7 | 345 | 13.0751 | 13.0904 | 0.0153
GEN-2020-087 | 04 - Southeast | 516096 | NORMHLL7 | 345 | 28.3474 | 28.39 | 0.0426
GEN-2020-087 | 04 - Southeast | 516097 | NORMHLL4 | 138 | 54.5997 | 54.6462 | 0.0465
GEN-2020-087 | 04 - Southeast | 520422 | SEQUOYAHJ4 | 138 | 25.194 | 25.2282 | 0.0342
GEN-2020-087 | 04 - Southeast | 520508 | CLVLDSW4 | 138 | 12.5712 | 12.5769 | 0.0057
GEN-2020-087 | 04 - Southeast | 520810 | ANADARK2 | 69 | 14.3122 | 14.3178 | 0.0056
GEN-2020-087 | 04 - Southeast | 520814 | ANADARK4 | 138 | 35.0625 | 35.129 | 0.0665
GEN-2020-087 | 04 - Southeast | 520923 | GEORGIA4 | 138 | 18.1729 | 18.1909 | 0.018
GEN-2020-087 | 04 - Southeast | 521017 | ONEY | 138 | 10.9147 | 10.9218 | 0.0071
GEN-2020-087 | 04 - Southeast | 521031 | POCASET4 | 138 | 8.0513 | 8.0538 | 0.0025
GEN-2020-087 | 04 - Southeast | 521088 | WASHITA2 | 69 | 9.0267 | 9.0288 | 0.0021
GEN-2020-087 | 04 - Southeast | 521089 | WASHITA4 | 138 | 29.2098 | 29.2654 | 0.0556
GEN-2020-087 | 04 - Southeast | 521103 | SLKHILLS | 138 | 6.4054 | 6.407 | 0.0016
GEN-2020-087 | 04 - Southeast | 521129 | CHERRYRD | 138 | 5.8631 | 5.865 | 0.0019
GEN-2020-087 | 04 - Southeast | 523961 | POTTER_CO | 345 | 13.608 | 13.6108 | 0.0028
GEN-2020-087 | 04 - Southeast | 525830 | TUCO_INT | 230 | 22.2985 | 22.3183 | 0.0198
GEN-2020-087 | 04 - Southeast | 525832 | TUCO_INT | 345 | 14.978 | 15.0061 | 0.0281
GEN-2020-087 | 04 - Southeast | 525850 | ELK_CT1 | 345 | 14.8236 | 14.851 | 0.0274
GEN-2020-087 | 04 - Southeast | 529304 | OMDUNCN4 | 138 | 6.6744 | 6.6835 | 0.0091
GEN-2020-087 | 04 - Southeast | 555234 | NSUB345 | 345 | 28.371 | 28.4136 | 0.0426
GEN-2020-087 | 04 - Southeast | 560022 | CRAWFISH_DR | 345 | 14.7463 | 14.775 | 0.0287
GEN-2020-087 | 04 - Southeast | 560078 | G16-037-TAP | 345 | 10.316 | 10.3447 | 0.0287
GEN-2020-087 | 04 - Southeast | 563259 | GEN-2015-09 | 345 | 7.0419 | 7.0727 | 0.0308
GEN-2020-087 | 04 - Southeast | 563269 | GEN-2015-09 | 345 | 10.81 | 10.887 | 0.077
GEN-2020-087 | 04 - Southeast | 587230 | GEN-2016-03 | 345 | 9.8205 | 9.8463 | 0.0258
GEN-2020-087 | 04 - Southeast | 587740 | GEN-2016-09 | 345 | 11.3739 | 11.5492 | 0.1753
GEN-2020-087 | 04 - Southeast | 587770 | GEN-2016-09 | 345 | 11.6868 | 11.8747 | 0.1879
GEN-2020-087 | 04 - Southeast | 587790 | GEN-2016-09 | 138 | 9.0139 | 9.0224 | 0.0085
GEN-2020-087 | 04 - Southeast | 587794 | G16-097-TAP | 138 | 11.1629 | 11.1761 | 0.0132
GEN-2020-087 | 04 - Southeast | 588760 | GEN-2017-03 | 345 | 4.5578 | 4.5778 | 0.02
GEN-2020-087 | 04 - Southeast | 599891 | OKLAUN | 345 | 4.0421 | 4.0421 | 0
GEN-2020-087 | 04 - Southeast | 760938 | G17-171-TAP | 345 | 13.0669 | 13.2607 | 0.1938
GEN-2020-087 | 04 - Southeast | 760939 | GEN-2017-17 | 345 | 12.9808 | 13.1719 | 0.1911
GEN-2020-087 | 04 - Southeast | 761229 | GEN-2017-15 | 345 | 25.1516 | 25.2488 | 0.0972
GEN-2020-087 | 04 - Southeast | 761250 | GEN-2017-23 | 345 | 25.2072 | 25.3047 | 0.0975
GEN-2020-087 | 04 - Southeast | 762216 | G17-151TAP | 345 | 8.3182 | 8.3328 | 0.0146
GEN-2020-087 | 04 - Southeast | 762217 | GEN-2017-15 | 345 | 5.8331 | 5.8403 | 0.0072
GEN-2020-087 | 04 - Southeast | 762460 | GEN-2018-01 | 345 | 8.8304 | 8.8755 | 0.0451
GEN-2020-087 | 04 - Southeast | 762467 | G18-015-TAP | 345 | 8.864 | 8.9095 | 0.0455
GEN-2020-087 | 04 - Southeast | 762900 | GEN-2018-05 | 345 | 4.9328 | 4.9469 | 0.0141
GEN-2020-087 | 04 - Southeast | 763215 | G18-092-PRO | 345 | 8.9853 | 9.0421 | 0.0568
GEN-2020-087 | 04 - Southeast | 763318 | GEN-2018-11 | 345 | 16.4597 | 16.9151 | 0.4554
GEN-2020-087 | 04 - Southeast | 764105 | GEN-2020-07 | 345 | 11.5272 | 11.566 | 0.0388
GEN-2020-087 | 04 - Southeast | 764115 | G20-074-TAP | 345 | 11.5331 | 11.572 | 0.0389
GEN-2020-087 | 04 - Southeast | 764540 | GEN-2020-07 | 345 | 15.3427 | 16.1068 | 0.7641
GEN-2020-087 | 04 - Southeast | 764550 | G20-075-TAP | 345 | 15.3549 | 16.1203 | 0.7654
GEN-2020-087 | 04 - Southeast | 764555 | GEN-2020-08 | 345 | 15.3422 | 16.1076 | 0.7654
GEN-2020-087 | 04 - Southeast | 764945 | G20-067-TAP | 345 | 8.4567 | 8.4591 | 0.0024
GEN-2020-087 | 04 - Southeast | 766290 | GEN-2020-00 | 345 | 9.3956 | 9.5138 | 0.1182
GEN-2020-087 | 04 - Southeast | 766291 | G20-009-TAP | 345 | 9.3956 | 9.5138 | 0.1182
GEN-2020-085 | 04 - Southeast | 507455 | TURK | 345 | 11.7628 | 11.7688 | 0.006
GEN-2020-085 | 04 - Southeast | 508298 | LYDIA | 345 | 14.092 | 14.1015 | 0.0095
GEN-2020-085 | 04 - Southeast | 510907 | PITTSB-7 | 345 | 16.6732 | 16.7355 | 0.0623
GEN-2020-085 | 04 - Southeast | 510911 | VALIANT7 | 345 | 17.2598 | 17.3049 | 0.0451
GEN-2020-085 | 04 - Southeast | 510918 | VALIANT4 | 138 | 15.9479 | 15.9621 | 0.0142
GEN-2020-085 | 04 - Southeast | 510925 | KIOWA | 345 | 16.3155 | 16.3752 | 0.0597
GEN-2020-085 | 04 - Southeast | 510946 | C-RIVER4 | 138 | 13.6737 | 13.6807 | 0.007
GEN-2020-085 | 04 - Southeast | 511409 | TREASILD7 | 345 | 17.2461 | 17.2896 | 0.0435
GEN-2020-085 | 04 - Southeast | 511423 | FLE | 138 | 8.7944 | 8.7982 | 0.0038
GEN-2020-085 | 04 - Southeast | 511437 | COMANC-4 | 138 | 19.0962 | 19.1291 | 0.0329
GEN-2020-085 | 04 - Southeast | 511439 | LWSTAP | 138 | 12.0072 | 12.0203 | 0.0131
GEN-2020-085 | 04 - Southeast | 511456 | O.K.U.-7 | 345 | 7.1035 | 7.1171 | 0.0136
GEN-2020-085 | 04 - Southeast | 511466 | L.E.S.-2 | 69 | 16.6892 | 16.7009 | 0.0117
GEN-2020-085 | 04 - Southeast | 511467 | L.E.S.-4 | 138 | 26.975 | 27.0517 | 0.0767
GEN-2020-085 | 04 - Southeast | 511468 | L.E.S.-7 | 345 | 17.1837 | 17.3217 | 0.138
GEN-2020-085 | 04 - Southeast | 511474 | SHERID4 | 138 | 12.8446 | 12.8605 | 0.0159
GEN-2020-085 | 04 - Southeast | 511486 | ELGINJT4 | 138 | 10.1497 | 10.1556 | 0.0059
GEN-2020-085 | 04 - Southeast | 511494 | COMMTAP4 | 138 | 23.1837 | 23.2383 | 0.0546
GEN-2020-085 | 04 - Southeast | 511568 | TERRYRD7 | 345 | 11.5897 | 11.8801 | 0.2904
GEN-2020-085 | 04 - Southeast | 511571 | RUSHSPR7 | 345 | 7.2417 | 7.3351 | 0.0934
GEN-2020-085 | 04 - Southeast | 514808 | JOHNCO | 138 | 15.5261 | 15.6362 | 0.1101
GEN-2020-085 | 04 - Southeast | 514809 | JOHNCO | 345 | 11.0645 | 11.2498 | 0.1853
GEN-2020-085 | 04 - Southeast | 514908 | ARCADIA7 | 345 | 28.6358 | 28.6404 | 0.0046
GEN-2020-085 | 04 - Southeast | 514934 | DRAPER | 345 | 31.3974 | 31.4206 | 0.0232
GEN-2020-085 | 04 - Southeast | 515044 | SEMINOL4 | 138 | 40.7758 | 40.813 | 0.0372
GEN-2020-085 | 04 - Southeast | 515045 | SEMINOL7 | 345 | 32.1278 | 32.1637 | 0.0359
GEN-2020-085 | 04 - Southeast | 515120 | RUSSET-4 | 138 | 11.3879 | 11.4439 | 0.056
GEN-2020-085 | 04 - Southeast | 515121 | MILLCKT4 | 138 | 10.99 | 11.0343 | 0.0443
GEN-2020-085 | 04 - Southeast | 515122 | SXMLCKT4 | 138 | 11.1458 | 11.1923 | 0.0465
GEN-2020-085 | 04 - Southeast | 515128 | RATLIFF2 | 69 | 4.9252 | 4.9323 | 0.0071
GEN-2020-085 | 04 - Southeast | 515129 | RATLIFF4 | 138 | 6.0651 | 6.085 | 0.0199
GEN-2020-085 | 04 - Southeast | 515130 | POOLVIL4 | 138 | 7.3865 | 7.422 | 0.0355
GEN-2020-085 | 04 - Southeast | 515131 | FOX | 138 | 6.2903 | 6.3176 | 0.0273
GEN-2020-085 | 04 - Southeast | 515134 | PRARPNT4 | 138 | 5.2075 | 5.218 | 0.0105
GEN-2020-085 | 04 - Southeast | 515135 | SUNNYSD4 | 138 | 18.7753 | 19.1158 | 0.3405
GEN-2020-085 | 04 - Southeast | 515136 | SUNNYSD7 | 345 | 12.0264 | 12.5482 | 0.5218
GEN-2020-085 | 04 - Southeast | 515137 | UNIROY | 138 | 12.6189 | 12.7393 | 0.1204
GEN-2020-085 | 04 - Southeast | 515138 | CARTER | 138 | 12.5471 | 12.642 | 0.0949
GEN-2020-085 | 04 - Southeast | 515143 | WOLFCRK4 | 138 | 9.4719 | 9.5527 | 0.0808
GEN-2020-085 | 04 - Southeast | 515144 | LONEGRV4 | 138 | 13.2801 | 13.4458 | 0.1657
GEN-2020-085 | 04 - Southeast | 515147 | GLASSES4 | 138 | 8.3485 | 8.3772 | 0.0287
GEN-2020-085 | 04 - Southeast | 515149 | MADINDT4 | 138 | 8.3461 | 8.3747 | 0.0286
GEN-2020-085 | 04 - Southeast | 515150 | CANEYCK4 | 138 | 9.1308 | 9.1642 | 0.0334
GEN-2020-085 | 04 - Southeast | 515151 | LTLCITY4 | 138 | 7.2445 | 7.2617 | 0.0172
GEN-2020-085 | 04 - Southeast | 515160 | MRIETA | 138 | 7.4004 | 7.4272 | 0.0268
GEN-2020-085 | 04 - Southeast | 515162 | FNDTION4 | 138 | 11.8514 | 11.9322 | 0.0808
GEN-2020-085 | 04 - Southeast | 515163 | ROCKYPT2 | 69 | 7.8852 | 7.9044 | 0.0192
GEN-2020-085 | 04 - Southeast | 515164 | ROCKYPT4 | 138 | 11.8028 | 11.8959 | 0.0931
GEN-2020-085 | 04 - Southeast | 515172 | SPRNDAL4 | 138 | 11.8019 | 11.8828 | 0.0809
GEN-2020-085 | 04 - Southeast | 515372 | ARDWEST4 | 138 | 12.4495 | 12.5636 | 0.1141
GEN-2020-085 | 04 - Southeast | 515415 | CHEEKTP4 | 138 | 11.9545 | 12.0874 | 0.1329
GEN-2020-085 | 04 - Southeast | 515420 | SCMMRCT2 | 69 | 9.0582 | 9.0827 | 0.0245
GEN-2020-085 | 04 - Southeast | 515422 | C-RIVER7 | 345 | 11.7039 | 11.7184 | 0.0145
GEN-2020-085 | 04 - Southeast | 515561 | CARTRCO4 | 138 | 7.523 | 7.5597 | 0.0367
GEN-2020-085 | 04 - Southeast | 515563 | ORIGINW4 | 138 | 3.4813 | 3.4891 | 0.0078
GEN-2020-085 | 04 - Southeast | 515873 | DRPSPRG4 | 138 | 10.9343 | 11.0021 | 0.0678
GEN-2020-085 | 04 - Southeast | 515932 | STIRLNG4 | 138 | 9.9287 | 9.9823 | 0.0536
GEN-2020-085 | 04 - Southeast | 516006 | DMNDSPG7 | 345 | 7.4594 | 7.539 | 0.0796
GEN-2020-085 | 04 - Southeast | 520560 | HUGOITC4 | 138 | 22.9395 | 22.9729 | 0.0334
GEN-2020-085 | 04 - Southeast | 520948 | HUGO | 138 | 23.1265 | 23.1589 | 0.0324
GEN-2020-085 | 04 - Southeast | 520988 | MARIETA4 | 138 | 7.3163 | 7.341 | 0.0247
GEN-2020-085 | 04 - Southeast | 521044 | RUSSETT4 | 138 | 11.3164 | 11.3715 | 0.0551
GEN-2020-085 | 04 - Southeast | 521067 | TEXOMAJ4 | 138 | 9.0412 | 9.0741 | 0.0329
GEN-2020-085 | 04 - Southeast | 521122 | HOWE | 138 | 11.0393 | 11.0849 | 0.0456
GEN-2020-085 | 04 - Southeast | 521125 | CHEEK_4 | 138 | 8.4007 | 8.4663 | 0.0656
GEN-2020-085 | 04 - Southeast | 521157 | HUGO | 345 | 12.836 | 12.8771 | 0.0411
GEN-2020-085 | 04 - Southeast | 560022 | CRAWFISH_DR | 345 | 14.7672 | 14.775 | 0.0078
GEN-2020-085 | 04 - Southeast | 560088 | G16-063-TAP | 345 | 8.1782 | 8.2748 | 0.0966
GEN-2020-085 | 04 - Southeast | 563259 | GEN-2015-09 | 345 | 6.9862 | 7.0727 | 0.0865
GEN-2020-085 | 04 - Southeast | 587430 | GEN-2016-06 | 345 | 8.0693 | 8.163 | 0.0937
GEN-2020-085 | 04 - Southeast | 588710 | GEN-2017-02 | 138 | 7.4899 | 7.5262 | 0.0363
GEN-2020-085 | 04 - Southeast | 588839 | G17-092-TAP | 345 | 20.2645 | 20.2763 | 0.0118
GEN-2020-085 | 04 - Southeast | 589130 | GEN-2017-07 | 345 | 8.1665 | 8.2628 | 0.0963
GEN-2020-085 | 04 - Southeast | 760830 | GEN-2017-14 | 345 | 4.2006 | 4.2196 | 0.019
GEN-2020-085 | 04 - Southeast | 760851 | GEN-2017-15 | 345 | 3.8237 | 3.8391 | 0.0154
GEN-2020-085 | 04 - Southeast | 760938 | G17-171-TAP | 345 | 13.0651 | 13.2607 | 0.1956
GEN-2020-085 | 04 - Southeast | 760939 | GEN-2017-17 | 345 | 12.979 | 13.1719 | 0.1929
GEN-2020-085 | 04 - Southeast | 761859 | GEN-2017-16 | 345 | 6.9424 | 7.1064 | 0.164
GEN-2020-085 | 04 - Southeast | 761880 | GEN-2017-16 | 345 | 5.2143 | 5.3071 | 0.0928
GEN-2020-085 | 04 - Southeast | 762216 | G17-151TAP | 345 | 8.3288 | 8.3328 | 0.004
GEN-2020-085 | 04 - Southeast | 762460 | GEN-2018-01 | 345 | 8.8628 | 8.8755 | 0.0127
GEN-2020-085 | 04 - Southeast | 762467 | G18-015-TAP | 345 | 8.8967 | 8.9095 | 0.0128
GEN-2020-085 | 04 - Southeast | 762900 | GEN-2018-05 | 345 | 4.9071 | 4.9469 | 0.0398
GEN-2020-085 | 04 - Southeast | 763131 | GEN-2018-08 | 345 | 10.2349 | 10.2577 | 0.0228
GEN-2020-085 | 04 - Southeast | 763215 | G18-092-PRO | 345 | 9.0262 | 9.0421 | 0.0159
GEN-2020-085 | 04 - Southeast | 763318 | GEN-2018-11 | 345 | 16.7837 | 16.9151 | 0.1314
GEN-2020-085 | 04 - Southeast | 764105 | GEN-2020-07 | 345 | 10.8103 | 11.566 | 0.7557
GEN-2020-085 | 04 - Southeast | 764115 | G20-074-TAP | 345 | 10.8162 | 11.572 | 0.7558
GEN-2020-085 | 04 - Southeast | 764270 | GEN-2020-01 | 345 | 11.0645 | 11.2498 | 0.1853
GEN-2020-085 | 04 - Southeast | 764520 | G20-020-TAP | 345 | 17.0676 | 17.1115 | 0.0439
GEN-2020-085 | 04 - Southeast | 764540 | GEN-2020-07 | 345 | 16.0311 | 16.1068 | 0.0757
GEN-2020-085 | 04 - Southeast | 764550 | G20-075-TAP | 345 | 16.0445 | 16.1203 | 0.0758
GEN-2020-085 | 04 - Southeast | 764555 | GEN-2020-08 | 345 | 16.0319 | 16.1076 | 0.0757
GEN-2020-085 | 04 - Southeast | 766290 | GEN-2020-00 | 345 | 9.4801 | 9.5138 | 0.0337
GEN-2020-085 | 04 - Southeast | 766291 | G20-009-TAP | 345 | 9.4801 | 9.5138 | 0.0337
GEN-2020-081 | 04 - Southeast | 5917 | SPPMAINBUS | 345 | 21.564 | 21.6012 | 0.0372
GEN-2020-081 | 04 - Southeast | 46714 | J1671 | 230 | 7.7694 | 7.7756 | 0.0062
GEN-2020-081 | 04 - Southeast | 334020 | 4BRYAN% | 138 | 4.8978 | 4.8994 | 0.0016
GEN-2020-081 | 04 - Southeast | 334021 | 4COLSTTA% | 138 | 6.2605 | 6.2635 | 0.003
GEN-2020-081 | 04 - Southeast | 334022 | 4SPEEDWY | 138 | 5.9538 | 5.9564 | 0.0026
GEN-2020-081 | 04 - Southeast | 334024 | 4SOTA | 138 | 6.4183 | 6.4215 | 0.0032
GEN-2020-081 | 04 - Southeast | 334025 | 4MAG | 138 | 6.8497 | 6.8538 | 0.0041
GEN-2020-081 | 04 - Southeast | 334026 | 4GRIMES% | 138 | 16.2772 | 16.3057 | 0.0285
GEN-2020-081 | 04 - Southeast | 334027 | 6GRIMES! | 230 | 7.0851 | 7.0938 | 0.0087
GEN-2020-081 | 04 - Southeast | 334028 | 7GRIMES% | 345 | 8.4345 | 8.46 | 0.0255
GEN-2020-081 | 04 - Southeast | 334029 | 7FRONTR | 345 | 8.2217 | 8.2449 | 0.0232
GEN-2020-081 | 04 - Southeast | 334039 | 4BENTWATER! | 138 | 6.8476 | 6.85 | 0.0024
GEN-2020-081 | 04 - Southeast | 334040 | 4WALDEN | 138 | 7.2581 | 7.2605 | 0.0024
GEN-2020-081 | 04 - Southeast | 334058 | 4L558T485 | 138 | 8.8322 | 8.8347 | 0.0025
GEN-2020-081 | 04 - Southeast | 334060 | 4MT.ZION | 138 | 8.0211 | 8.024 | 0.0029
GEN-2020-081 | 04 - Southeast | 334087 | 4PONDEROSA% | 138 | 18.4612 | 18.4698 | 0.0086
GEN-2020-081 | 04 - Southeast | 334088 | 6PONDEROSA! | 230 | 7.0771 | 7.0807 | 0.0036
GEN-2020-081 | 04 - Southeast | 334197 | 7ROCKYCRK% | 345 | 6.8628 | 6.8774 | 0.0146
GEN-2020-081 | 04 - Southeast | 334198 | 6ROCKYCRK | 230 | 7.8267 | 7.8341 | 0.0074
GEN-2020-081 | 04 - Southeast | 500250 | DOLHILL7 | 345 | 12.3257 | 12.3276 | 0.0019
GEN-2020-081 | 04 - Southeast | 507759 | SW | 138 | 30.5876 | 30.6046 | 0.017
GEN-2020-081 | 04 - Southeast | 507760 | SW | 345 | 15.9894 | 16.0013 | 0.0119
GEN-2020-081 | 04 - Southeast | 508072 | NWTXARK7 | 345 | 16.788 | 16.7965 | 0.0085
GEN-2020-081 | 04 - Southeast | 508297 | LSSOUTH4 | 138 | 17.2079 | 17.2186 | 0.0107
GEN-2020-081 | 04 - Southeast | 508298 | LYDIA | 345 | 14.0942 | 14.1015 | 0.0073
GEN-2020-081 | 04 - Southeast | 508351 | PERDUE | 138 | 10.5639 | 10.5705 | 0.0066
GEN-2020-081 | 04 - Southeast | 508359 | WELSH | 345 | 21.564 | 21.6012 | 0.0372
GEN-2020-081 | 04 - Southeast | 508557 | MARSHL-4 | 138 | 16.5399 | 16.5666 | 0.0267
GEN-2020-081 | 04 - Southeast | 508562 | PIRKEY | 138 | 41.8117 | 42.0588 | 0.2471
GEN-2020-081 | 04 - Southeast | 508563 | PIRKEY | 345 | 16.9338 | 17.1469 | 0.2131
GEN-2020-081 | 04 - Southeast | 508566 | SABMINT4 | 138 | 34.0146 | 34.1731 | 0.1585
GEN-2020-081 | 04 - Southeast | 508569 | SEMRSHL4 | 138 | 13.3729 | 13.3888 | 0.0159
GEN-2020-081 | 04 - Southeast | 508571 | SPRHILL4 | 138 | 8.3 | 8.3047 | 0.0047
GEN-2020-081 | 04 - Southeast | 508572 | LEBROCK7 | 345 | 15.8066 | 16.0391 | 0.2325
GEN-2020-081 | 04 - Southeast | 508575 | WHITNEY4 | 138 | 21.4408 | 21.4733 | 0.0325
GEN-2020-081 | 04 - Southeast | 508576 | MARAUTO2 | 69 | 17.8827 | 17.8959 | 0.0132
GEN-2020-081 | 04 - Southeast | 508577 | SABINEM4 | 138 | 22.3509 | 22.4191 | 0.0682
GEN-2020-081 | 04 - Southeast | 508585 | TENRUSK7 | 345 | 7.7895 | 8.1203 | 0.3308
GEN-2020-081 | 04 - Southeast | 508586 | TENGEN | 345 | 7.7174 | 8.0419 | 0.3245
GEN-2020-081 | 04 - Southeast | 508595 | HALLSVLS4 | 138 | 18.4985 | 18.5286 | 0.0301
GEN-2020-081 | 04 - Southeast | 508596 | BRANDYBR | 138 | 24.6571 | 24.6942 | 0.0371
GEN-2020-081 | 04 - Southeast | 508809 | LONGWD | 345 | 16.0318 | 16.0421 | 0.0103
GEN-2020-081 | 04 - Southeast | 508831 | DIANA | 138 | 29.5155 | 29.5754 | 0.0599
GEN-2020-081 | 04 - Southeast | 508832 | DIANA | 345 | 19.0957 | 19.1686 | 0.0729
GEN-2020-081 | 04 - Southeast | 508835 | JEFFRSN4 | 138 | 13.4139 | 13.4209 | 0.007
GEN-2020-081 | 04 - Southeast | 508837 | NGPLTAP4 | 138 | 13.3991 | 13.4115 | 0.0124
GEN-2020-081 | 04 - Southeast | 508841 | WILKES | 345 | 17.7593 | 17.7735 | 0.0142
GEN-2020-081 | 04 - Southeast | 509092 | EASTON | 138 | 24.3873 | 24.4241 | 0.0368
GEN-2020-081 | 04 - Southeast | 509240 | CROCKET4 | 138 | 6.8609 | 6.8928 | 0.0319
GEN-2020-081 | 04 - Southeast | 509241 | CROCKET7 | 345 | 5.747 | 5.8102 | 0.0632
GEN-2020-081 | 04 - Southeast | 509320 | ALTO | 138 | 2.9712 | 2.9744 | 0.0032
GEN-2020-081 | 04 - Southeast | 509322 | GRAPLND4 | 138 | 4.5344 | 4.5465 | 0.0121
GEN-2020-081 | 04 - Southeast | 509326 | SLOCUM | 138 | 3.7136 | 3.7208 | 0.0072
GEN-2020-081 | 04 - Southeast | 509639 | DIANASW4 | 138 | 12.036 | 12.0459 | 0.0099
GEN-2020-081 | 04 - Southeast | 764120 | GEN-2020-08 | 345 | 7.7632 | 8.094 | 0.3308
GEN-2020-075 | 04 - Southeast | 511409 | TREASILD7 | 345 | 17.1357 | 17.2896 | 0.1539
GEN-2020-075 | 04 - Southeast | 511422 | FLETCHR4 | 138 | 8.0264 | 8.0306 | 0.0042
GEN-2020-075 | 04 - Southeast | 511423 | FLE | 138 | 8.7931 | 8.7982 | 0.0051
GEN-2020-075 | 04 - Southeast | 511428 | LG-YEAR4 | 138 | 12.4166 | 12.4343 | 0.0177
GEN-2020-075 | 04 - Southeast | 511431 | LWS | 138 | 11.4902 | 11.5061 | 0.0159
GEN-2020-075 | 04 - Southeast | 511436 | COMANC-2 | 69 | 9.2817 | 9.2847 | 0.003
GEN-2020-075 | 04 - Southeast | 511437 | COMANC-4 | 138 | 19.086 | 19.1291 | 0.0431
GEN-2020-075 | 04 - Southeast | 511439 | LWSTAP | 138 | 12.0031 | 12.0203 | 0.0172
GEN-2020-075 | 04 - Southeast | 511451 | CYRIL--2 | 69 | 4.6533 | 4.6539 | 0.0006
GEN-2020-075 | 04 - Southeast | 511453 | DUNCAN-4 | 138 | 6.4236 | 6.4264 | 0.0028
GEN-2020-075 | 04 - Southeast | 511456 | O.K.U.-7 | 345 | 7.0989 | 7.1171 | 0.0182
GEN-2020-075 | 04 - Southeast | 511461 | FT.SILL2 | 69 | 5.9524 | 5.954 | 0.0016
GEN-2020-075 | 04 - Southeast | 511466 | L.E.S.-2 | 69 | 16.6859 | 16.7009 | 0.015
GEN-2020-075 | 04 - Southeast | 511467 | L.E.S.-4 | 138 | 26.9509 | 27.0517 | 0.1008
GEN-2020-075 | 04 - Southeast | 511468 | L.E.S.-7 | 345 | 17.1382 | 17.3217 | 0.1835
GEN-2020-075 | 04 - Southeast | 511469 | LGORE-N2 | 69 | 8.0303 | 8.0336 | 0.0033
GEN-2020-075 | 04 - Southeast | 511470 | LGORE-S2 | 69 | 6.9567 | 6.9593 | 0.0026
GEN-2020-075 | 04 - Southeast | 511471 | LWS-NTP4 | 138 | 12.1358 | 12.1536 | 0.0178
GEN-2020-075 | 04 - Southeast | 511473 | PO.HILL2 | 69 | 5.8328 | 5.8342 | 0.0014
GEN-2020-075 | 04 - Southeast | 511474 | SHERID4 | 138 | 12.8396 | 12.8605 | 0.0209
GEN-2020-075 | 04 - Southeast | 511477 | S.W.S.-4 | 138 | 33.035 | 33.0598 | 0.0248
GEN-2020-075 | 04 - Southeast | 511486 | ELGINJT4 | 138 | 10.1477 | 10.1556 | 0.0079
GEN-2020-075 | 04 - Southeast | 511487 | ELGINJT2 | 69 | 8.5426 | 8.5453 | 0.0027
GEN-2020-075 | 04 - Southeast | 511488 | 112GORE4 | 138 | 13.277 | 13.2972 | 0.0202
GEN-2020-075 | 04 - Southeast | 511494 | COMMTAP4 | 138 | 23.167 | 23.2383 | 0.0713
GEN-2020-075 | 04 - Southeast | 511503 | LAW | 69 | 4.5387 | 4.5398 | 0.0011
GEN-2020-075 | 04 - Southeast | 511509 | 53CACHE4 | 138 | 12.1706 | 12.1888 | 0.0182
GEN-2020-075 | 04 - Southeast | 511510 | LAIRGST4 | 138 | 12.8451 | 12.8638 | 0.0187
GEN-2020-075 | 04 - Southeast | 511512 | RPPAPER4 | 138 | 12.4649 | 12.483 | 0.0181
GEN-2020-075 | 04 - Southeast | 511524 | L-DISTP2 | 69 | 8.5964 | 8.5989 | 0.0025
GEN-2020-075 | 04 - Southeast | 511537 | ARTVLTP4 | 138 | 12.191 | 12.2093 | 0.0183
GEN-2020-075 | 04 - Southeast | 511538 | ARTVILL4 | 138 | 8.7164 | 8.7257 | 0.0093
GEN-2020-075 | 04 - Southeast | 511553 | CHISHOLM7 | 345 | 13.1985 | 13.2045 | 0.006
GEN-2020-075 | 04 - Southeast | 511557 | CHISHOLM6 | 230 | 12.5604 | 12.5631 | 0.0027
GEN-2020-075 | 04 - Southeast | 511563 | ELSWORTH | 138 | 10.0671 | 10.0746 | 0.0075
GEN-2020-075 | 04 - Southeast | 511565 | OKLAUN | 345 | 7.0715 | 7.0896 | 0.0181
GEN-2020-075 | 04 - Southeast | 511568 | TERRYRD7 | 345 | 11.8405 | 11.8801 | 0.0396
GEN-2020-075 | 04 - Southeast | 511571 | RUSHSPR7 | 345 | 7.3225 | 7.3351 | 0.0126
GEN-2020-075 | 04 - Southeast | 514801 | MINCO | 345 | 26.2469 | 26.2868 | 0.0399
GEN-2020-075 | 04 - Southeast | 514880 | NORTWST7 | 345 | 33.6148 | 33.6247 | 0.0099
GEN-2020-075 | 04 - Southeast | 514898 | CIMARON4 | 138 | 45.9464 | 45.9573 | 0.0109
GEN-2020-075 | 04 - Southeast | 514901 | CIMARON7 | 345 | 36.6567 | 36.6785 | 0.0218
GEN-2020-075 | 04 - Southeast | 514929 | PLVALLY4 | 138 | 56.357 | 56.3755 | 0.0185
GEN-2020-075 | 04 - Southeast | 514934 | DRAPER | 345 | 31.4037 | 31.4206 | 0.0169
GEN-2020-075 | 04 - Southeast | 515136 | SUNNYSD7 | 345 | 12.5377 | 12.5482 | 0.0105
GEN-2020-075 | 04 - Southeast | 515444 | MCNOWND7 | 345 | 26.1266 | 26.1662 | 0.0396
GEN-2020-075 | 04 - Southeast | 515458 | BORDER | 345 | 8.5481 | 8.5506 | 0.0025
GEN-2020-075 | 04 - Southeast | 515497 | MATHWSN7 | 345 | 33.9018 | 33.9142 | 0.0124
GEN-2020-075 | 04 - Southeast | 515549 | MNCWND37 | 345 | 15.1353 | 15.1479 | 0.0126
GEN-2020-075 | 04 - Southeast | 515610 | FSHRTAP7 | 345 | 16.5186 | 16.5227 | 0.0041
GEN-2020-075 | 04 - Southeast | 515800 | GRACMNT7 | 345 | 20.6461 | 20.7563 | 0.1102
GEN-2020-075 | 04 - Southeast | 515802 | GRACMNT4 | 138 | 32.7517 | 32.7851 | 0.0334
GEN-2020-075 | 04 - Southeast | 515939 | MNCWND47 | 345 | 10.3368 | 10.3425 | 0.0057
GEN-2020-075 | 04 - Southeast | 516059 | BECKHAM7 | 345 | 13.0846 | 13.0904 | 0.0058
GEN-2020-075 | 04 - Southeast | 516096 | NORMHLL7 | 345 | 28.3739 | 28.39 | 0.0161
GEN-2020-075 | 04 - Southeast | 516097 | NORMHLL4 | 138 | 54.6287 | 54.6462 | 0.0175
GEN-2020-075 | 04 - Southeast | 520422 | SEQUOYAHJ4 | 138 | 25.2153 | 25.2282 | 0.0129
GEN-2020-075 | 04 - Southeast | 520508 | CLVLDSW4 | 138 | 12.5748 | 12.5769 | 0.0021
GEN-2020-075 | 04 - Southeast | 520810 | ANADARK2 | 69 | 14.3157 | 14.3178 | 0.0021
GEN-2020-075 | 04 - Southeast | 520814 | ANADARK4 | 138 | 35.1039 | 35.129 | 0.0251
GEN-2020-075 | 04 - Southeast | 520923 | GEORGIA4 | 138 | 18.1841 | 18.1909 | 0.0068
GEN-2020-075 | 04 - Southeast | 521017 | ONEY | 138 | 10.9191 | 10.9218 | 0.0027
GEN-2020-075 | 04 - Southeast | 521031 | POCASET4 | 138 | 8.0529 | 8.0538 | 0.0009
GEN-2020-075 | 04 - Southeast | 521088 | WASHITA2 | 69 | 9.028 | 9.0288 | 0.0008
GEN-2020-075 | 04 - Southeast | 521089 | WASHITA4 | 138 | 29.2444 | 29.2654 | 0.021
GEN-2020-075 | 04 - Southeast | 521103 | SLKHILLS | 138 | 6.4064 | 6.407 | 0.0006
GEN-2020-075 | 04 - Southeast | 521129 | CHERRYRD | 138 | 5.8643 | 5.865 | 0.0007
GEN-2020-075 | 04 - Southeast | 523961 | POTTER_CO | 345 | 13.6097 | 13.6108 | 0.0011
GEN-2020-075 | 04 - Southeast | 525830 | TUCO_INT | 230 | 22.3108 | 22.3183 | 0.0075
GEN-2020-075 | 04 - Southeast | 525832 | TUCO_INT | 345 | 14.9955 | 15.0061 | 0.0106
GEN-2020-075 | 04 - Southeast | 525850 | ELK_CT1 | 345 | 14.8407 | 14.851 | 0.0103
GEN-2020-075 | 04 - Southeast | 529304 | OMDUNCN4 | 138 | 6.68 | 6.6835 | 0.0035
GEN-2020-075 | 04 - Southeast | 555234 | NSUB345 | 345 | 28.3975 | 28.4136 | 0.0161
GEN-2020-075 | 04 - Southeast | 560022 | CRAWFISH_DR | 345 | 14.7641 | 14.775 | 0.0109
GEN-2020-075 | 04 - Southeast | 560078 | G16-037-TAP | 345 | 10.3338 | 10.3447 | 0.0109
GEN-2020-075 | 04 - Southeast | 563259 | GEN-2015-09 | 345 | 7.061 | 7.0727 | 0.0117
GEN-2020-075 | 04 - Southeast | 563269 | GEN-2015-09 | 345 | 10.8578 | 10.887 | 0.0292
GEN-2020-075 | 04 - Southeast | 587230 | GEN-2016-03 | 345 | 9.8366 | 9.8463 | 0.0097
GEN-2020-075 | 04 - Southeast | 587740 | GEN-2016-09 | 345 | 11.4824 | 11.5492 | 0.0668
GEN-2020-075 | 04 - Southeast | 587770 | GEN-2016-09 | 345 | 11.8031 | 11.8747 | 0.0716
GEN-2020-075 | 04 - Southeast | 587790 | GEN-2016-09 | 138 | 9.0192 | 9.0224 | 0.0032
GEN-2020-075 | 04 - Southeast | 587794 | G16-097-TAP | 138 | 11.1712 | 11.1761 | 0.0049
GEN-2020-075 | 04 - Southeast | 588760 | GEN-2017-03 | 345 | 4.5703 | 4.5778 | 0.0075
GEN-2020-075 | 04 - Southeast | 599891 | OKLAUN | 345 | 4.0421 | 4.0421 | 0
GEN-2020-075 | 04 - Southeast | 760938 | G17-171-TAP | 345 | 13.1869 | 13.2607 | 0.0738
GEN-2020-075 | 04 - Southeast | 760939 | GEN-2017-17 | 345 | 13.0991 | 13.1719 | 0.0728
GEN-2020-075 | 04 - Southeast | 761229 | GEN-2017-15 | 345 | 25.212 | 25.2488 | 0.0368
GEN-2020-075 | 04 - Southeast | 761250 | GEN-2017-23 | 345 | 25.2678 | 25.3047 | 0.0369
GEN-2020-075 | 04 - Southeast | 762216 | G17-151TAP | 345 | 8.3273 | 8.3328 | 0.0055
GEN-2020-075 | 04 - Southeast | 762217 | GEN-2017-15 | 345 | 5.8376 | 5.8403 | 0.0027
GEN-2020-075 | 04 - Southeast | 762460 | GEN-2018-01 | 345 | 8.8584 | 8.8755 | 0.0171
GEN-2020-075 | 04 - Southeast | 762467 | G18-015-TAP | 345 | 8.8922 | 8.9095 | 0.0173
GEN-2020-075 | 04 - Southeast | 762900 | GEN-2018-05 | 345 | 4.9415 | 4.9469 | 0.0054
GEN-2020-075 | 04 - Southeast | 763215 | G18-092-PRO | 345 | 9.0206 | 9.0421 | 0.0215
GEN-2020-075 | 04 - Southeast | 763318 | GEN-2018-11 | 345 | 16.7403 | 16.9151 | 0.1748
GEN-2020-075 | 04 - Southeast | 764105 | GEN-2020-07 | 345 | 11.5514 | 11.566 | 0.0146
GEN-2020-075 | 04 - Southeast | 764115 | G20-074-TAP | 345 | 11.5573 | 11.572 | 0.0147
GEN-2020-075 | 04 - Southeast | 764540 | GEN-2020-07 | 345 | 15.8091 | 16.1068 | 0.2977
GEN-2020-075 | 04 - Southeast | 764550 | G20-075-TAP | 345 | 15.8226 | 16.1203 | 0.2977
GEN-2020-075 | 04 - Southeast | 764555 | GEN-2020-08 | 345 | 15.8104 | 16.1076 | 0.2972
GEN-2020-075 | 04 - Southeast | 764945 | G20-067-TAP | 345 | 8.4582 | 8.4591 | 0.0009
GEN-2020-075 | 04 - Southeast | 766290 | GEN-2020-00 | 345 | 9.4689 | 9.5138 | 0.0449
GEN-2020-075 | 04 - Southeast | 766291 | G20-009-TAP | 345 | 9.4689 | 9.5138 | 0.0449
GEN-2020-074 | 04 - Southeast | 507455 | TURK | 345 | 11.7665 | 11.7688 | 0.0023
GEN-2020-074 | 04 - Southeast | 508298 | LYDIA | 345 | 14.0979 | 14.1015 | 0.0036
GEN-2020-074 | 04 - Southeast | 510907 | PITTSB-7 | 345 | 16.7118 | 16.7355 | 0.0237
GEN-2020-074 | 04 - Southeast | 510911 | VALIANT7 | 345 | 17.2878 | 17.3049 | 0.0171
GEN-2020-074 | 04 - Southeast | 510918 | VALIANT4 | 138 | 15.9567 | 15.9621 | 0.0054
GEN-2020-074 | 04 - Southeast | 510925 | KIOWA | 345 | 16.3525 | 16.3752 | 0.0227
GEN-2020-074 | 04 - Southeast | 510946 | C-RIVER4 | 138 | 13.678 | 13.6807 | 0.0027
GEN-2020-074 | 04 - Southeast | 511409 | TREASILD7 | 345 | 17.2731 | 17.2896 | 0.0165
GEN-2020-074 | 04 - Southeast | 511423 | FLE | 138 | 8.7967 | 8.7982 | 0.0015
GEN-2020-074 | 04 - Southeast | 511437 | COMANC-4 | 138 | 19.1166 | 19.1291 | 0.0125
GEN-2020-074 | 04 - Southeast | 511439 | LWSTAP | 138 | 12.0154 | 12.0203 | 0.0049
GEN-2020-074 | 04 - Southeast | 511456 | O.K.U.-7 | 345 | 7.112 | 7.1171 | 0.0051
GEN-2020-074 | 04 - Southeast | 511466 | L.E.S.-2 | 69 | 16.6964 | 16.7009 | 0.0045
GEN-2020-074 | 04 - Southeast | 511467 | L.E.S.-4 | 138 | 27.0226 | 27.0517 | 0.0291
GEN-2020-074 | 04 - Southeast | 511468 | L.E.S.-7 | 345 | 17.2692 | 17.3217 | 0.0525
GEN-2020-074 | 04 - Southeast | 511474 | SHERID4 | 138 | 12.8545 | 12.8605 | 0.006
GEN-2020-074 | 04 - Southeast | 511486 | ELGINJT4 | 138 | 10.1534 | 10.1556 | 0.0022
GEN-2020-074 | 04 - Southeast | 511494 | COMMTAP4 | 138 | 23.2176 | 23.2383 | 0.0207
GEN-2020-074 | 04 - Southeast | 511568 | TERRYRD7 | 345 | 11.7685 | 11.8801 | 0.1116
GEN-2020-074 | 04 - Southeast | 511571 | RUSHSPR7 | 345 | 7.2995 | 7.3351 | 0.0356
GEN-2020-074 | 04 - Southeast | 514808 | JOHNCO | 138 | 15.5943 | 15.6362 | 0.0419
GEN-2020-074 | 04 - Southeast | 514809 | JOHNCO | 345 | 11.1789 | 11.2498 | 0.0709
GEN-2020-074 | 04 - Southeast | 514908 | ARCADIA7 | 345 | 28.6386 | 28.6404 | 0.0018
GEN-2020-074 | 04 - Southeast | 514934 | DRAPER | 345 | 31.4118 | 31.4206 | 0.0088
GEN-2020-074 | 04 - Southeast | 515044 | SEMINOL4 | 138 | 40.7989 | 40.813 | 0.0141
GEN-2020-074 | 04 - Southeast | 515045 | SEMINOL7 | 345 | 32.1501 | 32.1637 | 0.0136
GEN-2020-074 | 04 - Southeast | 515120 | RUSSET-4 | 138 | 11.4226 | 11.4439 | 0.0213
GEN-2020-074 | 04 - Southeast | 515121 | MILLCKT4 | 138 | 11.0175 | 11.0343 | 0.0168
GEN-2020-074 | 04 - Southeast | 515122 | SXMLCKT4 | 138 | 11.1747 | 11.1923 | 0.0176
GEN-2020-074 | 04 - Southeast | 515128 | RATLIFF2 | 69 | 4.9296 | 4.9323 | 0.0027
GEN-2020-074 | 04 - Southeast | 515129 | RATLIFF4 | 138 | 6.0774 | 6.085 | 0.0076
GEN-2020-074 | 04 - Southeast | 515130 | POOLVIL4 | 138 | 7.4085 | 7.422 | 0.0135
GEN-2020-074 | 04 - Southeast | 515131 | FOX | 138 | 6.3072 | 6.3176 | 0.0104
GEN-2020-074 | 04 - Southeast | 515134 | PRARPNT4 | 138 | 5.2141 | 5.218 | 0.0039
GEN-2020-074 | 04 - Southeast | 515135 | SUNNYSD4 | 138 | 18.9854 | 19.1158 | 0.1304
GEN-2020-074 | 04 - Southeast | 515136 | SUNNYSD7 | 345 | 12.3454 | 12.5482 | 0.2028
GEN-2020-074 | 04 - Southeast | 515137 | UNIROY | 138 | 12.6935 | 12.7393 | 0.0458
GEN-2020-074 | 04 - Southeast | 515138 | CARTER | 138 | 12.6059 | 12.642 | 0.0361
GEN-2020-074 | 04 - Southeast | 515143 | WOLFCRK4 | 138 | 9.522 | 9.5527 | 0.0307
GEN-2020-074 | 04 - Southeast | 515144 | LONEGRV4 | 138 | 13.3826 | 13.4458 | 0.0632
GEN-2020-074 | 04 - Southeast | 515147 | GLASSES4 | 138 | 8.3664 | 8.3772 | 0.0108
GEN-2020-074 | 04 - Southeast | 515149 | MADINDT4 | 138 | 8.3639 | 8.3747 | 0.0108
GEN-2020-074 | 04 - Southeast | 515150 | CANEYCK4 | 138 | 9.1515 | 9.1642 | 0.0127
GEN-2020-074 | 04 - Southeast | 515151 | LTLCITY4 | 138 | 7.2552 | 7.2617 | 0.0065
GEN-2020-074 | 04 - Southeast | 515160 | MRIETA | 138 | 7.417 | 7.4272 | 0.0102
GEN-2020-074 | 04 - Southeast | 515162 | FNDTION4 | 138 | 11.9015 | 11.9322 | 0.0307
GEN-2020-074 | 04 - Southeast | 515163 | ROCKYPT2 | 69 | 7.8971 | 7.9044 | 0.0073
GEN-2020-074 | 04 - Southeast | 515164 | ROCKYPT4 | 138 | 11.8605 | 11.8959 | 0.0354
GEN-2020-074 | 04 - Southeast | 515172 | SPRNDAL4 | 138 | 11.8521 | 11.8828 | 0.0307
GEN-2020-074 | 04 - Southeast | 515372 | ARDWEST4 | 138 | 12.5201 | 12.5636 | 0.0435
GEN-2020-074 | 04 - Southeast | 515415 | CHEEKTP4 | 138 | 12.0367 | 12.0874 | 0.0507
GEN-2020-074 | 04 - Southeast | 515420 | SCMMRCT2 | 69 | 9.0734 | 9.0827 | 0.0093
GEN-2020-074 | 04 - Southeast | 515422 | C-RIVER7 | 345 | 11.7129 | 11.7184 | 0.0055
GEN-2020-074 | 04 - Southeast | 515561 | CARTRCO4 | 138 | 7.5457 | 7.5597 | 0.014
GEN-2020-074 | 04 - Southeast | 515563 | ORIGINW4 | 138 | 3.4861 | 3.4891 | 0.003
GEN-2020-074 | 04 - Southeast | 515873 | DRPSPRG4 | 138 | 10.9763 | 11.0021 | 0.0258
GEN-2020-074 | 04 - Southeast | 515932 | STIRLNG4 | 138 | 9.9619 | 9.9823 | 0.0204
GEN-2020-074 | 04 - Southeast | 516006 | DMNDSPG7 | 345 | 7.5087 | 7.539 | 0.0303
GEN-2020-074 | 04 - Southeast | 520560 | HUGOITC4 | 138 | 22.9602 | 22.9729 | 0.0127
GEN-2020-074 | 04 - Southeast | 520948 | HUGO | 138 | 23.1466 | 23.1589 | 0.0123
GEN-2020-074 | 04 - Southeast | 520988 | MARIETA4 | 138 | 7.3316 | 7.341 | 0.0094
GEN-2020-074 | 04 - Southeast | 521044 | RUSSETT4 | 138 | 11.3506 | 11.3715 | 0.0209
GEN-2020-074 | 04 - Southeast | 521067 | TEXOMAJ4 | 138 | 9.0616 | 9.0741 | 0.0125
GEN-2020-074 | 04 - Southeast | 521122 | HOWE | 138 | 11.0676 | 11.0849 | 0.0173
GEN-2020-074 | 04 - Southeast | 521125 | CHEEK_4 | 138 | 8.4413 | 8.4663 | 0.025
GEN-2020-074 | 04 - Southeast | 521157 | HUGO | 345 | 12.8615 | 12.8771 | 0.0156
GEN-2020-074 | 04 - Southeast | 560022 | CRAWFISH_DR | 345 | 14.772 | 14.775 | 0.003
GEN-2020-074 | 04 - Southeast | 560088 | G16-063-TAP | 345 | 8.2379 | 8.2748 | 0.0369
GEN-2020-074 | 04 - Southeast | 563259 | GEN-2015-09 | 345 | 7.0397 | 7.0727 | 0.033
GEN-2020-074 | 04 - Southeast | 587430 | GEN-2016-06 | 345 | 8.1273 | 8.163 | 0.0357
GEN-2020-074 | 04 - Southeast | 588710 | GEN-2017-02 | 138 | 7.5124 | 7.5262 | 0.0138
GEN-2020-074 | 04 - Southeast | 588839 | G17-092-TAP | 345 | 20.2718 | 20.2763 | 0.0045
GEN-2020-074 | 04 - Southeast | 589130 | GEN-2017-07 | 345 | 8.2261 | 8.2628 | 0.0367
GEN-2020-074 | 04 - Southeast | 760830 | GEN-2017-14 | 345 | 4.2124 | 4.2196 | 0.0072
GEN-2020-074 | 04 - Southeast | 760851 | GEN-2017-15 | 345 | 3.8333 | 3.8391 | 0.0058
GEN-2020-074 | 04 - Southeast | 760938 | G17-171-TAP | 345 | 13.186 | 13.2607 | 0.0747
GEN-2020-074 | 04 - Southeast | 760939 | GEN-2017-17 | 345 | 13.0982 | 13.1719 | 0.0737
GEN-2020-074 | 04 - Southeast | 761859 | GEN-2017-16 | 345 | 7.0435 | 7.1064 | 0.0629
GEN-2020-074 | 04 - Southeast | 761880 | GEN-2017-16 | 345 | 5.2716 | 5.3071 | 0.0355
GEN-2020-074 | 04 - Southeast | 762216 | G17-151TAP | 345 | 8.3313 | 8.3328 | 0.0015
GEN-2020-074 | 04 - Southeast | 762460 | GEN-2018-01 | 345 | 8.8707 | 8.8755 | 0.0048
GEN-2020-074 | 04 - Southeast | 762467 | G18-015-TAP | 345 | 8.9046 | 8.9095 | 0.0049
GEN-2020-074 | 04 - Southeast | 762900 | GEN-2018-05 | 345 | 4.9318 | 4.9469 | 0.0151
GEN-2020-074 | 04 - Southeast | 763131 | GEN-2018-08 | 345 | 10.2491 | 10.2577 | 0.0086
GEN-2020-074 | 04 - Southeast | 763215 | G18-092-PRO | 345 | 9.0361 | 9.0421 | 0.006
GEN-2020-074 | 04 - Southeast | 763318 | GEN-2018-11 | 345 | 16.8651 | 16.9151 | 0.05
GEN-2020-074 | 04 - Southeast | 764105 | GEN-2020-07 | 345 | 11.2678 | 11.566 | 0.2982
GEN-2020-074 | 04 - Southeast | 764115 | G20-074-TAP | 345 | 11.2737 | 11.572 | 0.2983
GEN-2020-074 | 04 - Southeast | 764270 | GEN-2020-01 | 345 | 11.1789 | 11.2498 | 0.0709
GEN-2020-074 | 04 - Southeast | 764520 | G20-020-TAP | 345 | 17.0949 | 17.1115 | 0.0166
GEN-2020-074 | 04 - Southeast | 764540 | GEN-2020-07 | 345 | 16.078 | 16.1068 | 0.0288
GEN-2020-074 | 04 - Southeast | 764550 | G20-075-TAP | 345 | 16.0915 | 16.1203 | 0.0288
GEN-2020-074 | 04 - Southeast | 764555 | GEN-2020-08 | 345 | 16.0788 | 16.1076 | 0.0288
GEN-2020-074 | 04 - Southeast | 766290 | GEN-2020-00 | 345 | 9.501 | 9.5138 | 0.0128
GEN-2020-074 | 04 - Southeast | 766291 | G20-009-TAP | 345 | 9.501 | 9.5138 | 0.0128
GEN-2020-054 | 04 - Southeast | 5917 | SPPMAINBUS | 345 | 21.3891 | 21.6012 | 0.2121
GEN-2020-054 | 04 - Southeast | 5918 | DCEAST | 345 | 4.7923 | 4.7923 | 0
GEN-2020-054 | 04 - Southeast | 5919 | WELSHDC1 | 345 | 21.3891 | 21.6012 | 0.2121
GEN-2020-054 | 04 - Southeast | 5921 | SPP-CAP1 | 345 | 21.3891 | 21.6012 | 0.2121
GEN-2020-054 | 04 - Southeast | 5922 | SPP-CAP2 | 345 | 21.3891 | 21.6012 | 0.2121
GEN-2020-054 | 04 - Southeast | 5923 | SPP-CAP3 | 345 | 21.3891 | 21.6012 | 0.2121
GEN-2020-054 | 04 - Southeast | 5924 | SPP-REAC1 | 345 | 21.3891 | 21.6012 | 0.2121
GEN-2020-054 | 04 - Southeast | 5925 | ERCOTMAINBU | 345 | 4.7923 | 4.7923 | 0
GEN-2020-054 | 04 - Southeast | 337363 | 3SAREPTA! | 115 | 19.6022 | 19.6062 | 0.004
GEN-2020-054 | 04 - Southeast | 337376 | 7SAREPTA% | 345 | 9.8255 | 9.829 | 0.0035
GEN-2020-054 | 04 - Southeast | 337562 | 7EL | 345 | 13.7307 | 13.7317 | 0.001
GEN-2020-054 | 04 - Southeast | 337672 | 4MURFBORO | 138 | 2.8754 | 2.8759 | 0.0005
GEN-2020-054 | 04 - Southeast | 500250 | DOLHILL7 | 345 | 12.3246 | 12.3276 | 0.003
GEN-2020-054 | 04 - Southeast | 500260 | DOLHILL6 | 230 | 14.9911 | 14.9932 | 0.0021
GEN-2020-054 | 04 - Southeast | 504029 | SFOREMAN | 138 | 8.6754 | 8.6861 | 0.0107
GEN-2020-054 | 04 - Southeast | 504030 | SFORE_1 | 69 | 2.8394 | 2.84 | 0.0006
GEN-2020-054 | 04 - Southeast | 504122 | MCNAB | 115 | 13.7345 | 13.7458 | 0.0113
GEN-2020-054 | 04 - Southeast | 504123 | LOCKSBRG | 138 | 5.9108 | 5.9155 | 0.0047
GEN-2020-054 | 04 - Southeast | 504124 | ASHDWN_W | 138 | 10.1043 | 10.1181 | 0.0138
GEN-2020-054 | 04 - Southeast | 504363 | NE-TEXARK2 | 69 | 5.3493 | 5.3513 | 0.002
GEN-2020-054 | 04 - Southeast | 507402 | ASHDWNR4 | 138 | 10.3848 | 10.3993 | 0.0145
GEN-2020-054 | 04 - Southeast | 507421 | FOREMAN2 | 69 | 3.6662 | 3.667 | 0.0008
GEN-2020-054 | 04 - Southeast | 507427 | OKAY | 69 | 7.4429 | 7.446 | 0.0031
GEN-2020-054 | 04 - Southeast | 507428 | OKAY | 138 | 10.2373 | 10.2499 | 0.0126
GEN-2020-054 | 04 - Southeast | 507429 | PATTERS2 | 69 | 14.3344 | 14.3491 | 0.0147
GEN-2020-054 | 04 - Southeast | 507431 | PATTERS4 | 138 | 13.57 | 13.5959 | 0.0259
GEN-2020-054 | 04 - Southeast | 507434 | SNASHVL4 | 138 | 3.7072 | 3.7085 | 0.0013
GEN-2020-054 | 04 - Southeast | 507454 | TURK | 138 | 27.3279 | 27.411 | 0.0831
GEN-2020-054 | 04 - Southeast | 507455 | TURK | 345 | 11.7026 | 11.7688 | 0.0662
GEN-2020-054 | 04 - Southeast | 507456 | TURK | 115 | 17.0744 | 17.0954 | 0.021
GEN-2020-054 | 04 - Southeast | 507463 | BARITERDTP | 138 | 3.6018 | 3.6034 | 0.0016
GEN-2020-054 | 04 - Southeast | 507732 | GENMOTR4 | 138 | 17.6014 | 17.6092 | 0.0078
GEN-2020-054 | 04 - Southeast | 507748 | POWELL | 138 | 19.18 | 19.1878 | 0.0078
GEN-2020-054 | 04 - Southeast | 507755 | S | 138 | 22.7507 | 22.7613 | 0.0106
GEN-2020-054 | 04 - Southeast | 507757 | SPRIDGE4 | 138 | 11.1616 | 11.1645 | 0.0029
GEN-2020-054 | 04 - Southeast | 507759 | SW | 138 | 30.581 | 30.6046 | 0.0236
GEN-2020-054 | 04 - Southeast | 507760 | SW | 345 | 15.982 | 16.0013 | 0.0193
GEN-2020-054 | 04 - Southeast | 507774 | NORAM | 138 | 17.0805 | 17.0873 | 0.0068
GEN-2020-054 | 04 - Southeast | 507793 | LEASIDE | 138 | 22.1305 | 22.1418 | 0.0113
GEN-2020-054 | 04 - Southeast | 508049 | NASH | 138 | 21.0918 | 21.1835 | 0.0917
GEN-2020-054 | 04 - Southeast | 508051 | ASHDOWN2 | 69 | 11.9314 | 11.9419 | 0.0105
GEN-2020-054 | 04 - Southeast | 508053 | BANN | 69 | 20.6174 | 20.6569 | 0.0395
GEN-2020-054 | 04 - Southeast | 508054 | BANN | 138 | 22.114 | 22.2133 | 0.0993
GEN-2020-054 | 04 - Southeast | 508056 | BRYANML4 | 138 | 7.1322 | 7.1375 | 0.0053
GEN-2020-054 | 04 - Southeast | 508064 | MUNZCTY4 | 138 | 7.2346 | 7.24 | 0.0054
GEN-2020-054 | 04 - Southeast | 508065 | NEKOOSA2 | 69 | 6.2869 | 6.2898 | 0.0029
GEN-2020-054 | 04 - Southeast | 508069 | NNBOSTN4 | 138 | 11.1479 | 11.1643 | 0.0164
GEN-2020-054 | 04 - Southeast | 508070 | NWT-BNT4 | 138 | 26.8234 | 26.9779 | 0.1545
GEN-2020-054 | 04 - Southeast | 508071 | NWTXARK4 | 138 | 28.1281 | 28.3004 | 0.1723
GEN-2020-054 | 04 - Southeast | 508072 | NWTXARK7 | 345 | 16.6035 | 16.7965 | 0.193
GEN-2020-054 | 04 - Southeast | 508075 | REDSPRG4 | 138 | 14.5608 | 14.6016 | 0.0408
GEN-2020-054 | 04 - Southeast | 508078 | SETEXAR4 | 138 | 11.085 | 11.1058 | 0.0208
GEN-2020-054 | 04 - Southeast | 508079 | SUGARHL2 | 69 | 17.847 | 17.8742 | 0.0272
GEN-2020-054 | 04 - Southeast | 508080 | SUGARHL4 | 138 | 12.5634 | 12.5911 | 0.0277
GEN-2020-054 | 04 - Southeast | 508081 | SUGHLET2 | 69 | 17.0233 | 17.0479 | 0.0246
GEN-2020-054 | 04 - Southeast | 508082 | SUGHLWT2 | 69 | 16.9753 | 17.0002 | 0.0249
GEN-2020-054 | 04 - Southeast | 508089 | WATLANT2 | 69 | 8.2195 | 8.2229 | 0.0034
GEN-2020-054 | 04 - Southeast | 508090 | WATLANT4 | 138 | 7.3661 | 7.3722 | 0.0061
GEN-2020-054 | 04 - Southeast | 508091 | ALUMAX | 138 | 18.4836 | 18.5541 | 0.0705
GEN-2020-054 | 04 - Southeast | 508105 | MANDEVILTP4 | 138 | 9.6045 | 9.6178 | 0.0133
GEN-2020-054 | 04 - Southeast | 508106 | CASSTP4 | 138 | 7.349 | 7.3553 | 0.0063
GEN-2020-054 | 04 - Southeast | 508296 | LSSOUTH2 | 69 | 10.0812 | 10.0847 | 0.0035
GEN-2020-054 | 04 - Southeast | 508297 | LSSOUTH4 | 138 | 17.1995 | 17.2186 | 0.0191
GEN-2020-054 | 04 - Southeast | 508298 | LYDIA | 345 | 13.6054 | 14.1015 | 0.4961
GEN-2020-054 | 04 - Southeast | 508313 | PITTSB_4 | 138 | 8.7512 | 8.7558 | 0.0046
GEN-2020-054 | 04 - Southeast | 508337 | CHAPELH4 | 138 | 7.3241 | 7.3274 | 0.0033
GEN-2020-054 | 04 - Southeast | 508350 | PERDUE | 69 | 13.3001 | 13.3039 | 0.0038
GEN-2020-054 | 04 - Southeast | 508351 | PERDUE | 138 | 10.5655 | 10.5705 | 0.005
GEN-2020-054 | 04 - Southeast | 508355 | WELSHRE4 | 138 | 7.3384 | 7.3416 | 0.0032
GEN-2020-054 | 04 - Southeast | 508359 | WELSH | 345 | 21.3891 | 21.6012 | 0.2121
GEN-2020-054 | 04 - Southeast | 508369 | EXXONM | 138 | 6.5674 | 6.5694 | 0.002
GEN-2020-054 | 04 - Southeast | 508552 | LLAMOND4 | 138 | 6.9915 | 6.9941 | 0.0026
GEN-2020-054 | 04 - Southeast | 508557 | MARSHL-4 | 138 | 16.5592 | 16.5666 | 0.0074
GEN-2020-054 | 04 - Southeast | 508560 | NEWGLAD4 | 138 | 9.4724 | 9.4758 | 0.0034
GEN-2020-054 | 04 - Southeast | 508562 | PIRKEY | 138 | 42.0177 | 42.0588 | 0.0411
GEN-2020-054 | 04 - Southeast | 508563 | PIRKEY | 345 | 17.1217 | 17.1469 | 0.0252
GEN-2020-054 | 04 - Southeast | 508564 | PLILER | 138 | 12.1697 | 12.1763 | 0.0066
GEN-2020-054 | 04 - Southeast | 508566 | SABMINT4 | 138 | 34.1459 | 34.1731 | 0.0272
GEN-2020-054 | 04 - Southeast | 508567 | SCOTTSV4 | 138 | 12.0674 | 12.071 | 0.0036
GEN-2020-054 | 04 - Southeast | 508571 | SPRHILL4 | 138 | 8.3005 | 8.3047 | 0.0042
GEN-2020-054 | 04 - Southeast | 508572 | LEBROCK7 | 345 | 16.0189 | 16.0391 | 0.0202
GEN-2020-054 | 04 - Southeast | 508585 | TENRUSK7 | 345 | 8.1167 | 8.1203 | 0.0036
GEN-2020-054 | 04 - Southeast | 508595 | HALLSVLS4 | 138 | 18.5203 | 18.5286 | 0.0083
GEN-2020-054 | 04 - Southeast | 508806 | LIEBERM4 | 138 | 16.6581 | 16.665 | 0.0069
GEN-2020-054 | 04 - Southeast | 508808 | LONGWD | 138 | 24.7593 | 24.7758 | 0.0165
GEN-2020-054 | 04 - Southeast | 508809 | LONGWD | 345 | 16.0191 | 16.0421 | 0.023
GEN-2020-054 | 04 - Southeast | 508816 | OAKPH | 138 | 19.3231 | 19.333 | 0.0099
GEN-2020-054 | 04 - Southeast | 508827 | NGPL | 138 | 10.1031 | 10.1087 | 0.0056
GEN-2020-054 | 04 - Southeast | 508831 | DIANA | 138 | 29.5097 | 29.5754 | 0.0657
GEN-2020-054 | 04 - Southeast | 508832 | DIANA | 345 | 19.0829 | 19.1686 | 0.0857
GEN-2020-054 | 04 - Southeast | 508833 | IPCJEFF4 | 138 | 12.1438 | 12.1496 | 0.0058
GEN-2020-054 | 04 - Southeast | 508835 | JEFFRSN4 | 138 | 13.4137 | 13.4209 | 0.0072
GEN-2020-054 | 04 - Southeast | 508837 | NGPLTAP4 | 138 | 13.4015 | 13.4115 | 0.01
GEN-2020-054 | 04 - Southeast | 508840 | WILKES | 138 | 30.4557 | 30.5081 | 0.0524
GEN-2020-054 | 04 - Southeast | 508841 | WILKES | 345 | 17.6942 | 17.7735 | 0.0793
GEN-2020-054 | 04 - Southeast | 509092 | EASTON | 138 | 24.4139 | 24.4241 | 0.0102
GEN-2020-054 | 04 - Southeast | 509603 | BIGSAND4 | 138 | 7.0947 | 7.097 | 0.0023
GEN-2020-054 | 04 - Southeast | 509607 | DIAN | 138 | 11.5551 | 11.5651 | 0.01
GEN-2020-054 | 04 - Southeast | 509624 | LAKEPIN4 | 138 | 7.3675 | 7.3697 | 0.0022
GEN-2020-054 | 04 - Southeast | 509628 | NOONDAY4 | 138 | 5.8004 | 5.8029 | 0.0025
GEN-2020-054 | 04 - Southeast | 509639 | DIANASW4 | 138 | 12.035 | 12.0459 | 0.0109
GEN-2020-054 | 04 - Southeast | 509666 | DUGLASV4 | 138 | 5.0308 | 5.0334 | 0.0026
GEN-2020-054 | 04 - Southeast | 510864 | B.BOW | 138 | 6.1956 | 6.1996 | 0.004
GEN-2020-054 | 04 - Southeast | 510866 | V-WEYCO4 | 138 | 9.9035 | 9.9191 | 0.0156
GEN-2020-054 | 04 - Southeast | 510868 | GA | 69 | 2.4979 | 2.4984 | 0.0005
GEN-2020-054 | 04 - Southeast | 510869 | W | 69 | 3.8823 | 3.8835 | 0.0012
GEN-2020-054 | 04 - Southeast | 510870 | WCITYTP2 | 69 | 6.4629 | 6.4661 | 0.0032
GEN-2020-054 | 04 - Southeast | 510875 | KI | 69 | 3.4715 | 3.4724 | 0.0009
GEN-2020-054 | 04 - Southeast | 510876 | KIPUMPT2 | 69 | 4.9158 | 4.9176 | 0.0018
GEN-2020-054 | 04 - Southeast | 510886 | IDABEL-4 | 138 | 6.8935 | 6.8994 | 0.0059
GEN-2020-054 | 04 - Southeast | 510888 | B.BOWTP4 | 138 | 7.2158 | 7.2212 | 0.0054
GEN-2020-054 | 04 - Southeast | 510890 | CRAIGJT4 | 138 | 8.7082 | 8.7153 | 0.0071
GEN-2020-054 | 04 - Southeast | 510893 | HUGO---2 | 69 | 5.1273 | 5.1292 | 0.0019
GEN-2020-054 | 04 - Southeast | 510894 | VALYTIM2 | 69 | 2.7062 | 2.7065 | 0.0003
GEN-2020-054 | 04 - Southeast | 510901 | HUGO---4 | 138 | 3.5377 | 3.5395 | 0.0018
GEN-2020-054 | 04 - Southeast | 510907 | PITTSB-7 | 345 | 16.701 | 16.7355 | 0.0345
GEN-2020-054 | 04 - Southeast | 510910 | VALIANT2 | 69 | 7.4467 | 7.451 | 0.0043
GEN-2020-054 | 04 - Southeast | 510911 | VALIANT7 | 345 | 17.1465 | 17.3049 | 0.1584
GEN-2020-054 | 04 - Southeast | 510917 | FTOWSON2 | 69 | 3.8102 | 3.8113 | 0.0011
GEN-2020-054 | 04 - Southeast | 510918 | VALIANT4 | 138 | 15.922 | 15.9621 | 0.0401
GEN-2020-054 | 04 - Southeast | 510920 | SAWYER | 69 | 3.9072 | 3.9083 | 0.0011
GEN-2020-054 | 04 - Southeast | 510925 | KIOWA | 345 | 16.3422 | 16.3752 | 0.033
GEN-2020-054 | 04 - Southeast | 510946 | C-RIVER4 | 138 | 13.6772 | 13.6807 | 0.0035
GEN-2020-054 | 04 - Southeast | 510951 | TALAWANDA | 138 | 9.7581 | 9.7595 | 0.0014
GEN-2020-054 | 04 - Southeast | 514808 | JOHNCO | 138 | 15.6321 | 15.6362 | 0.0041
GEN-2020-054 | 04 - Southeast | 514809 | JOHNCO | 345 | 11.2431 | 11.2498 | 0.0067
GEN-2020-054 | 04 - Southeast | 514880 | NORTWST7 | 345 | 33.6238 | 33.6247 | 0.0009
GEN-2020-054 | 04 - Southeast | 514907 | ARCADIA4 | 138 | 47.1885 | 47.1892 | 0.0007
GEN-2020-054 | 04 - Southeast | 514908 | ARCADIA7 | 345 | 28.6397 | 28.6404 | 0.0007
GEN-2020-054 | 04 - Southeast | 514909 | REDBUD | 345 | 27.6105 | 27.6111 | 0.0006
GEN-2020-054 | 04 - Southeast | 514933 | DRAPER | 138 | 45.2774 | 45.2793 | 0.0019
GEN-2020-054 | 04 - Southeast | 514934 | DRAPER | 345 | 31.4178 | 31.4206 | 0.0028
GEN-2020-054 | 04 - Southeast | 515044 | SEMINOL4 | 138 | 40.8084 | 40.813 | 0.0046
GEN-2020-054 | 04 - Southeast | 515045 | SEMINOL7 | 345 | 32.1547 | 32.1637 | 0.009
GEN-2020-054 | 04 - Southeast | 515055 | MAUD | 138 | 20.1804 | 20.1812 | 0.0008
GEN-2020-054 | 04 - Southeast | 515100 | PAOLI- | 138 | 10.3078 | 10.3083 | 0.0005
GEN-2020-054 | 04 - Southeast | 515120 | RUSSET-4 | 138 | 11.4416 | 11.4439 | 0.0023
GEN-2020-054 | 04 - Southeast | 515122 | SXMLCKT4 | 138 | 11.1906 | 11.1923 | 0.0017
GEN-2020-054 | 04 - Southeast | 515135 | SUNNYSD4 | 138 | 19.1104 | 19.1158 | 0.0054
GEN-2020-054 | 04 - Southeast | 515136 | SUNNYSD7 | 345 | 12.5413 | 12.5482 | 0.0069
GEN-2020-054 | 04 - Southeast | 515150 | CANEYCK4 | 138 | 9.1628 | 9.1642 | 0.0014
GEN-2020-054 | 04 - Southeast | 515224 | MUSKOGE7 | 345 | 28.1517 | 28.1532 | 0.0015
GEN-2020-054 | 04 - Southeast | 515422 | C-RIVER7 | 345 | 11.711 | 11.7184 | 0.0074
GEN-2020-054 | 04 - Southeast | 515531 | VANOSTP4 | 138 | 13.3447 | 13.3456 | 0.0009
GEN-2020-054 | 04 - Southeast | 515977 | LKKONWA4 | 138 | 39.871 | 39.8754 | 0.0044
GEN-2020-054 | 04 - Southeast | 516006 | DMNDSPG7 | 345 | 7.5362 | 7.539 | 0.0028
GEN-2020-054 | 04 - Southeast | 516096 | NORMHLL7 | 345 | 28.3882 | 28.39 | 0.0018
GEN-2020-054 | 04 - Southeast | 520411 | SAWYER4 | 138 | 10.5926 | 10.6016 | 0.009
GEN-2020-054 | 04 - Southeast | 520419 | GARVIN4 | 138 | 5.9851 | 5.9882 | 0.0031
GEN-2020-054 | 04 - Southeast | 520560 | HUGOITC4 | 138 | 22.9236 | 22.9729 | 0.0493
GEN-2020-054 | 04 - Southeast | 520918 | FROGVIL4 | 138 | 10.7143 | 10.7236 | 0.0093
GEN-2020-054 | 04 - Southeast | 520948 | HUGO | 138 | 23.1112 | 23.1589 | 0.0477
GEN-2020-054 | 04 - Southeast | 521036 | RATTAN | 138 | 6.8431 | 6.8464 | 0.0033
GEN-2020-054 | 04 - Southeast | 521079 | VALLANT4 | 138 | 8.6512 | 8.6578 | 0.0066
GEN-2020-054 | 04 - Southeast | 521098 | WSBNKTP4 | 138 | 6.5824 | 6.5855 | 0.0031
GEN-2020-054 | 04 - Southeast | 521157 | HUGO | 345 | 12.8144 | 12.8771 | 0.0627
GEN-2020-054 | 04 - Southeast | 555234 | NSUB345 | 345 | 28.4118 | 28.4136 | 0.0018
GEN-2020-054 | 04 - Southeast | 560088 | G16-063-TAP | 345 | 8.2669 | 8.2748 | 0.0079
GEN-2020-054 | 04 - Southeast | 587430 | GEN-2016-06 | 345 | 8.1554 | 8.163 | 0.0076
GEN-2020-054 | 04 - Southeast | 588670 | GEN-2017-02 | 138 | 18.9954 | 19.0276 | 0.0322
GEN-2020-054 | 04 - Southeast | 588838 | G17-092-SWY | 345 | 20.2718 | 20.2763 | 0.0045
GEN-2020-054 | 04 - Southeast | 588839 | G17-092-TAP | 345 | 20.2718 | 20.2763 | 0.0045
GEN-2020-054 | 04 - Southeast | 589130 | GEN-2017-07 | 345 | 8.255 | 8.2628 | 0.0078
GEN-2020-054 | 04 - Southeast | 760032 | GEN-2017-13 | 345 | 6.7843 | 6.7843 | 0
GEN-2020-054 | 04 - Southeast | 760830 | GEN-2017-14 | 345 | 4.2189 | 4.2196 | 0.0007
GEN-2020-054 | 04 - Southeast | 760851 | GEN-2017-15 | 345 | 3.8386 | 3.8391 | 0.0005
GEN-2020-054 | 04 - Southeast | 761859 | GEN-2017-16 | 345 | 7.1043 | 7.1064 | 0.0021
GEN-2020-054 | 04 - Southeast | 762427 | GEN-2018-00 | 138 | 11.2053 | 11.2213 | 0.016
GEN-2020-054 | 04 - Southeast | 762431 | G18-003-TAP | 138 | 11.2053 | 11.2213 | 0.016
GEN-2020-054 | 04 - Southeast | 762845 | GEN-2018-05 | 345 | 12.2909 | 12.304 | 0.0131
GEN-2020-054 | 04 - Southeast | 763131 | GEN-2018-08 | 345 | 10.2451 | 10.2577 | 0.0126
GEN-2020-054 | 04 - Southeast | 763164 | GEN-2018-08 | 345 | 13.0208 | 13.4745 | 0.4537
GEN-2020-054 | 04 - Southeast | 764075 | GEN-2020-05 | 345 | 12.0368 | 12.5353 | 0.4985
GEN-2020-054 | 04 - Southeast | 764115 | G20-074-TAP | 345 | 11.5679 | 11.572 | 0.0041
GEN-2020-054 | 04 - Southeast | 764270 | GEN-2020-01 | 345 | 11.2431 | 11.2498 | 0.0067
GEN-2020-054 | 04 - Southeast | 764510 | GEN-2020-02 | 345 | 16.9159 | 17.0701 | 0.1542
GEN-2020-054 | 04 - Southeast | 764520 | G20-020-TAP | 345 | 16.9565 | 17.1115 | 0.155
GEN-2020-023 | 04 - Southeast | 505610 | KEYSTON4 | 138 | 22.5616 | 22.563 | 0.0014
GEN-2020-023 | 04 - Southeast | 509755 | WEKIWA-7 | 345 | 22.111 | 22.1157 | 0.0047
GEN-2020-023 | 04 - Southeast | 509757 | WEKIWA-4 | 138 | 32.6995 | 32.7025 | 0.003
GEN-2020-023 | 04 - Southeast | 509782 | R.S.S.-7 | 345 | 31.9439 | 31.9466 | 0.0027
GEN-2020-023 | 04 - Southeast | 509812 | SHEFFD-4 | 138 | 25.8228 | 25.824 | 0.0012
GEN-2020-023 | 04 - Southeast | 509823 | WED-TAP4 | 138 | 19.0827 | 19.0835 | 0.0008
GEN-2020-023 | 04 - Southeast | 509851 | P&P | 138 | 15.1524 | 15.1529 | 0.0005
GEN-2020-023 | 04 - Southeast | 509852 | T.NO.--7 | 345 | 23.842 | 23.8464 | 0.0044
GEN-2020-023 | 04 - Southeast | 509870 | SAPLPRD7 | 345 | 22.6367 | 22.6392 | 0.0025
GEN-2020-023 | 04 - Southeast | 509871 | SAPLPRD4 | 138 | 33.0257 | 33.0271 | 0.0014
GEN-2020-023 | 04 - Southeast | 509895 | T.NO.2-4 | 138 | 35.1915 | 35.1938 | 0.0023
GEN-2020-023 | 04 - Southeast | 510406 | N.E.S.-7 | 345 | 18.802 | 18.8032 | 0.0012
GEN-2020-023 | 04 - Southeast | 511425 | TUTCONT4 | 138 | 10.0611 | 10.0615 | 0.0004
GEN-2020-023 | 04 - Southeast | 512694 | CLEVLND7 | 345 | 14.8498 | 14.8555 | 0.0057
GEN-2020-023 | 04 - Southeast | 512726 | SILVCTYGR4 | 138 | 15.5111 | 15.512 | 0.0009
GEN-2020-023 | 04 - Southeast | 512729 | CLEVLND | 138 | 16.5169 | 16.5188 | 0.0019
GEN-2020-023 | 04 - Southeast | 513596 | IGLOOV | 345 | 19.7421 | 19.7426 | 0.0005
GEN-2020-023 | 04 - Southeast | 514642 | BRCKWND4 | 138 | 7.736 | 7.741 | 0.005
GEN-2020-023 | 04 - Southeast | 514701 | BUNCHCK4 | 138 | 6.5933 | 6.5954 | 0.0021
GEN-2020-023 | 04 - Southeast | 514704 | MILLERT4 | 138 | 20.0817 | 20.0872 | 0.0055
GEN-2020-023 | 04 - Southeast | 514705 | COWCRK | 69 | 4.0359 | 4.0361 | 0.0002
GEN-2020-023 | 04 - Southeast | 514706 | COWCRK | 138 | 11.119 | 11.122 | 0.003
GEN-2020-023 | 04 - Southeast | 514707 | PERRY | 138 | 10.8567 | 10.8595 | 0.0028
GEN-2020-023 | 04 - Southeast | 514708 | OTTER | 138 | 8.6808 | 8.6864 | 0.0056
GEN-2020-023 | 04 - Southeast | 514709 | FRMNTAP4 | 138 | 17.9641 | 17.9989 | 0.0348
GEN-2020-023 | 04 - Southeast | 514710 | WAUKOMI4 | 138 | 10.6557 | 10.6634 | 0.0077
GEN-2020-023 | 04 - Southeast | 514711 | WAUKOTP4 | 138 | 15.7138 | 15.7369 | 0.0231
GEN-2020-023 | 04 - Southeast | 514712 | FAIRMON4 | 138 | 13.9639 | 13.9826 | 0.0187
GEN-2020-023 | 04 - Southeast | 514713 | WRVALLY4 | 138 | 8.4462 | 8.4489 | 0.0027
GEN-2020-023 | 04 - Southeast | 514714 | WOODRNG4 | 138 | 19.2104 | 19.2516 | 0.0412
GEN-2020-023 | 04 - Southeast | 514715 | WOODRNG7 | 345 | 18.9003 | 19.2151 | 0.3148
GEN-2020-023 | 04 - Southeast | 514718 | VANCE | 69 | 6.9974 | 6.9995 | 0.0021
GEN-2020-023 | 04 - Southeast | 514721 | IMO | 69 | 11.9324 | 11.9381 | 0.0057
GEN-2020-023 | 04 - Southeast | 514722 | CLEVETP2 | 69 | 11.7012 | 11.7068 | 0.0056
GEN-2020-023 | 04 - Southeast | 514727 | ENID | 69 | 10.8455 | 10.8505 | 0.005
GEN-2020-023 | 04 - Southeast | 514730 | SO4TH | 69 | 13.7243 | 13.7323 | 0.008
GEN-2020-023 | 04 - Southeast | 514731 | SO4TH | 138 | 15.3197 | 15.3412 | 0.0215
GEN-2020-023 | 04 - Southeast | 514733 | MARSHL | 138 | 7.9422 | 7.9462 | 0.004
GEN-2020-023 | 04 - Southeast | 514734 | GLENWD | 138 | 10.2531 | 10.2618 | 0.0087
GEN-2020-023 | 04 - Southeast | 514743 | OSAGE | 138 | 16.9936 | 16.9979 | 0.0043
GEN-2020-023 | 04 - Southeast | 514774 | HENESEY4 | 138 | 9.8941 | 9.8973 | 0.0032
GEN-2020-023 | 04 - Southeast | 514789 | MENOTAP4 | 138 | 7.0349 | 7.0378 | 0.0029
GEN-2020-023 | 04 - Southeast | 514790 | IMO | 138 | 11.8674 | 11.879 | 0.0116
GEN-2020-023 | 04 - Southeast | 514798 | SNRPMPT4 | 138 | 20.1342 | 20.1398 | 0.0056
GEN-2020-023 | 04 - Southeast | 514799 | SNRPMP | 138 | 11.1753 | 11.177 | 0.0017
GEN-2020-023 | 04 - Southeast | 514801 | MINCO | 345 | 26.2771 | 26.2868 | 0.0097
GEN-2020-023 | 04 - Southeast | 514802 | SOONER | 138 | 30.6752 | 30.688 | 0.0128
GEN-2020-023 | 04 - Southeast | 514803 | SOONER | 345 | 27.9208 | 27.9738 | 0.053
GEN-2020-023 | 04 - Southeast | 514815 | BRECKNR4 | 138 | 13.812 | 13.829 | 0.017
GEN-2020-023 | 04 - Southeast | 514819 | EL-RENO4 | 138 | 16.8163 | 16.8182 | 0.0019
GEN-2020-023 | 04 - Southeast | 514820 | JENSENT4 | 138 | 18.2309 | 18.233 | 0.0021
GEN-2020-023 | 04 - Southeast | 514825 | KAYWIND7 | 345 | 12.628 | 12.6324 | 0.0044
GEN-2020-023 | 04 - Southeast | 514827 | CTNWOOD4 | 138 | 18.282 | 18.2861 | 0.0041
GEN-2020-023 | 04 - Southeast | 514828 | KETCHTP4 | 138 | 26.954 | 26.9594 | 0.0054
GEN-2020-023 | 04 - Southeast | 514829 | PINE | 138 | 12.3289 | 12.3307 | 0.0018
GEN-2020-023 | 04 - Southeast | 514830 | FITZGRD4 | 138 | 9.1009 | 9.1018 | 0.0009
GEN-2020-023 | 04 - Southeast | 514831 | WATRLOO4 | 138 | 14.5659 | 14.5679 | 0.002
GEN-2020-023 | 04 - Southeast | 514854 | BRADEN | 138 | 31.9275 | 31.9361 | 0.0086
GEN-2020-023 | 04 - Southeast | 514863 | HAYMAKR4 | 138 | 26.9324 | 26.9375 | 0.0051
GEN-2020-023 | 04 - Southeast | 514864 | PIEDMNT4 | 138 | 22.6476 | 22.652 | 0.0044
GEN-2020-023 | 04 - Southeast | 514873 | LNEOAK | 138 | 27.2875 | 27.2938 | 0.0063
GEN-2020-023 | 04 - Southeast | 514879 | NORTWST4 | 138 | 45.0068 | 45.0259 | 0.0191
GEN-2020-023 | 04 - Southeast | 514880 | NORTWST7 | 345 | 33.5893 | 33.6247 | 0.0354
GEN-2020-023 | 04 - Southeast | 514881 | SPRNGCK7 | 345 | 23.5868 | 23.6042 | 0.0174
GEN-2020-023 | 04 - Southeast | 514894 | CZECHAL4 | 138 | 28.9723 | 28.9768 | 0.0045
GEN-2020-023 | 04 - Southeast | 514895 | SARA | 138 | 20.1379 | 20.1402 | 0.0023
GEN-2020-023 | 04 - Southeast | 514898 | CIMARON4 | 138 | 45.9418 | 45.9573 | 0.0155
GEN-2020-023 | 04 - Southeast | 514901 | CIMARON7 | 345 | 36.6386 | 36.6785 | 0.0399
GEN-2020-023 | 04 - Southeast | 514906 | JNSKAMO4 | 138 | 21.5694 | 21.5711 | 0.0017
GEN-2020-023 | 04 - Southeast | 514907 | ARCADIA4 | 138 | 47.1792 | 47.1892 | 0.01
GEN-2020-023 | 04 - Southeast | 514908 | ARCADIA7 | 345 | 28.6326 | 28.6404 | 0.0078
GEN-2020-023 | 04 - Southeast | 514909 | REDBUD | 345 | 27.6047 | 27.6111 | 0.0064
GEN-2020-023 | 04 - Southeast | 514929 | PLVALLY4 | 138 | 56.3612 | 56.3755 | 0.0143
GEN-2020-023 | 04 - Southeast | 514934 | DRAPER | 345 | 31.4082 | 31.4206 | 0.0124
GEN-2020-023 | 04 - Southeast | 515006 | MORRISN4 | 138 | 13.6905 | 13.6932 | 0.0027
GEN-2020-023 | 04 - Southeast | 515011 | STILWTR4 | 138 | 13.8229 | 13.8247 | 0.0018
GEN-2020-023 | 04 - Southeast | 515045 | SEMINOL7 | 345 | 32.1589 | 32.1637 | 0.0048
GEN-2020-023 | 04 - Southeast | 515373 | LBRTYLK4 | 138 | 14.1808 | 14.1829 | 0.0021
GEN-2020-023 | 04 - Southeast | 515375 | WWRDEHV7 | 345 | 21.2374 | 21.2419 | 0.0045
GEN-2020-023 | 04 - Southeast | 515376 | WWRDEHV4 | 138 | 24.5638 | 24.5659 | 0.0021
GEN-2020-023 | 04 - Southeast | 515377 | CRESENT4 | 138 | 10.6291 | 10.6305 | 0.0014
GEN-2020-023 | 04 - Southeast | 515383 | ENIDINT4 | 138 | 12.9318 | 12.9466 | 0.0148
GEN-2020-023 | 04 - Southeast | 515407 | TATONGA7 | 345 | 17.3999 | 17.4068 | 0.0069
GEN-2020-023 | 04 - Southeast | 515412 | DMNCRKT4 | 138 | 13.7357 | 13.7384 | 0.0027
GEN-2020-023 | 04 - Southeast | 515426 | RDRUNNR4 | 138 | 8.6916 | 8.6943 | 0.0027
GEN-2020-023 | 04 - Southeast | 515444 | MCNOWND7 | 345 | 26.1565 | 26.1662 | 0.0097
GEN-2020-023 | 04 - Southeast | 515447 | MORISNT4 | 138 | 13.7168 | 13.7195 | 0.0027
GEN-2020-023 | 04 - Southeast | 515448 | CRSRDSW7 | 345 | 12.0743 | 12.0776 | 0.0033
GEN-2020-023 | 04 - Southeast | 515456 | CHSTNTT2 | 69 | 11.4949 | 11.5005 | 0.0056
GEN-2020-023 | 04 - Southeast | 515461 | RNDBARN4 | 138 | 44.4391 | 44.448 | 0.0089
GEN-2020-023 | 04 - Southeast | 515465 | LGARBER4 | 138 | 21.6131 | 21.6151 | 0.002
GEN-2020-023 | 04 - Southeast | 515476 | HUNTERS7 | 345 | 12.9645 | 13.0497 | 0.0852
GEN-2020-023 | 04 - Southeast | 515477 | CHSHLMV7 | 345 | 12.9459 | 13.0309 | 0.085
GEN-2020-023 | 04 - Southeast | 515497 | MATHWSN7 | 345 | 33.8542 | 33.9142 | 0.06
GEN-2020-023 | 04 - Southeast | 515543 | RENFROW7 | 345 | 12.239 | 12.2781 | 0.0391
GEN-2020-023 | 04 - Southeast | 515544 | RENFROW4 | 138 | 14.3706 | 14.385 | 0.0144
GEN-2020-023 | 04 - Southeast | 515546 | GRANTCO4 | 138 | 6.4464 | 6.4492 | 0.0028
GEN-2020-023 | 04 - Southeast | 515547 | GRANTCO2 | 69 | 7.4483 | 7.4499 | 0.0016
GEN-2020-023 | 04 - Southeast | 515549 | MNCWND37 | 345 | 15.1448 | 15.1479 | 0.0031
GEN-2020-023 | 04 - Southeast | 515554 | BVRCNTY7 | 345 | 13.3328 | 13.3337 | 0.0009
GEN-2020-023 | 04 - Southeast | 515569 | MDFRDTP4 | 138 | 11.5407 | 11.549 | 0.0083
GEN-2020-023 | 04 - Southeast | 515576 | RANCHRD7 | 345 | 14.6133 | 14.6202 | 0.0069
GEN-2020-023 | 04 - Southeast | 515582 | SLNGWND7 | 345 | 8.4404 | 8.4419 | 0.0015
GEN-2020-023 | 04 - Southeast | 515585 | MAMTHPW7 | 345 | 13.469 | 13.4731 | 0.0041
GEN-2020-023 | 04 - Southeast | 515599 | G07621119-2 | 345 | 13.0906 | 13.0923 | 0.0017
GEN-2020-023 | 04 - Southeast | 515600 | KNGFSHR7 | 345 | 10.755 | 10.7581 | 0.0031
GEN-2020-023 | 04 - Southeast | 515605 | CANADN7 | 345 | 11.8049 | 11.8087 | 0.0038
GEN-2020-023 | 04 - Southeast | 515610 | FSHRTAP7 | 345 | 16.5152 | 16.5227 | 0.0075
GEN-2020-023 | 04 - Southeast | 515621 | OPENSKY7 | 345 | 12.6632 | 12.6676 | 0.0044
GEN-2020-023 | 04 - Southeast | 515641 | PLNSMEN4 | 138 | 13.818 | 13.836 | 0.018
GEN-2020-023 | 04 - Southeast | 515646 | GRNTWD | 345 | 10.7884 | 10.8184 | 0.03
GEN-2020-023 | 04 - Southeast | 515688 | FRNTWND7 | 345 | 11.4151 | 11.4192 | 0.0041
GEN-2020-023 | 04 - Southeast | 515694 | ARMFTWD4 | 138 | 8.6484 | 8.6539 | 0.0055
GEN-2020-023 | 04 - Southeast | 515800 | GRACMNT7 | 345 | 20.7537 | 20.7563 | 0.0026
GEN-2020-023 | 04 - Southeast | 515852 | DGRASSE7 | 345 | 14.5949 | 14.5974 | 0.0025
GEN-2020-023 | 04 - Southeast | 515875 | REDNGTN7 | 345 | 16.8643 | 16.9691 | 0.1048
GEN-2020-023 | 04 - Southeast | 515877 | REDDIRT7 | 345 | 16.86 | 16.9647 | 0.1047
GEN-2020-023 | 04 - Southeast | 515894 | THUNDER7 | 345 | 10.9208 | 10.9285 | 0.0077
GEN-2020-023 | 04 - Southeast | 515961 | GUTHRIE7 | 345 | 12.4993 | 12.5009 | 0.0016
GEN-2020-023 | 04 - Southeast | 515978 | OTOETAP4 | 138 | 16.106 | 16.1095 | 0.0035
GEN-2020-023 | 04 - Southeast | 515990 | SKELTON7 | 345 | 4.9494 | 4.9658 | 0.0164
GEN-2020-023 | 04 - Southeast | 516010 | PINTAIL7 | 345 | 16.6788 | 16.7837 | 0.1049
GEN-2020-023 | 04 - Southeast | 516019 | KINGWD | 345 | 16.6211 | 16.7252 | 0.1041
GEN-2020-023 | 04 - Southeast | 516059 | BECKHAM7 | 345 | 13.0898 | 13.0904 | 0.0006
GEN-2020-023 | 04 - Southeast | 516066 | FRNT2WD7 | 345 | 11.4162 | 11.4202 | 0.004
GEN-2020-023 | 04 - Southeast | 516096 | NORMHLL7 | 345 | 28.3781 | 28.39 | 0.0119
GEN-2020-023 | 04 - Southeast | 516097 | NORMHLL4 | 138 | 54.6326 | 54.6462 | 0.0136
GEN-2020-023 | 04 - Southeast | 516106 | BOBCAT | 345 | 14.8529 | 14.8546 | 0.0017
GEN-2020-023 | 04 - Southeast | 520409 | WFEC_RNFRO4 | 138 | 10.5788 | 10.586 | 0.0072
GEN-2020-023 | 04 - Southeast | 520434 | WAKTASW4 | 138 | 6.2573 | 6.2589 | 0.0016
GEN-2020-023 | 04 - Southeast | 520461 | GARBER | 138 | 4.4071 | 4.4078 | 0.0007
GEN-2020-023 | 04 - Southeast | 520535 | BULFTTP4 | 138 | 9.2606 | 9.2629 | 0.0023
GEN-2020-023 | 04 - Southeast | 520882 | DOVERSW4 | 138 | 10.9363 | 10.9391 | 0.0028
GEN-2020-023 | 04 - Southeast | 521006 | MARSHAL4 | 138 | 7.9422 | 7.9462 | 0.004
GEN-2020-023 | 04 - Southeast | 521073 | TWNLKSW4 | 138 | 9.9234 | 9.9247 | 0.0013
GEN-2020-023 | 04 - Southeast | 521100 | WARREN | 138 | 6.0864 | 6.0878 | 0.0014
GEN-2020-023 | 04 - Southeast | 522397 | MEDFORD4 | 138 | 7.515 | 7.5185 | 0.0035
GEN-2020-023 | 04 - Southeast | 529200 | OMCDLEC7 | 345 | 14.5878 | 14.5946 | 0.0068
GEN-2020-023 | 04 - Southeast | 532796 | WICHITA7 | 345 | 20.5478 | 20.5564 | 0.0086
GEN-2020-023 | 04 - Southeast | 532798 | VIOLA | 345 | 12.8078 | 12.8223 | 0.0145
GEN-2020-023 | 04 - Southeast | 533075 | VIOLA | 138 | 22.7139 | 22.727 | 0.0131
GEN-2020-023 | 04 - Southeast | 555234 | NSUB345 | 345 | 28.4017 | 28.4136 | 0.0119
GEN-2020-023 | 04 - Southeast | 560053 | G15-052T | 345 | 11.9063 | 11.9092 | 0.0029
GEN-2020-023 | 04 - Southeast | 560056 | G15-066T | 345 | 18.9359 | 18.955 | 0.0191
GEN-2020-023 | 04 - Southeast | 560389 | GEN-2010-05 | 138 | 32.6995 | 32.7025 | 0.003
GEN-2020-023 | 04 - Southeast | 585040 | GEN-2015-06 | 345 | 18.7526 | 18.7713 | 0.0187
GEN-2020-023 | 04 - Southeast | 587210 | GEN-2016-03 | 138 | 7.8117 | 7.8123 | 0.0006
GEN-2020-023 | 04 - Southeast | 587804 | G16-119-TAP | 345 | 15.1996 | 15.2103 | 0.0107
GEN-2020-023 | 04 - Southeast | 587950 | GEN-2016-11 | 345 | 9.0075 | 9.0109 | 0.0034
GEN-2020-023 | 04 - Southeast | 587955 | GEN2016-119 | 345 | 7.7559 | 7.7583 | 0.0024
GEN-2020-023 | 04 - Southeast | 588190 | GEN-2016-12 | 345 | 4.7073 | 4.722 | 0.0147
GEN-2020-023 | 04 - Southeast | 588364 | G16-153-TAP | 345 | 6.7107 | 6.7142 | 0.0035
GEN-2020-023 | 04 - Southeast | 760032 | GEN-2017-13 | 345 | 6.7841 | 6.7843 | 0.0002
GEN-2020-023 | 04 - Southeast | 760809 | GEN-2017-20 | 345 | 8.8049 | 8.8247 | 0.0198
GEN-2020-023 | 04 - Southeast | 761250 | GEN-2017-23 | 345 | 25.2957 | 25.3047 | 0.009
GEN-2020-023 | 04 - Southeast | 762321 | GEN-2017-16 | 345 | 11.2338 | 11.34 | 0.1062
GEN-2020-023 | 04 - Southeast | 762342 | GEN-2017-17 | 345 | 7.861 | 7.9125 | 0.0515
GEN-2020-023 | 04 - Southeast | 763065 | GEN-2018-07 | 345 | 14.1698 | 14.1762 | 0.0064
GEN-2020-023 | 04 - Southeast | 763069 | G18-071_TAP | 345 | 14.2248 | 14.2313 | 0.0065
GEN-2020-023 | 04 - Southeast | 763417 | GEN-2018-12 | 345 | 10.4056 | 10.4262 | 0.0206
GEN-2020-023 | 04 - Southeast | 763421 | G18-128-TAP | 345 | 11.5033 | 11.5285 | 0.0252
GEN-2020-023 | 04 - Southeast | 763527 | GEN-2019-01 | 345 | 18.5237 | 18.5272 | 0.0035
GEN-2020-023 | 04 - Southeast | 764525 | GEN-2020-02 | 345 | 16.8716 | 17.1869 | 0.3153
GEN-2020-023 | 04 - Southeast | 900001 | TRAVERSE3 | 345 | 6.9557 | 6.9572 | 0.0015
GEN-2020-023 | 04 - Southeast | 900002 | TRAVERSE-2 | 345 | 5.5808 | 5.5817 | 0.0009
GEN-2020-023 | 04 - Southeast | 900004 | TRW2-TRW3 | 345 | 6.2233 | 6.2245 | 0.0012
GEN-2020-020 | 04 - Southeast | 5917 | SPPMAINBUS | 345 | 21.5412 | 21.6012 | 0.06
GEN-2020-020 | 04 - Southeast | 5918 | DCEAST | 345 | 4.7923 | 4.7923 | 0
GEN-2020-020 | 04 - Southeast | 5919 | WELSHDC1 | 345 | 21.5412 | 21.6012 | 0.06
GEN-2020-020 | 04 - Southeast | 5921 | SPP-CAP1 | 345 | 21.5412 | 21.6012 | 0.06
GEN-2020-020 | 04 - Southeast | 5922 | SPP-CAP2 | 345 | 21.5412 | 21.6012 | 0.06
GEN-2020-020 | 04 - Southeast | 5923 | SPP-CAP3 | 345 | 21.5412 | 21.6012 | 0.06
GEN-2020-020 | 04 - Southeast | 5924 | SPP-REAC1 | 345 | 21.5412 | 21.6012 | 0.06
GEN-2020-020 | 04 - Southeast | 337363 | 3SAREPTA! | 115 | 19.6047 | 19.6062 | 0.0015
GEN-2020-020 | 04 - Southeast | 337376 | 7SAREPTA% | 345 | 9.8277 | 9.829 | 0.0013
GEN-2020-020 | 04 - Southeast | 337562 | 7EL | 345 | 13.7313 | 13.7317 | 0.0004
GEN-2020-020 | 04 - Southeast | 337672 | 4MURFBORO | 138 | 2.8755 | 2.8759 | 0.0004
GEN-2020-020 | 04 - Southeast | 500250 | DOLHILL7 | 345 | 12.3266 | 12.3276 | 0.001
GEN-2020-020 | 04 - Southeast | 504029 | SFOREMAN | 138 | 8.6788 | 8.6861 | 0.0073
GEN-2020-020 | 04 - Southeast | 504030 | SFORE_1 | 69 | 2.8396 | 2.84 | 0.0004
GEN-2020-020 | 04 - Southeast | 504122 | MCNAB | 115 | 13.7364 | 13.7458 | 0.0094
GEN-2020-020 | 04 - Southeast | 504123 | LOCKSBRG | 138 | 5.9118 | 5.9155 | 0.0037
GEN-2020-020 | 04 - Southeast | 504124 | ASHDWN_W | 138 | 10.1064 | 10.1181 | 0.0117
GEN-2020-020 | 04 - Southeast | 504363 | NE-TEXARK2 | 69 | 5.3499 | 5.3513 | 0.0014
GEN-2020-020 | 04 - Southeast | 507402 | ASHDWNR4 | 138 | 10.3879 | 10.3993 | 0.0114
GEN-2020-020 | 04 - Southeast | 507421 | FOREMAN2 | 69 | 3.6662 | 3.667 | 0.0008
GEN-2020-020 | 04 - Southeast | 507427 | OKAY | 69 | 7.4433 | 7.446 | 0.0027
GEN-2020-020 | 04 - Southeast | 507428 | OKAY | 138 | 10.2395 | 10.2499 | 0.0104
GEN-2020-020 | 04 - Southeast | 507429 | PATTERS2 | 69 | 14.3378 | 14.3491 | 0.0113
GEN-2020-020 | 04 - Southeast | 507431 | PATTERS4 | 138 | 13.5759 | 13.5959 | 0.02
GEN-2020-020 | 04 - Southeast | 507434 | SNASHVL4 | 138 | 3.7075 | 3.7085 | 0.001
GEN-2020-020 | 04 - Southeast | 507454 | TURK | 138 | 27.3409 | 27.411 | 0.0701
GEN-2020-020 | 04 - Southeast | 507455 | TURK | 345 | 11.7079 | 11.7688 | 0.0609
GEN-2020-020 | 04 - Southeast | 507456 | TURK | 115 | 17.0777 | 17.0954 | 0.0177
GEN-2020-020 | 04 - Southeast | 507463 | BARITERDTP | 138 | 3.6021 | 3.6034 | 0.0013
GEN-2020-020 | 04 - Southeast | 507759 | SW | 138 | 30.5965 | 30.6046 | 0.0081
GEN-2020-020 | 04 - Southeast | 507760 | SW | 345 | 15.9947 | 16.0013 | 0.0066
GEN-2020-020 | 04 - Southeast | 507774 | NORAM | 138 | 17.0849 | 17.0873 | 0.0024
GEN-2020-020 | 04 - Southeast | 508049 | NASH | 138 | 21.1283 | 21.1835 | 0.0552
GEN-2020-020 | 04 - Southeast | 508051 | ASHDOWN2 | 69 | 11.9341 | 11.9419 | 0.0078
GEN-2020-020 | 04 - Southeast | 508053 | BANN | 69 | 20.6325 | 20.6569 | 0.0244
GEN-2020-020 | 04 - Southeast | 508054 | BANN | 138 | 22.1533 | 22.2133 | 0.06
GEN-2020-020 | 04 - Southeast | 508056 | BRYANML4 | 138 | 7.1346 | 7.1375 | 0.0029
GEN-2020-020 | 04 - Southeast | 508064 | MUNZCTY4 | 138 | 7.2371 | 7.24 | 0.0029
GEN-2020-020 | 04 - Southeast | 508065 | NEKOOSA2 | 69 | 6.2876 | 6.2898 | 0.0022
GEN-2020-020 | 04 - Southeast | 508069 | NNBOSTN4 | 138 | 11.1541 | 11.1643 | 0.0102
GEN-2020-020 | 04 - Southeast | 508070 | NWT-BNT4 | 138 | 26.8853 | 26.9779 | 0.0926
GEN-2020-020 | 04 - Southeast | 508071 | NWTXARK4 | 138 | 28.1973 | 28.3004 | 0.1031
GEN-2020-020 | 04 - Southeast | 508072 | NWTXARK7 | 345 | 16.6882 | 16.7965 | 0.1083
GEN-2020-020 | 04 - Southeast | 508075 | REDSPRG4 | 138 | 14.5772 | 14.6016 | 0.0244
GEN-2020-020 | 04 - Southeast | 508078 | SETEXAR4 | 138 | 11.0922 | 11.1058 | 0.0136
GEN-2020-020 | 04 - Southeast | 508079 | SUGARHL2 | 69 | 17.8565 | 17.8742 | 0.0177
GEN-2020-020 | 04 - Southeast | 508080 | SUGARHL4 | 138 | 12.5728 | 12.5911 | 0.0183
GEN-2020-020 | 04 - Southeast | 508081 | SUGHLET2 | 69 | 17.0318 | 17.0479 | 0.0161
GEN-2020-020 | 04 - Southeast | 508082 | SUGHLWT2 | 69 | 16.9841 | 17.0002 | 0.0161
GEN-2020-020 | 04 - Southeast | 508089 | WATLANT2 | 69 | 8.2211 | 8.2229 | 0.0018
GEN-2020-020 | 04 - Southeast | 508090 | WATLANT4 | 138 | 7.369 | 7.3722 | 0.0032
GEN-2020-020 | 04 - Southeast | 508091 | ALUMAX | 138 | 18.5117 | 18.5541 | 0.0424
GEN-2020-020 | 04 - Southeast | 508105 | MANDEVILTP4 | 138 | 9.6082 | 9.6178 | 0.0096
GEN-2020-020 | 04 - Southeast | 508106 | CASSTP4 | 138 | 7.352 | 7.3553 | 0.0033
GEN-2020-020 | 04 - Southeast | 508296 | LSSOUTH2 | 69 | 10.0833 | 10.0847 | 0.0014
GEN-2020-020 | 04 - Southeast | 508297 | LSSOUTH4 | 138 | 17.2117 | 17.2186 | 0.0069
GEN-2020-020 | 04 - Southeast | 508298 | LYDIA | 345 | 14.0042 | 14.1015 | 0.0973
GEN-2020-020 | 04 - Southeast | 508313 | PITTSB_4 | 138 | 8.7541 | 8.7558 | 0.0017
GEN-2020-020 | 04 - Southeast | 508337 | CHAPELH4 | 138 | 7.3261 | 7.3274 | 0.0013
GEN-2020-020 | 04 - Southeast | 508351 | PERDUE | 138 | 10.5689 | 10.5705 | 0.0016
GEN-2020-020 | 04 - Southeast | 508355 | WELSHRE4 | 138 | 7.3404 | 7.3416 | 0.0012
GEN-2020-020 | 04 - Southeast | 508359 | WELSH | 345 | 21.5412 | 21.6012 | 0.06
GEN-2020-020 | 04 - Southeast | 508557 | MARSHL-4 | 138 | 16.5642 | 16.5666 | 0.0024
GEN-2020-020 | 04 - Southeast | 508562 | PIRKEY | 138 | 42.0461 | 42.0588 | 0.0127
GEN-2020-020 | 04 - Southeast | 508563 | PIRKEY | 345 | 17.1393 | 17.1469 | 0.0076
GEN-2020-020 | 04 - Southeast | 508567 | SCOTTSV4 | 138 | 12.0698 | 12.071 | 0.0012
GEN-2020-020 | 04 - Southeast | 508571 | SPRHILL4 | 138 | 8.3034 | 8.3047 | 0.0013
GEN-2020-020 | 04 - Southeast | 508572 | LEBROCK7 | 345 | 16.033 | 16.0391 | 0.0061
GEN-2020-020 | 04 - Southeast | 508806 | LIEBERM4 | 138 | 16.6625 | 16.665 | 0.0025
GEN-2020-020 | 04 - Southeast | 508808 | LONGWD | 138 | 24.7699 | 24.7758 | 0.0059
GEN-2020-020 | 04 - Southeast | 508809 | LONGWD | 345 | 16.0338 | 16.0421 | 0.0083
GEN-2020-020 | 04 - Southeast | 508816 | OAKPH | 138 | 19.3295 | 19.333 | 0.0035
GEN-2020-020 | 04 - Southeast | 508831 | DIANA | 138 | 29.5552 | 29.5754 | 0.0202
GEN-2020-020 | 04 - Southeast | 508832 | DIANA | 345 | 19.1434 | 19.1686 | 0.0252
GEN-2020-020 | 04 - Southeast | 508833 | IPCJEFF4 | 138 | 12.1474 | 12.1496 | 0.0022
GEN-2020-020 | 04 - Southeast | 508835 | JEFFRSN4 | 138 | 13.4182 | 13.4209 | 0.0027
GEN-2020-020 | 04 - Southeast | 508837 | NGPLTAP4 | 138 | 13.4084 | 13.4115 | 0.0031
GEN-2020-020 | 04 - Southeast | 508840 | WILKES | 138 | 30.487 | 30.5081 | 0.0211
GEN-2020-020 | 04 - Southeast | 508841 | WILKES | 345 | 17.743 | 17.7735 | 0.0305
GEN-2020-020 | 04 - Southeast | 509624 | LAKEPIN4 | 138 | 7.3689 | 7.3697 | 0.0008
GEN-2020-020 | 04 - Southeast | 509639 | DIANASW4 | 138 | 12.0425 | 12.0459 | 0.0034
GEN-2020-020 | 04 - Southeast | 509666 | DUGLASV4 | 138 | 5.032 | 5.0334 | 0.0014
GEN-2020-020 | 04 - Southeast | 510864 | B.BOW | 138 | 6.1918 | 6.1996 | 0.0078
GEN-2020-020 | 04 - Southeast | 510866 | V-WEYCO4 | 138 | 9.8756 | 9.9191 | 0.0435
GEN-2020-020 | 04 - Southeast | 510868 | GA | 69 | 2.497 | 2.4984 | 0.0014
GEN-2020-020 | 04 - Southeast | 510869 | W | 69 | 3.8802 | 3.8835 | 0.0033
GEN-2020-020 | 04 - Southeast | 510870 | WCITYTP2 | 69 | 6.4571 | 6.4661 | 0.009
GEN-2020-020 | 04 - Southeast | 510875 | KI | 69 | 3.4698 | 3.4724 | 0.0026
GEN-2020-020 | 04 - Southeast | 510876 | KIPUMPT2 | 69 | 4.9125 | 4.9176 | 0.0051
GEN-2020-020 | 04 - Southeast | 510886 | IDABEL-4 | 138 | 6.8859 | 6.8994 | 0.0135
GEN-2020-020 | 04 - Southeast | 510888 | B.BOWTP4 | 138 | 7.2106 | 7.2212 | 0.0106
GEN-2020-020 | 04 - Southeast | 510890 | CRAIGJT4 | 138 | 8.7029 | 8.7153 | 0.0124
GEN-2020-020 | 04 - Southeast | 510893 | HUGO---2 | 69 | 5.1241 | 5.1292 | 0.0051
GEN-2020-020 | 04 - Southeast | 510894 | VALYTIM2 | 69 | 2.7055 | 2.7065 | 0.001
GEN-2020-020 | 04 - Southeast | 510901 | HUGO---4 | 138 | 3.5344 | 3.5395 | 0.0051
GEN-2020-020 | 04 - Southeast | 510907 | PITTSB-7 | 345 | 16.6346 | 16.7355 | 0.1009
GEN-2020-020 | 04 - Southeast | 510910 | VALIANT2 | 69 | 7.439 | 7.451 | 0.012
GEN-2020-020 | 04 - Southeast | 510911 | VALIANT7 | 345 | 16.8459 | 17.3049 | 0.459
GEN-2020-020 | 04 - Southeast | 510917 | FTOWSON2 | 69 | 3.8083 | 3.8113 | 0.003
GEN-2020-020 | 04 - Southeast | 510918 | VALIANT4 | 138 | 15.8504 | 15.9621 | 0.1117
GEN-2020-020 | 04 - Southeast | 510920 | SAWYER | 69 | 3.9053 | 3.9083 | 0.003
GEN-2020-020 | 04 - Southeast | 510925 | KIOWA | 345 | 16.2786 | 16.3752 | 0.0966
GEN-2020-020 | 04 - Southeast | 510946 | C-RIVER4 | 138 | 13.6707 | 13.6807 | 0.01
GEN-2020-020 | 04 - Southeast | 510951 | TALAWANDA | 138 | 9.7556 | 9.7595 | 0.0039
GEN-2020-020 | 04 - Southeast | 514808 | JOHNCO | 138 | 15.6241 | 15.6362 | 0.0121
GEN-2020-020 | 04 - Southeast | 514809 | JOHNCO | 345 | 11.2302 | 11.2498 | 0.0196
GEN-2020-020 | 04 - Southeast | 514880 | NORTWST7 | 345 | 33.6221 | 33.6247 | 0.0026
GEN-2020-020 | 04 - Southeast | 514907 | ARCADIA4 | 138 | 47.1872 | 47.1892 | 0.002
GEN-2020-020 | 04 - Southeast | 514908 | ARCADIA7 | 345 | 28.6385 | 28.6404 | 0.0019
GEN-2020-020 | 04 - Southeast | 514909 | REDBUD | 345 | 27.6095 | 27.6111 | 0.0016
GEN-2020-020 | 04 - Southeast | 514933 | DRAPER | 138 | 45.2738 | 45.2793 | 0.0055
GEN-2020-020 | 04 - Southeast | 514934 | DRAPER | 345 | 31.4123 | 31.4206 | 0.0083
GEN-2020-020 | 04 - Southeast | 515044 | SEMINOL4 | 138 | 40.7997 | 40.813 | 0.0133
GEN-2020-020 | 04 - Southeast | 515045 | SEMINOL7 | 345 | 32.1374 | 32.1637 | 0.0263
GEN-2020-020 | 04 - Southeast | 515055 | MAUD | 138 | 20.1788 | 20.1812 | 0.0024
GEN-2020-020 | 04 - Southeast | 515100 | PAOLI- | 138 | 10.307 | 10.3083 | 0.0013
GEN-2020-020 | 04 - Southeast | 515120 | RUSSET-4 | 138 | 11.4374 | 11.4439 | 0.0065
GEN-2020-020 | 04 - Southeast | 515122 | SXMLCKT4 | 138 | 11.1872 | 11.1923 | 0.0051
GEN-2020-020 | 04 - Southeast | 515135 | SUNNYSD4 | 138 | 19.1001 | 19.1158 | 0.0157
GEN-2020-020 | 04 - Southeast | 515136 | SUNNYSD7 | 345 | 12.528 | 12.5482 | 0.0202
GEN-2020-020 | 04 - Southeast | 515150 | CANEYCK4 | 138 | 9.1601 | 9.1642 | 0.0041
GEN-2020-020 | 04 - Southeast | 515224 | MUSKOGE7 | 345 | 28.1489 | 28.1532 | 0.0043
GEN-2020-020 | 04 - Southeast | 515422 | C-RIVER7 | 345 | 11.697 | 11.7184 | 0.0214
GEN-2020-020 | 04 - Southeast | 515531 | VANOSTP4 | 138 | 13.343 | 13.3456 | 0.0026
GEN-2020-020 | 04 - Southeast | 515977 | LKKONWA4 | 138 | 39.8627 | 39.8754 | 0.0127
GEN-2020-020 | 04 - Southeast | 516006 | DMNDSPG7 | 345 | 7.5306 | 7.539 | 0.0084
GEN-2020-020 | 04 - Southeast | 516096 | NORMHLL7 | 345 | 28.3847 | 28.39 | 0.0053
GEN-2020-020 | 04 - Southeast | 520411 | SAWYER4 | 138 | 10.5762 | 10.6016 | 0.0254
GEN-2020-020 | 04 - Southeast | 520419 | GARVIN4 | 138 | 5.9812 | 5.9882 | 0.007
GEN-2020-020 | 04 - Southeast | 520560 | HUGOITC4 | 138 | 22.8337 | 22.9729 | 0.1392
GEN-2020-020 | 04 - Southeast | 520918 | FROGVIL4 | 138 | 10.6973 | 10.7236 | 0.0263
GEN-2020-020 | 04 - Southeast | 520948 | HUGO | 138 | 23.025 | 23.1589 | 0.1339
GEN-2020-020 | 04 - Southeast | 521036 | RATTAN | 138 | 6.8371 | 6.8464 | 0.0093
GEN-2020-020 | 04 - Southeast | 521079 | VALLANT4 | 138 | 8.6407 | 8.6578 | 0.0171
GEN-2020-020 | 04 - Southeast | 521098 | WSBNKTP4 | 138 | 6.5769 | 6.5855 | 0.0086
GEN-2020-020 | 04 - Southeast | 521157 | HUGO | 345 | 12.6955 | 12.8771 | 0.1816
GEN-2020-020 | 04 - Southeast | 555234 | NSUB345 | 345 | 28.4083 | 28.4136 | 0.0053
GEN-2020-020 | 04 - Southeast | 560088 | G16-063-TAP | 345 | 8.2518 | 8.2748 | 0.023
GEN-2020-020 | 04 - Southeast | 587430 | GEN-2016-06 | 345 | 8.1408 | 8.163 | 0.0222
GEN-2020-020 | 04 - Southeast | 588670 | GEN-2017-02 | 138 | 18.9369 | 19.0276 | 0.0907
GEN-2020-020 | 04 - Southeast | 588838 | G17-092-SWY | 345 | 20.2634 | 20.2763 | 0.0129
GEN-2020-020 | 04 - Southeast | 588839 | G17-092-TAP | 345 | 20.2634 | 20.2763 | 0.0129
GEN-2020-020 | 04 - Southeast | 589130 | GEN-2017-07 | 345 | 8.2399 | 8.2628 | 0.0229
GEN-2020-020 | 04 - Southeast | 760032 | GEN-2017-13 | 345 | 6.7842 | 6.7843 | 0.0001
GEN-2020-020 | 04 - Southeast | 760830 | GEN-2017-14 | 345 | 4.2176 | 4.2196 | 0.002
GEN-2020-020 | 04 - Southeast | 760851 | GEN-2017-15 | 345 | 3.8375 | 3.8391 | 0.0016
GEN-2020-020 | 04 - Southeast | 761859 | GEN-2017-16 | 345 | 7.1001 | 7.1064 | 0.0063
GEN-2020-020 | 04 - Southeast | 762427 | GEN-2018-00 | 138 | 11.2115 | 11.2213 | 0.0098
GEN-2020-020 | 04 - Southeast | 762431 | G18-003-TAP | 138 | 11.2115 | 11.2213 | 0.0098
GEN-2020-020 | 04 - Southeast | 762845 | GEN-2018-05 | 345 | 12.2993 | 12.304 | 0.0047
GEN-2020-020 | 04 - Southeast | 763131 | GEN-2018-08 | 345 | 10.2209 | 10.2577 | 0.0368
GEN-2020-020 | 04 - Southeast | 763164 | GEN-2018-08 | 345 | 13.3857 | 13.4745 | 0.0888
GEN-2020-020 | 04 - Southeast | 764075 | GEN-2020-05 | 345 | 12.4591 | 12.5353 | 0.0762
GEN-2020-020 | 04 - Southeast | 764115 | G20-074-TAP | 345 | 11.5602 | 11.572 | 0.0118
GEN-2020-020 | 04 - Southeast | 764270 | GEN-2020-01 | 345 | 11.2302 | 11.2498 | 0.0196
GEN-2020-020 | 04 - Southeast | 764510 | GEN-2020-02 | 345 | 16.6089 | 17.0701 | 0.4612
GEN-2020-020 | 04 - Southeast | 764520 | G20-020-TAP | 345 | 16.6503 | 17.1115 | 0.4612
GEN-2020-016 | 04 - Southeast | 511435 | SNYDER-4 | 138 | 7.1858 | 7.5284 | 0.3426
GEN-2020-016 | 04 - Southeast | 511440 | ALTUSJT4 | 138 | 5.1006 | 5.192 | 0.0914
GEN-2020-016 | 04 - Southeast | 511441 | ALTUSJT2 | 69 | 5.5926 | 5.6517 | 0.0591
GEN-2020-016 | 04 - Southeast | 511444 | ROSVTAP2 | 69 | 3.8724 | 3.8881 | 0.0157
GEN-2020-016 | 04 - Southeast | 511460 | FREDJC-2 | 69 | 2.7507 | 2.7696 | 0.0189
GEN-2020-016 | 04 - Southeast | 511462 | HEADRIK2 | 69 | 4.4899 | 4.5347 | 0.0448
GEN-2020-016 | 04 - Southeast | 511472 | TIPTE | 69 | 3.607 | 3.6395 | 0.0325
GEN-2020-016 | 04 - Southeast | 511475 | SNYDER-2 | 69 | 7.5318 | 7.6762 | 0.1444
GEN-2020-016 | 04 - Southeast | 511495 | TOMSTEED2 | 69 | 4.1156 | 4.1448 | 0.0292
GEN-2020-016 | 04 - Southeast | 511500 | CACHE4 | 138 | 8.5631 | 8.67 | 0.1069
GEN-2020-016 | 04 - Southeast | 511510 | LAIRGST4 | 138 | 12.7719 | 12.8638 | 0.0919
GEN-2020-016 | 04 - Southeast | 511543 | TIPTN | 69 | 4.4882 | 4.5329 | 0.0447
GEN-2020-016 | 04 - Southeast | 511545 | TIPTON | 69 | 2.4606 | 2.4757 | 0.0151
GEN-2020-016 | 04 - Southeast | 520404 | MDCPRK4 | 138 | 5.1648 | 5.407 | 0.2422
GEN-2020-016 | 04 - Southeast | 520410 | CACHE4 | 138 | 4.6921 | 5.1826 | 0.4905
GEN-2020-016 | 04 - Southeast | 520491 | NAVAJO | 69 | 2.2639 | 2.2784 | 0.0145
GEN-2020-016 | 04 - Southeast | 520513 | BCV | 138 | 5.145 | 5.303 | 0.158
GEN-2020-016 | 04 - Southeast | 520528 | ROSEVLT2 | 69 | 3.777 | 3.8016 | 0.0246
GEN-2020-016 | 04 - Southeast | 520541 | SNYDRSB2 | 69 | 6.9585 | 7.1537 | 0.1952
GEN-2020-016 | 04 - Southeast | 520602 | RANDLET4 | 138 | 1.9755 | 2.0413 | 0.0658
GEN-2020-016 | 04 - Southeast | 520805 | ALTUSSW2 | 69 | 3.5757 | 3.6098 | 0.0341
GEN-2020-016 | 04 - Southeast | 520814 | ANADARK4 | 138 | 34.9865 | 35.129 | 0.1425
GEN-2020-016 | 04 - Southeast | 520914 | FREDRIK2 | 69 | 3.4302 | 3.4792 | 0.049
GEN-2020-016 | 04 - Southeast | 520926 | GRANFLD2 | 69 | 4.8708 | 4.9859 | 0.1151
GEN-2020-016 | 04 - Southeast | 520945 | HOLLSTR2 | 69 | 3.4573 | 3.5076 | 0.0503
GEN-2020-016 | 04 - Southeast | 520954 | INDHOMA4 | 138 | 4.0702 | 4.4154 | 0.3452
GEN-2020-016 | 04 - Southeast | 521009 | NAVJOTP2 | 69 | 3.6215 | 3.6589 | 0.0374
GEN-2020-016 | 04 - Southeast | 521024 | PARADSE4 | 138 | 5.4204 | 5.6338 | 0.2134
GEN-2020-016 | 04 - Southeast | 521043 | RUSSELL4 | 138 | 3.8874 | 3.9365 | 0.0491
GEN-2020-016 | 04 - Southeast | 521051 | SNYDER | 69 | 6.9585 | 7.1537 | 0.1952
GEN-2020-016 | 04 - Southeast | 521052 | SNYDER | 138 | 6.6713 | 7.0786 | 0.4073
GEN-2020-016 | 04 - Southeast | 521069 | TIPTON-2 | 69 | 2.0666 | 2.0841 | 0.0175
GEN-2020-016 | 04 - Southeast | 521070 | TIPTONJ2 | 69 | 3.9292 | 3.9928 | 0.0636
GEN-2020-016 | 04 - Southeast | 521106 | GRNDFLD4 | 138 | 3.0493 | 3.2086 | 0.1593
GEN-2020-016 | 04 - Southeast | 521129 | CHERRYRD | 138 | 5.6687 | 5.865 | 0.1963
GEN-2020-016 | 04 - Southeast | 521190 | CACHEJ4 | 138 | 5.0832 | 5.6779 | 0.5947
GEN-2020-016 | 04 - Southeast | 529340 | OMFRDFK | 69 | 3.2907 | 3.3358 | 0.0451
GEN-2020-016 | 04 - Southeast | 529345 | OMPARK-4 | 138 | 4.8693 | 4.9471 | 0.0778
GEN-2020-016 | 04 - Southeast | 562683 | GEN-2015-01 | 138 | 6.6553 | 7.0606 | 0.4053
GEN-2020-016 | 04 - Southeast | 588779 | G17-036_TAP | 138 | 7.1319 | 7.4602 | 0.3283
GEN-2020-016 | 04 - Southeast | 588780 | GEN-2017-03 | 138 | 6.8791 | 7.1842 | 0.3051
GEN-2020-016 | 04 - Southeast | 764495 | GEN-2020-01 | 138 | 4.8114 | 5.5715 | 0.7601
GEN-2020-016 | 04 - Southeast | 764505 | G20-016-TAP | 138 | 5.1116 | 5.8632 | 0.7516
GEN-2020-016 | 04 - Southeast | 765220 | GEN-2020-01 | 138 | 5.9159 | 6.1033 | 0.1874
GEN-2020-016 | 04 - Southeast | 765230 | G20-012-TAP | 138 | 5.9561 | 6.1463 | 0.1902
GEN-2020-016 | 04 - Southeast | 765231 | G20-012-SS1 | 138 | 5.9159 | 6.1033 | 0.1874
GEN-2020-015 | 04 - Southeast | 5917 | SPPMAINBUS | 345 | 21.5992 | 21.6012 | 0.002
GEN-2020-015 | 04 - Southeast | 505600 | TUPELO | 138 | 10.008 | 10.0107 | 0.0027
GEN-2020-015 | 04 - Southeast | 505602 | S | 138 | 8.3691 | 8.3778 | 0.0087
GEN-2020-015 | 04 - Southeast | 505604 | DENISON4 | 138 | 3.1138 | 3.115 | 0.0012
GEN-2020-015 | 04 - Southeast | 507428 | OKAY | 138 | 10.2495 | 10.2499 | 0.0004
GEN-2020-015 | 04 - Southeast | 507454 | TURK | 138 | 27.4086 | 27.411 | 0.0024
GEN-2020-015 | 04 - Southeast | 507455 | TURK | 345 | 11.7667 | 11.7688 | 0.0021
GEN-2020-015 | 04 - Southeast | 507456 | TURK | 115 | 17.0948 | 17.0954 | 0.0006
GEN-2020-015 | 04 - Southeast | 508071 | NWTXARK4 | 138 | 28.2968 | 28.3004 | 0.0036
GEN-2020-015 | 04 - Southeast | 508072 | NWTXARK7 | 345 | 16.7928 | 16.7965 | 0.0037
GEN-2020-015 | 04 - Southeast | 508080 | SUGARHL4 | 138 | 12.5904 | 12.5911 | 0.0007
GEN-2020-015 | 04 - Southeast | 508105 | MANDEVILTP4 | 138 | 9.6175 | 9.6178 | 0.0003
GEN-2020-015 | 04 - Southeast | 508298 | LYDIA | 345 | 14.0981 | 14.1015 | 0.0034
GEN-2020-015 | 04 - Southeast | 508359 | WELSH | 345 | 21.5992 | 21.6012 | 0.002
GEN-2020-015 | 04 - Southeast | 508832 | DIANA | 345 | 19.1678 | 19.1686 | 0.0008
GEN-2020-015 | 04 - Southeast | 508841 | WILKES | 345 | 17.7725 | 17.7735 | 0.001
GEN-2020-015 | 04 - Southeast | 509745 | CLARKSV7 | 345 | 20.5083 | 20.5087 | 0.0004
GEN-2020-015 | 04 - Southeast | 509782 | R.S.S.-7 | 345 | 31.9461 | 31.9466 | 0.0005
GEN-2020-015 | 04 - Southeast | 510866 | V-WEYCO4 | 138 | 9.9172 | 9.9191 | 0.0019
GEN-2020-015 | 04 - Southeast | 510870 | WCITYTP2 | 69 | 6.4657 | 6.4661 | 0.0004
GEN-2020-015 | 04 - Southeast | 510876 | KIPUMPT2 | 69 | 4.9174 | 4.9176 | 0.0002
GEN-2020-015 | 04 - Southeast | 510886 | IDABEL-4 | 138 | 6.8988 | 6.8994 | 0.0006
GEN-2020-015 | 04 - Southeast | 510888 | B.BOWTP4 | 138 | 7.2206 | 7.2212 | 0.0006
GEN-2020-015 | 04 - Southeast | 510893 | HUGO---2 | 69 | 5.1289 | 5.1292 | 0.0003
GEN-2020-015 | 04 - Southeast | 510901 | HUGO---4 | 138 | 3.5393 | 3.5395 | 0.0002
GEN-2020-015 | 04 - Southeast | 510907 | PITTSB-7 | 345 | 16.6968 | 16.7355 | 0.0387
GEN-2020-015 | 04 - Southeast | 510908 | MCALEST4 | 138 | 9.8343 | 9.8355 | 0.0012
GEN-2020-015 | 04 - Southeast | 510909 | MCALESTIND | 138 | 5.6349 | 5.6354 | 0.0005
GEN-2020-015 | 04 - Southeast | 510910 | VALIANT2 | 69 | 7.4504 | 7.451 | 0.0006
GEN-2020-015 | 04 - Southeast | 510911 | VALIANT7 | 345 | 17.289 | 17.3049 | 0.0159
GEN-2020-015 | 04 - Southeast | 510918 | VALIANT4 | 138 | 15.9573 | 15.9621 | 0.0048
GEN-2020-015 | 04 - Southeast | 510925 | KIOWA | 345 | 16.3382 | 16.3752 | 0.037
GEN-2020-015 | 04 - Southeast | 510946 | C-RIVER4 | 138 | 13.6768 | 13.6807 | 0.0039
GEN-2020-015 | 04 - Southeast | 510948 | EARLSBORO | 138 | 8.3613 | 8.3617 | 0.0004
GEN-2020-015 | 04 - Southeast | 510951 | TALAWANDA | 138 | 9.7581 | 9.7595 | 0.0014
GEN-2020-015 | 04 - Southeast | 511468 | L.E.S.-7 | 345 | 17.3139 | 17.3217 | 0.0078
GEN-2020-015 | 04 - Southeast | 511508 | BLANCHD4 | 138 | 6.475 | 6.4751 | 0.0001
GEN-2020-015 | 04 - Southeast | 511568 | TERRYRD7 | 345 | 11.865 | 11.8801 | 0.0151
GEN-2020-015 | 04 - Southeast | 511571 | RUSHSPR7 | 345 | 7.3303 | 7.3351 | 0.0048
GEN-2020-015 | 04 - Southeast | 514801 | MINCO | 345 | 26.2837 | 26.2868 | 0.0031
GEN-2020-015 | 04 - Southeast | 514808 | JOHNCO | 138 | 15.5683 | 15.6362 | 0.0679
GEN-2020-015 | 04 - Southeast | 514809 | JOHNCO | 345 | 11.09 | 11.2498 | 0.1598
GEN-2020-015 | 04 - Southeast | 514827 | CTNWOOD4 | 138 | 18.286 | 18.2861 | 0.0001
GEN-2020-015 | 04 - Southeast | 514879 | NORTWST4 | 138 | 45.0244 | 45.0259 | 0.0015
GEN-2020-015 | 04 - Southeast | 514880 | NORTWST7 | 345 | 33.6226 | 33.6247 | 0.0021
GEN-2020-015 | 04 - Southeast | 514881 | SPRNGCK7 | 345 | 23.6034 | 23.6042 | 0.0008
GEN-2020-015 | 04 - Southeast | 514901 | CIMARON7 | 345 | 36.6747 | 36.6785 | 0.0038
GEN-2020-015 | 04 - Southeast | 514906 | JNSKAMO4 | 138 | 21.5708 | 21.5711 | 0.0003
GEN-2020-015 | 04 - Southeast | 514907 | ARCADIA4 | 138 | 47.1878 | 47.1892 | 0.0014
GEN-2020-015 | 04 - Southeast | 514908 | ARCADIA7 | 345 | 28.6391 | 28.6404 | 0.0013
GEN-2020-015 | 04 - Southeast | 514909 | REDBUD | 345 | 27.61 | 27.6111 | 0.0011
GEN-2020-015 | 04 - Southeast | 514929 | PLVALLY4 | 138 | 56.3699 | 56.3755 | 0.0056
GEN-2020-015 | 04 - Southeast | 514933 | DRAPER | 138 | 45.2748 | 45.2793 | 0.0045
GEN-2020-015 | 04 - Southeast | 514934 | DRAPER | 345 | 31.4145 | 31.4206 | 0.0061
GEN-2020-015 | 04 - Southeast | 514946 | MIDWEST4 | 138 | 35.8797 | 35.8826 | 0.0029
GEN-2020-015 | 04 - Southeast | 514949 | SOONRTP4 | 138 | 24.4885 | 24.4901 | 0.0016
GEN-2020-015 | 04 - Southeast | 514961 | GM | 138 | 20.2687 | 20.2694 | 0.0007
GEN-2020-015 | 04 - Southeast | 515003 | BARNES | 138 | 16.3491 | 16.3496 | 0.0005
GEN-2020-015 | 04 - Southeast | 515044 | SEMINOL4 | 138 | 40.7997 | 40.813 | 0.0133
GEN-2020-015 | 04 - Southeast | 515045 | SEMINOL7 | 345 | 32.1489 | 32.1637 | 0.0148
GEN-2020-015 | 04 - Southeast | 515054 | MAUD | 69 | 10.7967 | 10.797 | 0.0003
GEN-2020-015 | 04 - Southeast | 515055 | MAUD | 138 | 20.1789 | 20.1812 | 0.0023
GEN-2020-015 | 04 - Southeast | 515075 | FRSTHIL4 | 138 | 13.901 | 13.9016 | 0.0006
GEN-2020-015 | 04 - Southeast | 515097 | WLNUTCK4 | 138 | 9.5629 | 9.5639 | 0.001
GEN-2020-015 | 04 - Southeast | 515099 | PALIOGE2 | 69 | 8.6047 | 8.6057 | 0.001
GEN-2020-015 | 04 - Southeast | 515100 | PAOLI- | 138 | 10.3054 | 10.3083 | 0.0029
GEN-2020-015 | 04 - Southeast | 515114 | CHIGLEY4 | 138 | 8.0922 | 8.0954 | 0.0032
GEN-2020-015 | 04 - Southeast | 515116 | ARBUCKL2 | 69 | 6.1284 | 6.1296 | 0.0012
GEN-2020-015 | 04 - Southeast | 515117 | ARBUCKL4 | 138 | 15.7043 | 15.722 | 0.0177
GEN-2020-015 | 04 - Southeast | 515120 | RUSSET-4 | 138 | 11.4189 | 11.4439 | 0.025
GEN-2020-015 | 04 - Southeast | 515121 | MILLCKT4 | 138 | 11.0103 | 11.0343 | 0.024
GEN-2020-015 | 04 - Southeast | 515122 | SXMLCKT4 | 138 | 11.1668 | 11.1923 | 0.0255
GEN-2020-015 | 04 - Southeast | 515123 | OAKLAW-4 | 138 | 12.7015 | 12.7124 | 0.0109
GEN-2020-015 | 04 - Southeast | 515124 | MAYSVIL4 | 138 | 6.0717 | 6.0732 | 0.0015
GEN-2020-015 | 04 - Southeast | 515128 | RATLIFF2 | 69 | 4.9312 | 4.9323 | 0.0011
GEN-2020-015 | 04 - Southeast | 515129 | RATLIFF4 | 138 | 6.0817 | 6.085 | 0.0033
GEN-2020-015 | 04 - Southeast | 515130 | POOLVIL4 | 138 | 7.4163 | 7.422 | 0.0057
GEN-2020-015 | 04 - Southeast | 515131 | FOX | 138 | 6.3132 | 6.3176 | 0.0044
GEN-2020-015 | 04 - Southeast | 515133 | BLUERIV4 | 138 | 10.4794 | 10.4842 | 0.0048
GEN-2020-015 | 04 - Southeast | 515134 | PRARPNT4 | 138 | 5.2162 | 5.218 | 0.0018
GEN-2020-015 | 04 - Southeast | 515135 | SUNNYSD4 | 138 | 19.0622 | 19.1158 | 0.0536
GEN-2020-015 | 04 - Southeast | 515136 | SUNNYSD7 | 345 | 12.4791 | 12.5482 | 0.0691
GEN-2020-015 | 04 - Southeast | 515137 | UNIROY | 138 | 12.7174 | 12.7393 | 0.0219
GEN-2020-015 | 04 - Southeast | 515138 | CARTER | 138 | 12.622 | 12.642 | 0.02
GEN-2020-015 | 04 - Southeast | 515143 | WOLFCRK4 | 138 | 9.54 | 9.5527 | 0.0127
GEN-2020-015 | 04 - Southeast | 515144 | LONEGRV4 | 138 | 13.4198 | 13.4458 | 0.026
GEN-2020-015 | 04 - Southeast | 515147 | GLASSES4 | 138 | 8.3646 | 8.3772 | 0.0126
GEN-2020-015 | 04 - Southeast | 515149 | MADINDT4 | 138 | 8.3621 | 8.3747 | 0.0126
GEN-2020-015 | 04 - Southeast | 515150 | CANEYCK4 | 138 | 9.1497 | 9.1642 | 0.0145
GEN-2020-015 | 04 - Southeast | 515151 | LTLCITY4 | 138 | 7.2543 | 7.2617 | 0.0074
GEN-2020-015 | 04 - Southeast | 515152 | BROWNTP4 | 138 | 8.219 | 8.2274 | 0.0084
GEN-2020-015 | 04 - Southeast | 515155 | BODLE | 138 | 6.275 | 6.2799 | 0.0049
GEN-2020-015 | 04 - Southeast | 515157 | BROWN | 138 | 8.3271 | 8.3357 | 0.0086
GEN-2020-015 | 04 - Southeast | 515158 | MADLIND4 | 138 | 7.7776 | 7.7886 | 0.011
GEN-2020-015 | 04 - Southeast | 515159 | COLBRTP4 | 138 | 6.3362 | 6.3412 | 0.005
GEN-2020-015 | 04 - Southeast | 515160 | MRIETA | 138 | 7.4203 | 7.4272 | 0.0069
GEN-2020-015 | 04 - Southeast | 515162 | FNDTION4 | 138 | 11.9135 | 11.9322 | 0.0187
GEN-2020-015 | 04 - Southeast | 515163 | ROCKYPT2 | 69 | 7.9003 | 7.9044 | 0.0041
GEN-2020-015 | 04 - Southeast | 515164 | ROCKYPT4 | 138 | 11.8765 | 11.8959 | 0.0194
GEN-2020-015 | 04 - Southeast | 515172 | SPRNDAL4 | 138 | 11.8633 | 11.8828 | 0.0195
GEN-2020-015 | 04 - Southeast | 515173 | BERWYN | 138 | 8.2642 | 8.2716 | 0.0074
GEN-2020-015 | 04 - Southeast | 515174 | VANOSS | 138 | 13.2137 | 13.2189 | 0.0052
GEN-2020-015 | 04 - Southeast | 515178 | PARKLN | 138 | 16.2925 | 16.2986 | 0.0061
GEN-2020-015 | 04 - Southeast | 515196 | MILLCRK4 | 138 | 9.0426 | 9.0588 | 0.0162
GEN-2020-015 | 04 - Southeast | 515224 | MUSKOGE7 | 345 | 28.1513 | 28.1532 | 0.0019
GEN-2020-015 | 04 - Southeast | 515235 | PECANCK7 | 345 | 21.911 | 21.9118 | 0.0008
GEN-2020-015 | 04 - Southeast | 515302 | FTSMITH7 | 345 | 10.0533 | 10.0533 | 0
GEN-2020-015 | 04 - Southeast | 515372 | ARDWEST4 | 138 | 12.5424 | 12.5636 | 0.0212
GEN-2020-015 | 04 - Southeast | 515415 | CHEEKTP4 | 138 | 12.0665 | 12.0874 | 0.0209
GEN-2020-015 | 04 - Southeast | 515420 | SCMMRCT2 | 69 | 9.0773 | 9.0827 | 0.0054
GEN-2020-015 | 04 - Southeast | 515422 | C-RIVER7 | 345 | 11.71 | 11.7184 | 0.0084
GEN-2020-015 | 04 - Southeast | 515461 | RNDBARN4 | 138 | 44.4468 | 44.448 | 0.0012
GEN-2020-015 | 04 - Southeast | 515465 | LGARBER4 | 138 | 21.6147 | 21.6151 | 0.0004
GEN-2020-015 | 04 - Southeast | 515497 | MATHWSN7 | 345 | 33.912 | 33.9142 | 0.0022
GEN-2020-015 | 04 - Southeast | 515531 | VANOSTP4 | 138 | 13.3403 | 13.3456 | 0.0053
GEN-2020-015 | 04 - Southeast | 515559 | SULPHR | 138 | 14.2541 | 14.2689 | 0.0148
GEN-2020-015 | 04 - Southeast | 515561 | CARTRCO4 | 138 | 7.5537 | 7.5597 | 0.006
GEN-2020-015 | 04 - Southeast | 515563 | ORIGINW4 | 138 | 3.4878 | 3.4891 | 0.0013
GEN-2020-015 | 04 - Southeast | 515873 | DRPSPRG4 | 138 | 10.9849 | 11.0021 | 0.0172
GEN-2020-015 | 04 - Southeast | 515932 | STIRLNG4 | 138 | 9.9674 | 9.9823 | 0.0149
GEN-2020-015 | 04 - Southeast | 515944 | STRRDTP4 | 138 | 8.2985 | 8.3071 | 0.0086
GEN-2020-015 | 04 - Southeast | 515977 | LKKONWA4 | 138 | 39.8626 | 39.8754 | 0.0128
GEN-2020-015 | 04 - Southeast | 516006 | DMNDSPG7 | 345 | 7.4703 | 7.539 | 0.0687
GEN-2020-015 | 04 - Southeast | 516096 | NORMHLL7 | 345 | 28.3858 | 28.39 | 0.0042
GEN-2020-015 | 04 - Southeast | 516097 | NORMHLL4 | 138 | 54.641 | 54.6462 | 0.0052
GEN-2020-015 | 04 - Southeast | 520411 | SAWYER4 | 138 | 10.5996 | 10.6016 | 0.002
GEN-2020-015 | 04 - Southeast | 520465 | REAGAN | 138 | 4.2108 | 4.2142 | 0.0034
GEN-2020-015 | 04 - Southeast | 520467 | ENOSJCT4 | 138 | 7.6424 | 7.6526 | 0.0102
GEN-2020-015 | 04 - Southeast | 520488 | LEBANON4 | 138 | 6.0203 | 6.0259 | 0.0056
GEN-2020-015 | 04 - Southeast | 520511 | ENVILLE4 | 138 | 6.4491 | 6.4551 | 0.006
GEN-2020-015 | 04 - Southeast | 520560 | HUGOITC4 | 138 | 22.9631 | 22.9729 | 0.0098
GEN-2020-015 | 04 - Southeast | 520901 | ENOS | 138 | 4.862 | 4.8661 | 0.0041
GEN-2020-015 | 04 - Southeast | 520918 | FROGVIL4 | 138 | 10.7209 | 10.7236 | 0.0027
GEN-2020-015 | 04 - Southeast | 520948 | HUGO | 138 | 23.1493 | 23.1589 | 0.0096
GEN-2020-015 | 04 - Southeast | 520963 | KIERSEY4 | 138 | 5.4844 | 5.4881 | 0.0037
GEN-2020-015 | 04 - Southeast | 520972 | LEBANTP4 | 138 | 6.8985 | 6.906 | 0.0075
GEN-2020-015 | 04 - Southeast | 520988 | MARIETA4 | 138 | 7.3344 | 7.341 | 0.0066
GEN-2020-015 | 04 - Southeast | 521044 | RUSSETT4 | 138 | 11.3469 | 11.3715 | 0.0246
GEN-2020-015 | 04 - Southeast | 521049 | SCLMNJC4 | 138 | 7.044 | 7.0498 | 0.0058
GEN-2020-015 | 04 - Southeast | 521066 | TEXOMA | 138 | 5.7539 | 5.7597 | 0.0058
GEN-2020-015 | 04 - Southeast | 521067 | TEXOMAJ4 | 138 | 9.0598 | 9.0741 | 0.0143
GEN-2020-015 | 04 - Southeast | 521079 | VALLANT4 | 138 | 8.6566 | 8.6578 | 0.0012
GEN-2020-015 | 04 - Southeast | 521122 | HOWE | 138 | 11.0599 | 11.0849 | 0.025
GEN-2020-015 | 04 - Southeast | 521125 | CHEEK_4 | 138 | 8.456 | 8.4663 | 0.0103
GEN-2020-015 | 04 - Southeast | 521157 | HUGO | 345 | 12.8662 | 12.8771 | 0.0109
GEN-2020-015 | 04 - Southeast | 555234 | NSUB345 | 345 | 28.4095 | 28.4136 | 0.0041
GEN-2020-015 | 04 - Southeast | 560088 | G16-063-TAP | 345 | 8.2606 | 8.2748 | 0.0142
GEN-2020-015 | 04 - Southeast | 563259 | GEN-2015-09 | 345 | 7.0682 | 7.0727 | 0.0045
GEN-2020-015 | 04 - Southeast | 587430 | GEN-2016-06 | 345 | 8.1493 | 8.163 | 0.0137
GEN-2020-015 | 04 - Southeast | 588180 | GEN-2016-12 | 138 | 12.9868 | 12.9987 | 0.0119
GEN-2020-015 | 04 - Southeast | 588670 | GEN-2017-02 | 138 | 19.0211 | 19.0276 | 0.0065
GEN-2020-015 | 04 - Southeast | 588710 | GEN-2017-02 | 138 | 7.5203 | 7.5262 | 0.0059
GEN-2020-015 | 04 - Southeast | 588810 | GEN-2017-04 | 345 | 19.7645 | 19.77 | 0.0055
GEN-2020-015 | 04 - Southeast | 588838 | G17-092-SWY | 345 | 20.2704 | 20.2763 | 0.0059
GEN-2020-015 | 04 - Southeast | 588839 | G17-092-TAP | 345 | 20.2704 | 20.2763 | 0.0059
GEN-2020-015 | 04 - Southeast | 589130 | GEN-2017-07 | 345 | 8.2487 | 8.2628 | 0.0141
GEN-2020-015 | 04 - Southeast | 589300 | GEN-2017-09 | 345 | 16.1462 | 16.1499 | 0.0037
GEN-2020-015 | 04 - Southeast | 760032 | GEN-2017-13 | 345 | 6.7843 | 6.7843 | 0
GEN-2020-015 | 04 - Southeast | 760830 | GEN-2017-14 | 345 | 4.2032 | 4.2196 | 0.0164
GEN-2020-015 | 04 - Southeast | 760851 | GEN-2017-15 | 345 | 3.8259 | 3.8391 | 0.0132
GEN-2020-015 | 04 - Southeast | 760938 | G17-171-TAP | 345 | 13.2503 | 13.2607 | 0.0104
GEN-2020-015 | 04 - Southeast | 760939 | GEN-2017-17 | 345 | 13.1616 | 13.1719 | 0.0103
GEN-2020-015 | 04 - Southeast | 761859 | GEN-2017-16 | 345 | 7.085 | 7.1064 | 0.0214
GEN-2020-015 | 04 - Southeast | 761880 | GEN-2017-16 | 345 | 5.295 | 5.3071 | 0.0121
GEN-2020-015 | 04 - Southeast | 762592 | GEN-2018-02 | 345 | 19.6027 | 19.6082 | 0.0055
GEN-2020-015 | 04 - Southeast | 762900 | GEN-2018-05 | 345 | 4.9448 | 4.9469 | 0.0021
GEN-2020-015 | 04 - Southeast | 763131 | GEN-2018-08 | 345 | 10.2436 | 10.2577 | 0.0141
GEN-2020-015 | 04 - Southeast | 763164 | GEN-2018-08 | 345 | 13.4714 | 13.4745 | 0.0031
GEN-2020-015 | 04 - Southeast | 764075 | GEN-2020-05 | 345 | 12.5327 | 12.5353 | 0.0026
GEN-2020-015 | 04 - Southeast | 764105 | GEN-2020-07 | 345 | 11.5262 | 11.566 | 0.0398
GEN-2020-015 | 04 - Southeast | 764115 | G20-074-TAP | 345 | 11.5321 | 11.572 | 0.0399
GEN-2020-015 | 04 - Southeast | 764270 | GEN-2020-01 | 345 | 11.09 | 11.2498 | 0.1598
GEN-2020-015 | 04 - Southeast | 764510 | GEN-2020-02 | 345 | 17.0546 | 17.0701 | 0.0155
GEN-2020-015 | 04 - Southeast | 764520 | G20-020-TAP | 345 | 17.096 | 17.1115 | 0.0155
GEN-2020-012 | 04 - Southeast | 511429 | L | 138 | 11.9212 | 11.9952 | 0.074
GEN-2020-012 | 04 - Southeast | 511432 | R-AMOCO2 | 69 | 3.6568 | 3.6746 | 0.0178
GEN-2020-012 | 04 - Southeast | 511435 | SNYDER-4 | 138 | 7.1708 | 7.5284 | 0.3576
GEN-2020-012 | 04 - Southeast | 511438 | DUKE---2 | 69 | 4.0606 | 4.0967 | 0.0361
GEN-2020-012 | 04 - Southeast | 511440 | ALTUSJT4 | 138 | 5.0152 | 5.192 | 0.1768
GEN-2020-012 | 04 - Southeast | 511441 | ALTUSJT2 | 69 | 5.5502 | 5.6517 | 0.1015
GEN-2020-012 | 04 - Southeast | 511444 | ROSVTAP2 | 69 | 3.8682 | 3.8881 | 0.0199
GEN-2020-012 | 04 - Southeast | 511460 | FREDJC-2 | 69 | 2.7495 | 2.7696 | 0.0201
GEN-2020-012 | 04 - Southeast | 511462 | HEADRIK2 | 69 | 4.4724 | 4.5347 | 0.0623
GEN-2020-012 | 04 - Southeast | 511465 | HOBART-2 | 69 | 5.4116 | 5.4352 | 0.0236
GEN-2020-012 | 04 - Southeast | 511472 | TIPTE | 69 | 3.6038 | 3.6395 | 0.0357
GEN-2020-012 | 04 - Southeast | 511475 | SNYDER-2 | 69 | 7.5121 | 7.6762 | 0.1641
GEN-2020-012 | 04 - Southeast | 511479 | TIPTCTY2 | 69 | 2.3046 | 2.3191 | 0.0145
GEN-2020-012 | 04 - Southeast | 511488 | 112GORE4 | 138 | 13.2129 | 13.2972 | 0.0843
GEN-2020-012 | 04 - Southeast | 511495 | TOMSTEED2 | 69 | 4.1099 | 4.1448 | 0.0349
GEN-2020-012 | 04 - Southeast | 511500 | CACHE4 | 138 | 8.5644 | 8.67 | 0.1056
GEN-2020-012 | 04 - Southeast | 511510 | LAIRGST4 | 138 | 12.7789 | 12.8638 | 0.0849
GEN-2020-012 | 04 - Southeast | 511520 | DAV | 69 | 2.1943 | 2.206 | 0.0117
GEN-2020-012 | 04 - Southeast | 511543 | TIPTN | 69 | 4.4706 | 4.5329 | 0.0623
GEN-2020-012 | 04 - Southeast | 511545 | TIPTON | 69 | 2.4592 | 2.4757 | 0.0165
GEN-2020-012 | 04 - Southeast | 511564 | MARTHA | 138 | 4.3108 | 4.39 | 0.0792
GEN-2020-012 | 04 - Southeast | 512100 | CHLDR2WT | 69 | 2.2517 | 2.2577 | 0.006
GEN-2020-012 | 04 - Southeast | 512101 | CHILD4WT | 138 | 1.6684 | 1.6761 | 0.0077
GEN-2020-012 | 04 - Southeast | 512103 | HOLTP4WT | 138 | 1.4969 | 1.5022 | 0.0053
GEN-2020-012 | 04 - Southeast | 512110 | LAKEP4WT | 138 | 2.156 | 2.1754 | 0.0194
GEN-2020-012 | 04 - Southeast | 512111 | LAKEP2WT | 69 | 3.0657 | 3.0853 | 0.0196
GEN-2020-012 | 04 - Southeast | 512113 | VRNMTAP2 | 69 | 2.4015 | 2.4146 | 0.0131
GEN-2020-012 | 04 - Southeast | 520404 | MDCPRK4 | 138 | 5.3767 | 5.407 | 0.0303
GEN-2020-012 | 04 - Southeast | 520410 | CACHE4 | 138 | 5.1199 | 5.1826 | 0.0627
GEN-2020-012 | 04 - Southeast | 520499 | WHTECTY2 | 69 | 1.8527 | 1.8605 | 0.0078
GEN-2020-012 | 04 - Southeast | 520528 | ROSEVLT2 | 69 | 3.7722 | 3.8016 | 0.0294
GEN-2020-012 | 04 - Southeast | 520534 | DUKE | 69 | 5.27 | 5.3301 | 0.0601
GEN-2020-012 | 04 - Southeast | 520541 | SNYDRSB2 | 69 | 7.0297 | 7.1537 | 0.124
GEN-2020-012 | 04 - Southeast | 520803 | ALTUS_ | 69 | 3.5851 | 3.6151 | 0.03
GEN-2020-012 | 04 - Southeast | 520805 | ALTUSSW2 | 69 | 3.5797 | 3.6098 | 0.0301
GEN-2020-012 | 04 - Southeast | 520896 | ELDORDO2 | 69 | 2.0841 | 2.0933 | 0.0092
GEN-2020-012 | 04 - Southeast | 520914 | FREDRIK2 | 69 | 3.457 | 3.4792 | 0.0222
GEN-2020-012 | 04 - Southeast | 520927 | GRANITE2 | 69 | 3.2027 | 3.2098 | 0.0071
GEN-2020-012 | 04 - Southeast | 520929 | GYPSUM | 69 | 3.6232 | 3.6519 | 0.0287
GEN-2020-012 | 04 - Southeast | 520980 | LOCKETT2 | 69 | 1.8935 | 1.9012 | 0.0077
GEN-2020-012 | 04 - Southeast | 521009 | NAVJOTP2 | 69 | 3.6276 | 3.6589 | 0.0313
GEN-2020-012 | 04 - Southeast | 521042 | RUSSELL2 | 69 | 5.27 | 5.3301 | 0.0601
GEN-2020-012 | 04 - Southeast | 521043 | RUSSELL4 | 138 | 3.8492 | 3.9365 | 0.0873
GEN-2020-012 | 04 - Southeast | 521051 | SNYDER | 69 | 7.0297 | 7.1537 | 0.124
GEN-2020-012 | 04 - Southeast | 521052 | SNYDER | 138 | 6.8134 | 7.0786 | 0.2652
GEN-2020-012 | 04 - Southeast | 521069 | TIPTON-2 | 69 | 2.0749 | 2.0841 | 0.0092
GEN-2020-012 | 04 - Southeast | 521070 | TIPTONJ2 | 69 | 3.9591 | 3.9928 | 0.0337
GEN-2020-012 | 04 - Southeast | 521081 | VERNON | 69 | 2.4031 | 2.4162 | 0.0131
GEN-2020-012 | 04 - Southeast | 521190 | CACHEJ4 | 138 | 5.6023 | 5.6779 | 0.0756
GEN-2020-012 | 04 - Southeast | 529298 | OMPVET-4 | 138 | 4.5826 | 4.7059 | 0.1233
GEN-2020-012 | 04 - Southeast | 529302 | OMALTUS4 | 138 | 4.4678 | 4.5758 | 0.108
GEN-2020-012 | 04 - Southeast | 529342 | OMMANGM2 | 69 | 3.1404 | 3.1497 | 0.0093
GEN-2020-012 | 04 - Southeast | 529345 | OMPARK-4 | 138 | 4.7972 | 4.9471 | 0.1499
GEN-2020-012 | 04 - Southeast | 562683 | GEN-2015-01 | 138 | 6.7967 | 7.0606 | 0.2639
GEN-2020-012 | 04 - Southeast | 588779 | G17-036_TAP | 138 | 7.1177 | 7.4602 | 0.3425
GEN-2020-012 | 04 - Southeast | 588780 | GEN-2017-03 | 138 | 6.8659 | 7.1842 | 0.3183
GEN-2020-012 | 04 - Southeast | 764495 | GEN-2020-01 | 138 | 5.4875 | 5.5715 | 0.084
GEN-2020-012 | 04 - Southeast | 764505 | G20-016-TAP | 138 | 5.7684 | 5.8632 | 0.0948
GEN-2020-012 | 04 - Southeast | 765220 | GEN-2020-01 | 138 | 5.6703 | 6.1033 | 0.433
GEN-2020-012 | 04 - Southeast | 765230 | G20-012-TAP | 138 | 5.7135 | 6.1463 | 0.4328
GEN-2020-012 | 04 - Southeast | 765231 | G20-012-SS1 | 138 | 5.6703 | 6.1033 | 0.433
GEN-2020-012 | 04 - Southeast | 765232 | G20-012-SS2 | 138 | 5.3903 | 5.8019 | 0.4116
GEN-2020-010 | 04 - Southeast | 514777 | CLEOCOR2 | 69 | 8.1654 | 8.1687 | 0.0033
GEN-2020-010 | 04 - Southeast | 514778 | CLEOCOR4 | 138 | 6.331 | 6.3341 | 0.0031
GEN-2020-010 | 04 - Southeast | 514782 | WODWRD | 69 | 10.8955 | 10.9202 | 0.0247
GEN-2020-010 | 04 - Southeast | 514785 | WOODWRD4 | 138 | 13.0653 | 13.1117 | 0.0464
GEN-2020-010 | 04 - Southeast | 514787 | DEWEY | 138 | 7.36 | 7.71 | 0.35
GEN-2020-010 | 04 - Southeast | 514788 | GLASMTN4 | 138 | 5.1114 | 5.1171 | 0.0057
GEN-2020-010 | 04 - Southeast | 514794 | KNOBHIL2 | 69 | 8.8549 | 8.8565 | 0.0016
GEN-2020-010 | 04 - Southeast | 514795 | KNOBHIL4 | 138 | 10.2206 | 10.2241 | 0.0035
GEN-2020-010 | 04 - Southeast | 514796 | IODINE-4 | 138 | 7.2989 | 7.3941 | 0.0952
GEN-2020-010 | 04 - Southeast | 514822 | SOUTHRD4 | 138 | 4.5668 | 4.6149 | 0.0481
GEN-2020-010 | 04 - Southeast | 514823 | ROMNOSE4 | 138 | 5.9083 | 5.9333 | 0.025
GEN-2020-010 | 04 - Southeast | 515363 | CENT | 138 | 3.0853 | 3.0871 | 0.0018
GEN-2020-010 | 04 - Southeast | 515375 | WWRDEHV7 | 345 | 21.2088 | 21.2419 | 0.0331
GEN-2020-010 | 04 - Southeast | 515376 | WWRDEHV4 | 138 | 24.4698 | 24.5659 | 0.0961
GEN-2020-010 | 04 - Southeast | 515390 | TLGAWND4 | 138 | 3.5906 | 3.6574 | 0.0668
GEN-2020-010 | 04 - Southeast | 515425 | WWDPST | 138 | 17.625 | 17.6838 | 0.0588
GEN-2020-010 | 04 - Southeast | 515533 | REDCLFT4 | 138 | 6.6046 | 6.733 | 0.1284
GEN-2020-010 | 04 - Southeast | 515562 | CLEOPLT4 | 138 | 6.3282 | 6.3312 | 0.003
GEN-2020-010 | 04 - Southeast | 515785 | WINDFRM4 | 138 | 19.6108 | 19.7706 | 0.1598
GEN-2020-010 | 04 - Southeast | 515786 | FPLWIND4 | 138 | 6.1897 | 6.2039 | 0.0142
GEN-2020-010 | 04 - Southeast | 515852 | DGRASSE7 | 345 | 14.587 | 14.5974 | 0.0104
GEN-2020-010 | 04 - Southeast | 515853 | DGRASSE4 | 138 | 16.8743 | 16.8839 | 0.0096
GEN-2020-010 | 04 - Southeast | 515863 | REDCLF | 138 | 6.5906 | 6.7183 | 0.1277
GEN-2020-010 | 04 - Southeast | 515964 | CANTNLK4 | 138 | 4.7305 | 4.8078 | 0.0773
GEN-2020-010 | 04 - Southeast | 516025 | SUNDANC4 | 138 | 4.482 | 4.4833 | 0.0013
GEN-2020-010 | 04 - Southeast | 520425 | PIC4 | 138 | 7.9875 | 8.0103 | 0.0228
GEN-2020-010 | 04 - Southeast | 520430 | NOELSW | 138 | 10.2896 | 10.2931 | 0.0035
GEN-2020-010 | 04 - Southeast | 520436 | ROSEVLY4 | 138 | 12.2553 | 12.2603 | 0.005
GEN-2020-010 | 04 - Southeast | 520454 | STALOGA2 | 69 | 4.4188 | 4.4638 | 0.045
GEN-2020-010 | 04 - Southeast | 520462 | ASPEN | 138 | 19.3734 | 19.5298 | 0.1564
GEN-2020-010 | 04 - Southeast | 520480 | CURTIS | 69 | 3.9237 | 3.9272 | 0.0035
GEN-2020-010 | 04 - Southeast | 520500 | BEARCAT4 | 138 | 14.2736 | 14.3543 | 0.0807
GEN-2020-010 | 04 - Southeast | 520507 | CEDRDAL4 | 138 | 4.5921 | 4.5985 | 0.0064
GEN-2020-010 | 04 - Southeast | 520553 | SEILING4 | 138 | 6.6066 | 7.0454 | 0.4388
GEN-2020-010 | 04 - Southeast | 520601 | AVARD | 138 | 6.8255 | 6.827 | 0.0015
GEN-2020-010 | 04 - Southeast | 520843 | CANTON-2 | 69 | 4.701 | 4.7358 | 0.0348
GEN-2020-010 | 04 - Southeast | 520848 | CDRDLTP4 | 138 | 5.7144 | 5.7243 | 0.0099
GEN-2020-010 | 04 - Southeast | 520909 | FAIRVEW2 | 69 | 4.518 | 4.5207 | 0.0027
GEN-2020-010 | 04 - Southeast | 520919 | FTSUPLY2 | 69 | 7.5232 | 7.5322 | 0.009
GEN-2020-010 | 04 - Southeast | 520920 | FTSUPLY4 | 138 | 5.3198 | 5.3285 | 0.0087
GEN-2020-010 | 04 - Southeast | 520922 | SLEEPBR4 | 138 | 4.2038 | 4.2085 | 0.0047
GEN-2020-010 | 04 - Southeast | 520942 | HM-BTTP2 | 69 | 2.3038 | 2.3107 | 0.0069
GEN-2020-010 | 04 - Southeast | 520957 | IODINE | 138 | 7.7335 | 7.7553 | 0.0218
GEN-2020-010 | 04 - Southeast | 520995 | MOORLND2 | 69 | 8.5323 | 8.5493 | 0.017
GEN-2020-010 | 04 - Southeast | 520999 | MOORLND4 | 138 | 20.0803 | 20.2491 | 0.1688
GEN-2020-010 | 04 - Southeast | 521015 | OKEENE | 69 | 6.3876 | 6.3996 | 0.012
GEN-2020-010 | 04 - Southeast | 521016 | OKEENE | 138 | 7.0683 | 7.076 | 0.0077
GEN-2020-010 | 04 - Southeast | 521033 | PUTNAM | 69 | 2.6239 | 2.6351 | 0.0112
GEN-2020-010 | 04 - Southeast | 521064 | TALOGA | 69 | 8.1225 | 8.2948 | 0.1723
GEN-2020-010 | 04 - Southeast | 521065 | TALOGA | 138 | 7.1647 | 7.6363 | 0.4716
GEN-2020-010 | 04 - Southeast | 521082 | VICI | 69 | 3.8312 | 3.8512 | 0.02
GEN-2020-010 | 04 - Southeast | 521096 | WOODWRD2 | 69 | 9.8684 | 9.8947 | 0.0263
GEN-2020-010 | 04 - Southeast | 521128 | NINMLTP4 | 138 | 4.7199 | 4.7233 | 0.0034
GEN-2020-010 | 04 - Southeast | 521196 | FARGOJCT2 | 69 | 7.5451 | 7.5594 | 0.0143
GEN-2020-010 | 04 - Southeast | 521197 | CRTSJCT2 | 69 | 8.1398 | 8.1555 | 0.0157
GEN-2020-010 | 04 - Southeast | 539801 | THISTLE7 | 345 | 14.9359 | 14.9399 | 0.004
GEN-2020-010 | 04 - Southeast | 585300 | GEN-2015-09 | 138 | 16.6744 | 16.6838 | 0.0094
GEN-2020-010 | 04 - Southeast | 587140 | GEN-2016-02 | 138 | 7.4235 | 7.444 | 0.0205
GEN-2020-010 | 04 - Southeast | 763769 | GEN-2019-04 | 138 | 16.8743 | 16.8839 | 0.0096
GEN-2020-010 | 04 - Southeast | 765205 | GEN-2020-01 | 138 | 6.7697 | 7.3373 | 0.5676
GEN-2020-010 | 04 - Southeast | 765212 | G20-010-SS1 | 138 | 6.7543 | 7.322 | 0.5677
GEN-2020-010 | 04 - Southeast | 765213 | G20-010-SS2 | 138 | 6.5742 | 7.127 | 0.5528
GEN-2020-010 | 04 - Southeast | 765215 | G20-010-TAP | 138 | 6.7875 | 7.355 | 0.5675
GEN-2020-068 | 05 - Southwest | 511456 | O.K.U.-7 | 345 | 7.4343 | 7.442 | 0.0077
GEN-2020-068 | 05 - Southwest | 511467 | L.E.S.-4 | 138 | 25.6447 | 25.6514 | 0.0067
GEN-2020-068 | 05 - Southwest | 511468 | L.E.S.-7 | 345 | 15.4013 | 15.4119 | 0.0106
GEN-2020-068 | 05 - Southwest | 511553 | CHISHOLM7 | 345 | 12.738 | 12.7423 | 0.0043
GEN-2020-068 | 05 - Southwest | 511565 | OKLAUN | 345 | 7.4043 | 7.4119 | 0.0076
GEN-2020-068 | 05 - Southwest | 515375 | WWRDEHV7 | 345 | 19.3927 | 19.3939 | 0.0012
GEN-2020-068 | 05 - Southwest | 515458 | BORDER | 345 | 8.3864 | 8.3898 | 0.0034
GEN-2020-068 | 05 - Southwest | 516059 | BECKHAM7 | 345 | 12.6369 | 12.6411 | 0.0042
GEN-2020-068 | 05 - Southwest | 523959 | POTTER_CO | 230 | 23.0812 | 23.0856 | 0.0044
GEN-2020-068 | 05 - Southwest | 523961 | POTTER_CO | 345 | 13.9493 | 13.9531 | 0.0038
GEN-2020-068 | 05 - Southwest | 524044 | NICHOLS | 230 | 26.4052 | 26.409 | 0.0038
GEN-2020-068 | 05 - Southwest | 524365 | RANDALL | 230 | 14.6287 | 14.6304 | 0.0017
GEN-2020-068 | 05 - Southwest | 524414 | AMA_SOUTH | 115 | 16.851 | 16.8521 | 0.0011
GEN-2020-068 | 05 - Southwest | 524415 | AMA_SOUTH | 230 | 13.687 | 13.6888 | 0.0018
GEN-2020-068 | 05 - Southwest | 524770 | PLSNT_HILL | 230 | 6.7955 | 6.7966 | 0.0011
GEN-2020-068 | 05 - Southwest | 524875 | OASIS | 230 | 8.5024 | 8.5041 | 0.0017
GEN-2020-068 | 05 - Southwest | 524908 | ROOSEVELT | 115 | 11.4754 | 11.4769 | 0.0015
GEN-2020-068 | 05 - Southwest | 524909 | ROOSEVELT | 230 | 10.2301 | 10.2326 | 0.0025
GEN-2020-068 | 05 - Southwest | 525192 | KRESS_INT | 115 | 11.946 | 11.9501 | 0.0041
GEN-2020-068 | 05 - Southwest | 525212 | SWISHER | 115 | 11.5222 | 11.5262 | 0.004
GEN-2020-068 | 05 - Southwest | 525213 | SWISHER | 230 | 10.4324 | 10.4397 | 0.0073
GEN-2020-068 | 05 - Southwest | 525326 | COX | 115 | 6.2865 | 6.2881 | 0.0016
GEN-2020-068 | 05 - Southwest | 525414 | LAMTON | 115 | 7.6225 | 7.6239 | 0.0014
GEN-2020-068 | 05 - Southwest | 525453 | HALE_CNTY | 69 | 6.9144 | 6.9155 | 0.0011
GEN-2020-068 | 05 - Southwest | 525454 | HALE_CNTY | 115 | 10.1893 | 10.1932 | 0.0039
GEN-2020-068 | 05 - Southwest | 525460 | NEWHART | 115 | 14.9595 | 14.9641 | 0.0046
GEN-2020-068 | 05 - Southwest | 525461 | NEWHART | 230 | 11.0127 | 11.0177 | 0.005
GEN-2020-068 | 05 - Southwest | 525480 | PLANT_X | 115 | 19.3136 | 19.3204 | 0.0068
GEN-2020-068 | 05 - Southwest | 525481 | PLANT_X | 230 | 24.0193 | 24.0384 | 0.0191
GEN-2020-068 | 05 - Southwest | 525531 | TOLK | 230 | 32.1444 | 32.177 | 0.0326
GEN-2020-068 | 05 - Southwest | 525549 | TOLK | 345 | 16.4508 | 16.4645 | 0.0137
GEN-2020-068 | 05 - Southwest | 525584 | BLUECLDCOL | 230 | 10.5074 | 10.5131 | 0.0057
GEN-2020-068 | 05 - Southwest | 525585 | BLUECLDPOI | 230 | 11.1111 | 11.1174 | 0.0063
GEN-2020-068 | 05 - Southwest | 525586 | NEEDMORE | 230 | 11.1111 | 11.1174 | 0.0063
GEN-2020-068 | 05 - Southwest | 525636 | LAMB_CNTY | 115 | 8.5301 | 8.5317 | 0.0016
GEN-2020-068 | 05 - Southwest | 525637 | LAMB_CNTY | 230 | 5.5681 | 5.5692 | 0.0011
GEN-2020-068 | 05 - Southwest | 525731 | SP-ABERNTHY | 69 | 3.0133 | 3.0138 | 0.0005
GEN-2020-068 | 05 - Southwest | 525738 | HALECENTER | 69 | 2.4592 | 2.4595 | 0.0003
GEN-2020-068 | 05 - Southwest | 525763 | CALLAHAN | 115 | 5.5807 | 5.5822 | 0.0015
GEN-2020-068 | 05 - Southwest | 525779 | FLOYD_CNTY | 69 | 5.4099 | 5.4108 | 0.0009
GEN-2020-068 | 05 - Southwest | 525780 | FLOYD_CNTY | 115 | 6.2708 | 6.2729 | 0.0021
GEN-2020-068 | 05 - Southwest | 525803 | BLANCO | 115 | 5.0579 | 5.059 | 0.0011
GEN-2020-068 | 05 - Southwest | 525816 | TUCO_INT2 | 69 | 4.6621 | 4.6632 | 0.0011
GEN-2020-068 | 05 - Southwest | 525826 | TUCO_INT | 69 | 7.8813 | 7.8845 | 0.0032
GEN-2020-068 | 05 - Southwest | 525828 | TUCO_INT | 115 | 19.6455 | 19.6784 | 0.0329
GEN-2020-068 | 05 - Southwest | 525830 | TUCO_INT | 230 | 23.0346 | 23.1605 | 0.1259
GEN-2020-068 | 05 - Southwest | 525832 | TUCO_INT | 345 | 15.5296 | 15.7032 | 0.1736
GEN-2020-068 | 05 - Southwest | 525840 | ANTELOPE_1 | 230 | 22.8271 | 22.9505 | 0.1234
GEN-2020-068 | 05 - Southwest | 525850 | ELK_CT1 | 345 | 15.3626 | 15.5321 | 0.1695
GEN-2020-068 | 05 - Southwest | 525853 | LH-WIL&ELN+ | 69 | 2.5431 | 2.5434 | 0.0003
GEN-2020-068 | 05 - Southwest | 525885 | SP-NEWDEAL | 69 | 3.3121 | 3.3127 | 0.0006
GEN-2020-068 | 05 - Southwest | 525926 | CROSBY | 115 | 4.7256 | 4.7267 | 0.0011
GEN-2020-068 | 05 - Southwest | 525957 | HALE_WNDCL1 | 230 | 10.7272 | 10.7515 | 0.0243
GEN-2020-068 | 05 - Southwest | 526076 | STANTON_W | 115 | 8.9493 | 8.9548 | 0.0055
GEN-2020-068 | 05 - Southwest | 526109 | SP-ERSKINE | 115 | 11.0047 | 11.0127 | 0.008
GEN-2020-068 | 05 - Southwest | 526146 | INDIANA | 115 | 9.3289 | 9.3348 | 0.0059
GEN-2020-068 | 05 - Southwest | 526159 | CARLISLE | 69 | 2.5575 | 2.5578 | 0.0003
GEN-2020-068 | 05 - Southwest | 526160 | CARLISLE | 115 | 12.7997 | 12.8103 | 0.0106
GEN-2020-068 | 05 - Southwest | 526161 | CARLISLE | 230 | 10.4264 | 10.4424 | 0.016
GEN-2020-068 | 05 - Southwest | 526162 | LP-DOUD_TP | 115 | 11.3424 | 11.3506 | 0.0082
GEN-2020-068 | 05 - Southwest | 526192 | MURPHY | 115 | 10.2738 | 10.2801 | 0.0063
GEN-2020-068 | 05 - Southwest | 526268 | LUBBCK_STH | 115 | 17.8116 | 17.8257 | 0.0141
GEN-2020-068 | 05 - Southwest | 526269 | LUBBCK_STH | 230 | 15.2453 | 15.2638 | 0.0185
GEN-2020-068 | 05 - Southwest | 526297 | LUBBCK_EST | 69 | 7.9266 | 7.9284 | 0.0018
GEN-2020-068 | 05 - Southwest | 526298 | LUBBCK_EST | 115 | 14.5891 | 14.5991 | 0.01
GEN-2020-068 | 05 - Southwest | 526299 | LUBBCK_EST | 230 | 11.477 | 11.4866 | 0.0096
GEN-2020-068 | 05 - Southwest | 526337 | JONES | 230 | 16.9632 | 16.984 | 0.0208
GEN-2020-068 | 05 - Southwest | 526434 | SUNDOWN | 115 | 10.8025 | 10.8088 | 0.0063
GEN-2020-068 | 05 - Southwest | 526435 | SUNDOWN | 230 | 11.0307 | 11.0455 | 0.0148
GEN-2020-068 | 05 - Southwest | 526460 | AMOCO_SS | 230 | 9.7629 | 9.7761 | 0.0132
GEN-2020-068 | 05 - Southwest | 526524 | WOLFFORTH | 115 | 11.2879 | 11.2957 | 0.0078
GEN-2020-068 | 05 - Southwest | 526525 | WOLFFORTH | 230 | 12.6421 | 12.6605 | 0.0184
GEN-2020-068 | 05 - Southwest | 526676 | GRASSLAND | 115 | 6.8916 | 6.8934 | 0.0018
GEN-2020-068 | 05 - Southwest | 526677 | GRASSLAND | 230 | 6.0179 | 6.0206 | 0.0027
GEN-2020-068 | 05 - Southwest | 526679 | CIRRUS_WND | 230 | 4.7065 | 4.7081 | 0.0016
GEN-2020-068 | 05 - Southwest | 526736 | TERRY_CNTY | 115 | 10.7215 | 10.7284 | 0.0069
GEN-2020-068 | 05 - Southwest | 526784 | AMOCOWASSON | 230 | 15.9438 | 15.9881 | 0.0443
GEN-2020-068 | 05 - Southwest | 526792 | PRENTICE | 115 | 6.0487 | 6.0516 | 0.0029
GEN-2020-068 | 05 - Southwest | 526928 | PLAINS_INT | 115 | 10.0807 | 10.0903 | 0.0096
GEN-2020-068 | 05 - Southwest | 526934 | YOAKUM | 115 | 19.4948 | 19.5335 | 0.0387
GEN-2020-068 | 05 - Southwest | 526935 | YOAKUM | 230 | 20.4888 | 20.6089 | 0.1201
GEN-2020-068 | 05 - Southwest | 526936 | YOAKUM_345 | 345 | 11.3241 | 11.5801 | 0.256
GEN-2020-068 | 05 - Southwest | 526944 | LG-PLAINS | 115 | 7.9351 | 7.9407 | 0.0056
GEN-2020-068 | 05 - Southwest | 527000 | GAINES_PLNT | 345 | 12.5257 | 12.548 | 0.0223
GEN-2020-068 | 05 - Southwest | 527009 | BRU_SUB | 230 | 16.0529 | 16.1115 | 0.0586
GEN-2020-068 | 05 - Southwest | 527010 | OXYBRU | 230 | 15.8992 | 15.9566 | 0.0574
GEN-2020-068 | 05 - Southwest | 527011 | XTO_MAHONEY | 230 | 15.7144 | 15.7661 | 0.0517
GEN-2020-068 | 05 - Southwest | 527018 | BENNETT | 115 | 13.8641 | 13.8773 | 0.0132
GEN-2020-068 | 05 - Southwest | 527020 | SIDEWINDER | 345 | 13.0799 | 13.1087 | 0.0288
GEN-2020-068 | 05 - Southwest | 527027 | INK_BASIN | 115 | 13.0688 | 13.0796 | 0.0108
GEN-2020-068 | 05 - Southwest | 527028 | INK_BASIN | 230 | 11.4827 | 11.5066 | 0.0239
GEN-2020-068 | 05 - Southwest | 527030 | ALRDCRTZ_TP | 115 | 12.2112 | 12.2202 | 0.009
GEN-2020-068 | 05 - Southwest | 527041 | ARCO_TP | 115 | 13.7686 | 13.7818 | 0.0132
GEN-2020-068 | 05 - Southwest | 527047 | OXY_WILRD1 | 115 | 10.9492 | 10.9574 | 0.0082
GEN-2020-068 | 05 - Southwest | 527062 | SHELL_CO2 | 115 | 16.8122 | 16.8291 | 0.0169
GEN-2020-068 | 05 - Southwest | 527130 | DENVER_N | 115 | 22.6957 | 22.723 | 0.0273
GEN-2020-068 | 05 - Southwest | 527136 | DENVER_S | 115 | 22.6957 | 22.723 | 0.0273
GEN-2020-068 | 05 - Southwest | 527146 | MUSTANG | 115 | 24.2585 | 24.2882 | 0.0297
GEN-2020-068 | 05 - Southwest | 527149 | MUSTANG | 230 | 18.2714 | 18.3209 | 0.0495
GEN-2020-068 | 05 - Southwest | 527151 | GS-MUSTANG | 230 | 18.2714 | 18.3209 | 0.0495
GEN-2020-068 | 05 - Southwest | 527194 | LG-PLSHILL | 115 | 8.0035 | 8.0078 | 0.0043
GEN-2020-068 | 05 - Southwest | 527202 | SEAGRAVES | 115 | 9.2137 | 9.2189 | 0.0052
GEN-2020-068 | 05 - Southwest | 527275 | SEMINOLE | 115 | 14.7627 | 14.7752 | 0.0125
GEN-2020-068 | 05 - Southwest | 527276 | SEMINOLE | 230 | 8.2647 | 8.2736 | 0.0089
GEN-2020-068 | 05 - Southwest | 527610 | SAGA_SCOL | 345 | 11.0684 | 11.0808 | 0.0124
GEN-2020-068 | 05 - Southwest | 527655 | RSVLT_CC_E | 345 | 10.831 | 10.8431 | 0.0121
GEN-2020-068 | 05 - Southwest | 527656 | CROSSROADS | 345 | 12.6846 | 12.7018 | 0.0172
GEN-2020-068 | 05 - Southwest | 527802 | EDDY_CNTY | 345 | 8.0156 | 8.026 | 0.0104
GEN-2020-068 | 05 - Southwest | 527867 | CUNNIGHM_S | 230 | 18.6008 | 18.6259 | 0.0251
GEN-2020-068 | 05 - Southwest | 527891 | HOBBS_INT | 115 | 33.1725 | 33.199 | 0.0265
GEN-2020-068 | 05 - Southwest | 527894 | HOBBS_INT | 230 | 20.8665 | 20.9035 | 0.037
GEN-2020-068 | 05 - Southwest | 527896 | HOBBS_INT | 345 | 16.5299 | 16.6041 | 0.0742
GEN-2020-068 | 05 - Southwest | 527965 | KIOWA | 345 | 10.2268 | 10.2483 | 0.0215
GEN-2020-068 | 05 - Southwest | 527966 | KIOWA | 115 | 18.3993 | 18.4184 | 0.0191
GEN-2020-068 | 05 - Southwest | 528015 | PHANTOM | 345 | 6.2507 | 6.259 | 0.0083
GEN-2020-068 | 05 - Southwest | 528025 | RDRUNNER | 115 | 14.8527 | 14.8681 | 0.0154
GEN-2020-068 | 05 - Southwest | 528027 | RDRUNNER | 345 | 10.3402 | 10.3653 | 0.0251
GEN-2020-068 | 05 - Southwest | 528185 | N_LOVING | 345 | 7.2958 | 7.3067 | 0.0109
GEN-2020-068 | 05 - Southwest | 528325 | LE-WAITS | 115 | 8.9378 | 8.942 | 0.0042
GEN-2020-068 | 05 - Southwest | 528604 | ANDREWS | 345 | 9.107 | 9.1206 | 0.0136
GEN-2020-068 | 05 - Southwest | 528626 | LE-PLNSINT | 69 | 3.6424 | 3.6431 | 0.0007
GEN-2020-068 | 05 - Southwest | 560022 | CRAWFISH_DR | 345 | 15.3098 | 15.4742 | 0.1644
GEN-2020-068 | 05 - Southwest | 588460 | A16-008SUB | 115 | 13.0688 | 13.0796 | 0.0108
GEN-2020-068 | 05 - Southwest | 588760 | GEN-2017-03 | 345 | 4.9306 | 4.9338 | 0.0032
GEN-2020-068 | 05 - Southwest | 599955 | PNM-DC6 | 230 | 10.2301 | 10.2326 | 0.0025
GEN-2020-068 | 05 - Southwest | 760498 | G17-146-TAP | 230 | 7.7314 | 7.7326 | 0.0012
GEN-2020-068 | 05 - Southwest | 760938 | G17-171-TAP | 345 | 11.3063 | 11.3107 | 0.0044
GEN-2020-068 | 05 - Southwest | 761355 | GEN-2017-23 | 230 | 14.0824 | 14.1234 | 0.041
GEN-2020-068 | 05 - Southwest | 762132 | GEN-2017-15 | 230 | 13.9728 | 13.9781 | 0.0053
GEN-2020-068 | 05 - Southwest | 762216 | G17-151TAP | 345 | 8.8908 | 8.9343 | 0.0435
GEN-2020-068 | 05 - Southwest | 762217 | GEN-2017-15 | 345 | 6.3627 | 6.3839 | 0.0212
GEN-2020-068 | 05 - Southwest | 762460 | GEN-2018-01 | 345 | 9.3805 | 9.4054 | 0.0249
GEN-2020-068 | 05 - Southwest | 762467 | G18-015-TAP | 345 | 9.4147 | 9.4398 | 0.0251
GEN-2020-068 | 05 - Southwest | 763186 | GEN-2018-08 | 230 | 10.7028 | 10.7075 | 0.0047
GEN-2020-068 | 05 - Southwest | 763215 | G18-092-PRO | 345 | 9.3495 | 9.3698 | 0.0203
GEN-2020-068 | 05 - Southwest | 763318 | GEN-2018-11 | 345 | 15.0556 | 15.0657 | 0.0101
GEN-2020-068 | 05 - Southwest | 763483 | GEN-2019-00 | 230 | 9.1544 | 9.1563 | 0.0019
GEN-2020-068 | 05 - Southwest | 763516 | GEN-2019-01 | 345 | 10.4915 | 10.7109 | 0.2194
GEN-2020-068 | 05 - Southwest | 764550 | G20-075-TAP | 345 | 14.3897 | 14.3962 | 0.0065
GEN-2020-068 | 05 - Southwest | 764825 | GEN-2020-01 | 230 | 5.5498 | 5.5509 | 0.0011
GEN-2020-068 | 05 - Southwest | 764840 | GEN-2020-05 | 345 | 11.3215 | 11.4535 | 0.132
GEN-2020-068 | 05 - Southwest | 764866 | G20-059-TAP | 345 | 11.3989 | 11.5328 | 0.1339
GEN-2020-068 | 05 - Southwest | 764875 | GEN-2020-06 | 230 | 11.302 | 11.3113 | 0.0093
GEN-2020-068 | 05 - Southwest | 764935 | GEN-2020-06 | 345 | 6.602 | 7.0161 | 0.4141
GEN-2020-068 | 05 - Southwest | 764945 | G20-067-TAP | 345 | 7.9828 | 8.6182 | 0.6354
GEN-2020-068 | 05 - Southwest | 764948 | G20-068-SS1 | 345 | 6.3818 | 6.9074 | 0.5256
GEN-2020-068 | 05 - Southwest | 764949 | G20-068-SS2 | 345 | 6.3818 | 6.9054 | 0.5236
GEN-2020-068 | 05 - Southwest | 764950 | GEN-2020-06 | 345 | 7.9402 | 8.5759 | 0.6357
GEN-2020-068 | 05 - Southwest | 766291 | G20-009-TAP | 345 | 9.4665 | 9.4725 | 0.006
GEN-2020-067 | 05 - Southwest | 511456 | O.K.U.-7 | 345 | 7.4356 | 7.442 | 0.0064
GEN-2020-067 | 05 - Southwest | 511467 | L.E.S.-4 | 138 | 25.6459 | 25.6514 | 0.0055
GEN-2020-067 | 05 - Southwest | 511468 | L.E.S.-7 | 345 | 15.4031 | 15.4119 | 0.0088
GEN-2020-067 | 05 - Southwest | 511553 | CHISHOLM7 | 345 | 12.7388 | 12.7423 | 0.0035
GEN-2020-067 | 05 - Southwest | 511565 | OKLAUN | 345 | 7.4056 | 7.4119 | 0.0063
GEN-2020-067 | 05 - Southwest | 515375 | WWRDEHV7 | 345 | 19.3929 | 19.3939 | 0.001
GEN-2020-067 | 05 - Southwest | 515458 | BORDER | 345 | 8.3869 | 8.3898 | 0.0029
GEN-2020-067 | 05 - Southwest | 516059 | BECKHAM7 | 345 | 12.6376 | 12.6411 | 0.0035
GEN-2020-067 | 05 - Southwest | 523959 | POTTER_CO | 230 | 23.0819 | 23.0856 | 0.0037
GEN-2020-067 | 05 - Southwest | 523961 | POTTER_CO | 345 | 13.9499 | 13.9531 | 0.0032
GEN-2020-067 | 05 - Southwest | 524044 | NICHOLS | 230 | 26.4059 | 26.409 | 0.0031
GEN-2020-067 | 05 - Southwest | 524365 | RANDALL | 230 | 14.629 | 14.6304 | 0.0014
GEN-2020-067 | 05 - Southwest | 524414 | AMA_SOUTH | 115 | 16.8512 | 16.8521 | 0.0009
GEN-2020-067 | 05 - Southwest | 524415 | AMA_SOUTH | 230 | 13.6873 | 13.6888 | 0.0015
GEN-2020-067 | 05 - Southwest | 524770 | PLSNT_HILL | 230 | 6.7957 | 6.7966 | 0.0009
GEN-2020-067 | 05 - Southwest | 524875 | OASIS | 230 | 8.5027 | 8.5041 | 0.0014
GEN-2020-067 | 05 - Southwest | 524908 | ROOSEVELT | 115 | 11.4757 | 11.4769 | 0.0012
GEN-2020-067 | 05 - Southwest | 524909 | ROOSEVELT | 230 | 10.2305 | 10.2326 | 0.0021
GEN-2020-067 | 05 - Southwest | 525192 | KRESS_INT | 115 | 11.9467 | 11.9501 | 0.0034
GEN-2020-067 | 05 - Southwest | 525212 | SWISHER | 115 | 11.5229 | 11.5262 | 0.0033
GEN-2020-067 | 05 - Southwest | 525213 | SWISHER | 230 | 10.4337 | 10.4397 | 0.006
GEN-2020-067 | 05 - Southwest | 525326 | COX | 115 | 6.2868 | 6.2881 | 0.0013
GEN-2020-067 | 05 - Southwest | 525414 | LAMTON | 115 | 7.6227 | 7.6239 | 0.0012
GEN-2020-067 | 05 - Southwest | 525453 | HALE_CNTY | 69 | 6.9146 | 6.9155 | 0.0009
GEN-2020-067 | 05 - Southwest | 525454 | HALE_CNTY | 115 | 10.19 | 10.1932 | 0.0032
GEN-2020-067 | 05 - Southwest | 525460 | NEWHART | 115 | 14.9603 | 14.9641 | 0.0038
GEN-2020-067 | 05 - Southwest | 525461 | NEWHART | 230 | 11.0135 | 11.0177 | 0.0042
GEN-2020-067 | 05 - Southwest | 525480 | PLANT_X | 115 | 19.3147 | 19.3204 | 0.0057
GEN-2020-067 | 05 - Southwest | 525481 | PLANT_X | 230 | 24.0225 | 24.0384 | 0.0159
GEN-2020-067 | 05 - Southwest | 525531 | TOLK | 230 | 32.1499 | 32.177 | 0.0271
GEN-2020-067 | 05 - Southwest | 525549 | TOLK | 345 | 16.4531 | 16.4645 | 0.0114
GEN-2020-067 | 05 - Southwest | 525584 | BLUECLDCOL | 230 | 10.5084 | 10.5131 | 0.0047
GEN-2020-067 | 05 - Southwest | 525585 | BLUECLDPOI | 230 | 11.1121 | 11.1174 | 0.0053
GEN-2020-067 | 05 - Southwest | 525586 | NEEDMORE | 230 | 11.1121 | 11.1174 | 0.0053
GEN-2020-067 | 05 - Southwest | 525636 | LAMB_CNTY | 115 | 8.5304 | 8.5317 | 0.0013
GEN-2020-067 | 05 - Southwest | 525637 | LAMB_CNTY | 230 | 5.5683 | 5.5692 | 0.0009
GEN-2020-067 | 05 - Southwest | 525731 | SP-ABERNTHY | 69 | 3.0134 | 3.0138 | 0.0004
GEN-2020-067 | 05 - Southwest | 525738 | HALECENTER | 69 | 2.4592 | 2.4595 | 0.0003
GEN-2020-067 | 05 - Southwest | 525763 | CALLAHAN | 115 | 5.5809 | 5.5822 | 0.0013
GEN-2020-067 | 05 - Southwest | 525779 | FLOYD_CNTY | 69 | 5.41 | 5.4108 | 0.0008
GEN-2020-067 | 05 - Southwest | 525780 | FLOYD_CNTY | 115 | 6.2712 | 6.2729 | 0.0017
GEN-2020-067 | 05 - Southwest | 525803 | BLANCO | 115 | 5.0581 | 5.059 | 0.0009
GEN-2020-067 | 05 - Southwest | 525816 | TUCO_INT2 | 69 | 4.6622 | 4.6632 | 0.001
GEN-2020-067 | 05 - Southwest | 525826 | TUCO_INT | 69 | 7.8819 | 7.8845 | 0.0026
GEN-2020-067 | 05 - Southwest | 525828 | TUCO_INT | 115 | 19.651 | 19.6784 | 0.0274
GEN-2020-067 | 05 - Southwest | 525830 | TUCO_INT | 230 | 23.0556 | 23.1605 | 0.1049
GEN-2020-067 | 05 - Southwest | 525832 | TUCO_INT | 345 | 15.5584 | 15.7032 | 0.1448
GEN-2020-067 | 05 - Southwest | 525840 | ANTELOPE_1 | 230 | 22.8476 | 22.9505 | 0.1029
GEN-2020-067 | 05 - Southwest | 525850 | ELK_CT1 | 345 | 15.3907 | 15.5321 | 0.1414
GEN-2020-067 | 05 - Southwest | 525853 | LH-WIL&ELN+ | 69 | 2.5432 | 2.5434 | 0.0002
GEN-2020-067 | 05 - Southwest | 525885 | SP-NEWDEAL | 69 | 3.3122 | 3.3127 | 0.0005
GEN-2020-067 | 05 - Southwest | 525926 | CROSBY | 115 | 4.7258 | 4.7267 | 0.0009
GEN-2020-067 | 05 - Southwest | 525957 | HALE_WNDCL1 | 230 | 10.7313 | 10.7515 | 0.0202
GEN-2020-067 | 05 - Southwest | 526076 | STANTON_W | 115 | 8.9502 | 8.9548 | 0.0046
GEN-2020-067 | 05 - Southwest | 526109 | SP-ERSKINE | 115 | 11.0061 | 11.0127 | 0.0066
GEN-2020-067 | 05 - Southwest | 526146 | INDIANA | 115 | 9.3299 | 9.3348 | 0.0049
GEN-2020-067 | 05 - Southwest | 526159 | CARLISLE | 69 | 2.5576 | 2.5578 | 0.0002
GEN-2020-067 | 05 - Southwest | 526160 | CARLISLE | 115 | 12.8015 | 12.8103 | 0.0088
GEN-2020-067 | 05 - Southwest | 526161 | CARLISLE | 230 | 10.4291 | 10.4424 | 0.0133
GEN-2020-067 | 05 - Southwest | 526162 | LP-DOUD_TP | 115 | 11.3438 | 11.3506 | 0.0068
GEN-2020-067 | 05 - Southwest | 526192 | MURPHY | 115 | 10.2749 | 10.2801 | 0.0052
GEN-2020-067 | 05 - Southwest | 526268 | LUBBCK_STH | 115 | 17.814 | 17.8257 | 0.0117
GEN-2020-067 | 05 - Southwest | 526269 | LUBBCK_STH | 230 | 15.2484 | 15.2638 | 0.0154
GEN-2020-067 | 05 - Southwest | 526297 | LUBBCK_EST | 69 | 7.9269 | 7.9284 | 0.0015
GEN-2020-067 | 05 - Southwest | 526298 | LUBBCK_EST | 115 | 14.5907 | 14.5991 | 0.0084
GEN-2020-067 | 05 - Southwest | 526299 | LUBBCK_EST | 230 | 11.4786 | 11.4866 | 0.008
GEN-2020-067 | 05 - Southwest | 526337 | JONES | 230 | 16.9667 | 16.984 | 0.0173
GEN-2020-067 | 05 - Southwest | 526434 | SUNDOWN | 115 | 10.8035 | 10.8088 | 0.0053
GEN-2020-067 | 05 - Southwest | 526435 | SUNDOWN | 230 | 11.0332 | 11.0455 | 0.0123
GEN-2020-067 | 05 - Southwest | 526460 | AMOCO_SS | 230 | 9.7652 | 9.7761 | 0.0109
GEN-2020-067 | 05 - Southwest | 526524 | WOLFFORTH | 115 | 11.2892 | 11.2957 | 0.0065
GEN-2020-067 | 05 - Southwest | 526525 | WOLFFORTH | 230 | 12.6452 | 12.6605 | 0.0153
GEN-2020-067 | 05 - Southwest | 526676 | GRASSLAND | 115 | 6.8919 | 6.8934 | 0.0015
GEN-2020-067 | 05 - Southwest | 526677 | GRASSLAND | 230 | 6.0184 | 6.0206 | 0.0022
GEN-2020-067 | 05 - Southwest | 526679 | CIRRUS_WND | 230 | 4.7067 | 4.7081 | 0.0014
GEN-2020-067 | 05 - Southwest | 526736 | TERRY_CNTY | 115 | 10.7227 | 10.7284 | 0.0057
GEN-2020-067 | 05 - Southwest | 526784 | AMOCOWASSON | 230 | 15.9512 | 15.9881 | 0.0369
GEN-2020-067 | 05 - Southwest | 526792 | PRENTICE | 115 | 6.0492 | 6.0516 | 0.0024
GEN-2020-067 | 05 - Southwest | 526928 | PLAINS_INT | 115 | 10.0823 | 10.0903 | 0.008
GEN-2020-067 | 05 - Southwest | 526934 | YOAKUM | 115 | 19.5013 | 19.5335 | 0.0322
GEN-2020-067 | 05 - Southwest | 526935 | YOAKUM | 230 | 20.5087 | 20.6089 | 0.1002
GEN-2020-067 | 05 - Southwest | 526936 | YOAKUM_345 | 345 | 11.3662 | 11.5801 | 0.2139
GEN-2020-067 | 05 - Southwest | 526944 | LG-PLAINS | 115 | 7.9361 | 7.9407 | 0.0046
GEN-2020-067 | 05 - Southwest | 527000 | GAINES_PLNT | 345 | 12.5295 | 12.548 | 0.0185
GEN-2020-067 | 05 - Southwest | 527009 | BRU_SUB | 230 | 16.0627 | 16.1115 | 0.0488
GEN-2020-067 | 05 - Southwest | 527010 | OXYBRU | 230 | 15.9088 | 15.9566 | 0.0478
GEN-2020-067 | 05 - Southwest | 527011 | XTO_MAHONEY | 230 | 15.723 | 15.7661 | 0.0431
GEN-2020-067 | 05 - Southwest | 527018 | BENNETT | 115 | 13.8663 | 13.8773 | 0.011
GEN-2020-067 | 05 - Southwest | 527020 | SIDEWINDER | 345 | 13.0847 | 13.1087 | 0.024
GEN-2020-067 | 05 - Southwest | 527027 | INK_BASIN | 115 | 13.0706 | 13.0796 | 0.009
GEN-2020-067 | 05 - Southwest | 527028 | INK_BASIN | 230 | 11.4867 | 11.5066 | 0.0199
GEN-2020-067 | 05 - Southwest | 527030 | ALRDCRTZ_TP | 115 | 12.2127 | 12.2202 | 0.0075
GEN-2020-067 | 05 - Southwest | 527041 | ARCO_TP | 115 | 13.7709 | 13.7818 | 0.0109
GEN-2020-067 | 05 - Southwest | 527047 | OXY_WILRD1 | 115 | 10.9506 | 10.9574 | 0.0068
GEN-2020-067 | 05 - Southwest | 527062 | SHELL_CO2 | 115 | 16.8151 | 16.8291 | 0.014
GEN-2020-067 | 05 - Southwest | 527130 | DENVER_N | 115 | 22.7003 | 22.723 | 0.0227
GEN-2020-067 | 05 - Southwest | 527136 | DENVER_S | 115 | 22.7003 | 22.723 | 0.0227
GEN-2020-067 | 05 - Southwest | 527146 | MUSTANG | 115 | 24.2635 | 24.2882 | 0.0247
GEN-2020-067 | 05 - Southwest | 527149 | MUSTANG | 230 | 18.2797 | 18.3209 | 0.0412
GEN-2020-067 | 05 - Southwest | 527151 | GS-MUSTANG | 230 | 18.2797 | 18.3209 | 0.0412
GEN-2020-067 | 05 - Southwest | 527194 | LG-PLSHILL | 115 | 8.0042 | 8.0078 | 0.0036
GEN-2020-067 | 05 - Southwest | 527202 | SEAGRAVES | 115 | 9.2146 | 9.2189 | 0.0043
GEN-2020-067 | 05 - Southwest | 527275 | SEMINOLE | 115 | 14.7648 | 14.7752 | 0.0104
GEN-2020-067 | 05 - Southwest | 527276 | SEMINOLE | 230 | 8.2662 | 8.2736 | 0.0074
GEN-2020-067 | 05 - Southwest | 527610 | SAGA_SCOL | 345 | 11.0705 | 11.0808 | 0.0103
GEN-2020-067 | 05 - Southwest | 527655 | RSVLT_CC_E | 345 | 10.8331 | 10.8431 | 0.01
GEN-2020-067 | 05 - Southwest | 527656 | CROSSROADS | 345 | 12.6875 | 12.7018 | 0.0143
GEN-2020-067 | 05 - Southwest | 527802 | EDDY_CNTY | 345 | 8.0173 | 8.026 | 0.0087
GEN-2020-067 | 05 - Southwest | 527867 | CUNNIGHM_S | 230 | 18.6051 | 18.6259 | 0.0208
GEN-2020-067 | 05 - Southwest | 527891 | HOBBS_INT | 115 | 33.177 | 33.199 | 0.022
GEN-2020-067 | 05 - Southwest | 527894 | HOBBS_INT | 230 | 20.8727 | 20.9035 | 0.0308
GEN-2020-067 | 05 - Southwest | 527896 | HOBBS_INT | 345 | 16.5424 | 16.6041 | 0.0617
GEN-2020-067 | 05 - Southwest | 527965 | KIOWA | 345 | 10.2304 | 10.2483 | 0.0179
GEN-2020-067 | 05 - Southwest | 527966 | KIOWA | 115 | 18.4025 | 18.4184 | 0.0159
GEN-2020-067 | 05 - Southwest | 528015 | PHANTOM | 345 | 6.2521 | 6.259 | 0.0069
GEN-2020-067 | 05 - Southwest | 528025 | RDRUNNER | 115 | 14.8553 | 14.8681 | 0.0128
GEN-2020-067 | 05 - Southwest | 528027 | RDRUNNER | 345 | 10.3444 | 10.3653 | 0.0209
GEN-2020-067 | 05 - Southwest | 528185 | N_LOVING | 345 | 7.2976 | 7.3067 | 0.0091
GEN-2020-067 | 05 - Southwest | 528325 | LE-WAITS | 115 | 8.9385 | 8.942 | 0.0035
GEN-2020-067 | 05 - Southwest | 528604 | ANDREWS | 345 | 9.1093 | 9.1206 | 0.0113
GEN-2020-067 | 05 - Southwest | 528626 | LE-PLNSINT | 69 | 3.6425 | 3.6431 | 0.0006
GEN-2020-067 | 05 - Southwest | 560022 | CRAWFISH_DR | 345 | 15.3371 | 15.4742 | 0.1371
GEN-2020-067 | 05 - Southwest | 588460 | A16-008SUB | 115 | 13.0706 | 13.0796 | 0.009
GEN-2020-067 | 05 - Southwest | 588760 | GEN-2017-03 | 345 | 4.9311 | 4.9338 | 0.0027
GEN-2020-067 | 05 - Southwest | 599955 | PNM-DC6 | 230 | 10.2305 | 10.2326 | 0.0021
GEN-2020-067 | 05 - Southwest | 760498 | G17-146-TAP | 230 | 7.7316 | 7.7326 | 0.001
GEN-2020-067 | 05 - Southwest | 760938 | G17-171-TAP | 345 | 11.3071 | 11.3107 | 0.0036
GEN-2020-067 | 05 - Southwest | 761355 | GEN-2017-23 | 230 | 14.0892 | 14.1234 | 0.0342
GEN-2020-067 | 05 - Southwest | 762132 | GEN-2017-15 | 230 | 13.9737 | 13.9781 | 0.0044
GEN-2020-067 | 05 - Southwest | 762216 | G17-151TAP | 345 | 8.8981 | 8.9343 | 0.0362
GEN-2020-067 | 05 - Southwest | 762217 | GEN-2017-15 | 345 | 6.3663 | 6.3839 | 0.0176
GEN-2020-067 | 05 - Southwest | 762460 | GEN-2018-01 | 345 | 9.3847 | 9.4054 | 0.0207
GEN-2020-067 | 05 - Southwest | 762467 | G18-015-TAP | 345 | 9.4189 | 9.4398 | 0.0209
GEN-2020-067 | 05 - Southwest | 763186 | GEN-2018-08 | 230 | 10.7036 | 10.7075 | 0.0039
GEN-2020-067 | 05 - Southwest | 763215 | G18-092-PRO | 345 | 9.3529 | 9.3698 | 0.0169
GEN-2020-067 | 05 - Southwest | 763318 | GEN-2018-11 | 345 | 15.0573 | 15.0657 | 0.0084
GEN-2020-067 | 05 - Southwest | 763483 | GEN-2019-00 | 230 | 9.1547 | 9.1563 | 0.0016
GEN-2020-067 | 05 - Southwest | 763516 | GEN-2019-01 | 345 | 10.5276 | 10.7109 | 0.1833
GEN-2020-067 | 05 - Southwest | 764550 | G20-075-TAP | 345 | 14.3908 | 14.3962 | 0.0054
GEN-2020-067 | 05 - Southwest | 764825 | GEN-2020-01 | 230 | 5.55 | 5.5509 | 0.0009
GEN-2020-067 | 05 - Southwest | 764840 | GEN-2020-05 | 345 | 11.3434 | 11.4535 | 0.1101
GEN-2020-067 | 05 - Southwest | 764866 | G20-059-TAP | 345 | 11.4211 | 11.5328 | 0.1117
GEN-2020-067 | 05 - Southwest | 764875 | GEN-2020-06 | 230 | 11.3036 | 11.3113 | 0.0077
GEN-2020-067 | 05 - Southwest | 764935 | GEN-2020-06 | 345 | 6.4717 | 7.0161 | 0.5444
GEN-2020-067 | 05 - Southwest | 764945 | G20-067-TAP | 345 | 8.0824 | 8.6182 | 0.5358
GEN-2020-067 | 05 - Southwest | 764948 | G20-068-SS1 | 345 | 6.5656 | 6.9074 | 0.3418
GEN-2020-067 | 05 - Southwest | 764949 | G20-068-SS2 | 345 | 6.5637 | 6.9054 | 0.3417
GEN-2020-067 | 05 - Southwest | 764950 | GEN-2020-06 | 345 | 8.0456 | 8.5759 | 0.5303
GEN-2020-067 | 05 - Southwest | 766291 | G20-009-TAP | 345 | 9.4675 | 9.4725 | 0.005
GEN-2020-065 | 05 - Southwest | 511553 | CHISHOLM7 | 345 | 12.7359 | 12.7423 | 0.0064
GEN-2020-065 | 05 - Southwest | 523097 | HITCHLAND | 345 | 14.6228 | 14.6258 | 0.003
GEN-2020-065 | 05 - Southwest | 523959 | POTTER_CO | 230 | 23.0641 | 23.0856 | 0.0215
GEN-2020-065 | 05 - Southwest | 523961 | POTTER_CO | 345 | 13.9236 | 13.9531 | 0.0295
GEN-2020-065 | 05 - Southwest | 524296 | SPNSPUR_WND | 345 | 5.6814 | 5.6855 | 0.0041
GEN-2020-065 | 05 - Southwest | 524909 | ROOSEVELT | 230 | 10.2023 | 10.2326 | 0.0303
GEN-2020-065 | 05 - Southwest | 525481 | PLANT_X | 230 | 23.9099 | 24.0384 | 0.1285
GEN-2020-065 | 05 - Southwest | 525531 | TOLK | 230 | 31.8876 | 32.177 | 0.2894
GEN-2020-065 | 05 - Southwest | 525549 | TOLK | 345 | 16.2463 | 16.4645 | 0.2182
GEN-2020-065 | 05 - Southwest | 525586 | NEEDMORE | 230 | 11.0729 | 11.1174 | 0.0445
GEN-2020-065 | 05 - Southwest | 525637 | LAMB_CNTY | 230 | 5.5611 | 5.5692 | 0.0081
GEN-2020-065 | 05 - Southwest | 525830 | TUCO_INT | 230 | 23.0864 | 23.1605 | 0.0741
GEN-2020-065 | 05 - Southwest | 525832 | TUCO_INT | 345 | 15.6413 | 15.7032 | 0.0619
GEN-2020-065 | 05 - Southwest | 526460 | AMOCO_SS | 230 | 9.7327 | 9.7761 | 0.0434
GEN-2020-065 | 05 - Southwest | 526934 | YOAKUM | 115 | 19.3604 | 19.5335 | 0.1731
GEN-2020-065 | 05 - Southwest | 526935 | YOAKUM | 230 | 20.1203 | 20.6089 | 0.4886
GEN-2020-065 | 05 - Southwest | 526936 | YOAKUM_345 | 345 | 10.9716 | 11.5801 | 0.6085
GEN-2020-065 | 05 - Southwest | 527000 | GAINES_PLNT | 345 | 7.2328 | 12.548 | 5.3152
GEN-2020-065 | 05 - Southwest | 527009 | BRU_SUB | 230 | 15.8643 | 16.1115 | 0.2472
GEN-2020-065 | 05 - Southwest | 527020 | SIDEWINDER | 345 | 8.2221 | 13.1087 | 4.8866
GEN-2020-065 | 05 - Southwest | 527027 | INK_BASIN | 115 | 12.9681 | 13.0796 | 0.1115
GEN-2020-065 | 05 - Southwest | 527028 | INK_BASIN | 230 | 11.2774 | 11.5066 | 0.2292
GEN-2020-065 | 05 - Southwest | 527030 | ALRDCRTZ_TP | 115 | 12.1357 | 12.2202 | 0.0845
GEN-2020-065 | 05 - Southwest | 527149 | MUSTANG | 230 | 18.0928 | 18.3209 | 0.2281
GEN-2020-065 | 05 - Southwest | 527363 | HIGG | 115 | 10.371 | 10.4399 | 0.0689
GEN-2020-065 | 05 - Southwest | 527483 | CHAVES_CNTY | 230 | 4.5251 | 4.5767 | 0.0516
GEN-2020-065 | 05 - Southwest | 527599 | SAGA_SDCOL | 345 | 10.495 | 11.0808 | 0.5858
GEN-2020-065 | 05 - Southwest | 527600 | SAGA_SMEAS | 345 | 10.495 | 11.0808 | 0.5858
GEN-2020-065 | 05 - Southwest | 527610 | SAGA_SCOL | 345 | 10.495 | 11.0808 | 0.5858
GEN-2020-065 | 05 - Southwest | 527654 | RSVLT_CC_W | 345 | 8.9136 | 9.325 | 0.4114
GEN-2020-065 | 05 - Southwest | 527655 | RSVLT_CC_E | 345 | 10.272 | 10.8431 | 0.5711
GEN-2020-065 | 05 - Southwest | 527656 | CROSSROADS | 345 | 11.8953 | 12.7018 | 0.8065
GEN-2020-065 | 05 - Southwest | 527666 | RSVLT_COL1 | 345 | 8.9136 | 9.325 | 0.4114
GEN-2020-065 | 05 - Southwest | 527667 | RSVLT_COL2 | 345 | 8.9136 | 9.325 | 0.4114
GEN-2020-065 | 05 - Southwest | 527793 | EDDY_STH | 115 | 12.0443 | 12.4148 | 0.3705
GEN-2020-065 | 05 - Southwest | 527798 | EDDY_NTH | 115 | 12.0443 | 12.4148 | 0.3705
GEN-2020-065 | 05 - Southwest | 527799 | EDDY_NORTH | 230 | 9.5153 | 9.9892 | 0.4739
GEN-2020-065 | 05 - Southwest | 527802 | EDDY_CNTY | 345 | 7.4625 | 8.026 | 0.5635
GEN-2020-065 | 05 - Southwest | 527864 | CUNNINHAM | 115 | 28.1471 | 29.042 | 0.8949
GEN-2020-065 | 05 - Southwest | 527865 | CUNNIGHM_N | 230 | 17.5539 | 18.6259 | 1.072
GEN-2020-065 | 05 - Southwest | 527867 | CUNNIGHM_S | 230 | 17.5539 | 18.6259 | 1.072
GEN-2020-065 | 05 - Southwest | 527891 | HOBBS_INT | 115 | 32.0926 | 33.199 | 1.1064
GEN-2020-065 | 05 - Southwest | 527894 | HOBBS_INT | 230 | 19.4052 | 20.9035 | 1.4983
GEN-2020-065 | 05 - Southwest | 527896 | HOBBS_INT | 345 | 12.8822 | 16.6041 | 3.7219
GEN-2020-065 | 05 - Southwest | 527930 | PCA | 115 | 12.0409 | 12.4891 | 0.4482
GEN-2020-065 | 05 - Southwest | 527961 | POTASH_JCT | 69 | 9.8934 | 10.0901 | 0.1967
GEN-2020-065 | 05 - Southwest | 527962 | POTASH_JCT | 115 | 17.3473 | 18.4308 | 1.0835
GEN-2020-065 | 05 - Southwest | 527963 | POTASH_JCT | 230 | 7.5192 | 7.8188 | 0.2996
GEN-2020-065 | 05 - Southwest | 527965 | KIOWA | 345 | 9.0632 | 10.2483 | 1.1851
GEN-2020-065 | 05 - Southwest | 527966 | KIOWA | 115 | 17.3249 | 18.4184 | 1.0935
GEN-2020-065 | 05 - Southwest | 527999 | INTREPDW_TP | 115 | 14.0653 | 14.7878 | 0.7225
GEN-2020-065 | 05 - Southwest | 528013 | PHANTOM | 115 | 13.2323 | 14.0685 | 0.8362
GEN-2020-065 | 05 - Southwest | 528015 | PHANTOM | 345 | 5.7678 | 6.259 | 0.4912
GEN-2020-065 | 05 - Southwest | 528016 | SAND_DUNES | 115 | 7.4611 | 7.7171 | 0.256
GEN-2020-065 | 05 - Southwest | 528018 | RED_BLUFF | 115 | 10.2569 | 10.7584 | 0.5015
GEN-2020-065 | 05 - Southwest | 528020 | BOPCO_PKRLK | 115 | 13.0195 | 13.8284 | 0.8089
GEN-2020-065 | 05 - Southwest | 528024 | RR_SVC_HV | 115 | 13.8857 | 14.8681 | 0.9824
GEN-2020-065 | 05 - Southwest | 528025 | RDRUNNER | 115 | 13.8857 | 14.8681 | 0.9824
GEN-2020-065 | 05 - Southwest | 528027 | RDRUNNER | 345 | 8.9621 | 10.3653 | 1.4032
GEN-2020-065 | 05 - Southwest | 528040 | BATTLE_AXE | 115 | 3.2172 | 3.267 | 0.0498
GEN-2020-065 | 05 - Southwest | 528095 | 7-RIVERS | 230 | 6.435 | 6.6545 | 0.2195
GEN-2020-065 | 05 - Southwest | 528160 | CARLSBAD | 115 | 11.4718 | 11.8661 | 0.3943
GEN-2020-065 | 05 - Southwest | 528182 | NORTH_LOVNG | 115 | 12.5561 | 13.2437 | 0.6876
GEN-2020-065 | 05 - Southwest | 528185 | N_LOVING | 345 | 6.676 | 7.3067 | 0.6307
GEN-2020-065 | 05 - Southwest | 528192 | SOUTH_LOVNG | 115 | 9.4563 | 9.8454 | 0.3891
GEN-2020-065 | 05 - Southwest | 528193 | BLACKRIVER | 115 | 10.3943 | 10.8642 | 0.4699
GEN-2020-065 | 05 - Southwest | 528194 | MALAGABEND | 115 | 7.9487 | 8.2342 | 0.2855
GEN-2020-065 | 05 - Southwest | 528195 | AGAVE_PDURO | 115 | 8.0948 | 8.3744 | 0.2796
GEN-2020-065 | 05 - Southwest | 528222 | CHINA_DRAW | 115 | 11.1097 | 11.678 | 0.5683
GEN-2020-065 | 05 - Southwest | 528223 | CHINA_DRAW | 345 | 5.9211 | 6.425 | 0.5039
GEN-2020-065 | 05 - Southwest | 528226 | HOPI_SUB | 115 | 7.3421 | 7.5199 | 0.1778
GEN-2020-065 | 05 - Southwest | 528228 | WOOD_DRAW | 115 | 8.27 | 8.5846 | 0.3146
GEN-2020-065 | 05 - Southwest | 528230 | AGAVE_RHILL | 115 | 12.4367 | 13.2193 | 0.7826
GEN-2020-065 | 05 - Southwest | 528231 | AGAVE_RHIL2 | 115 | 11.6952 | 12.3846 | 0.6894
GEN-2020-065 | 05 - Southwest | 528232 | OCHOA | 115 | 11.7517 | 12.448 | 0.6963
GEN-2020-065 | 05 - Southwest | 528235 | WOLFCAMP_TP | 115 | 12.2913 | 13.0106 | 0.7193
GEN-2020-065 | 05 - Southwest | 528239 | CUSTERMTN | 115 | 7.7236 | 7.9871 | 0.2635
GEN-2020-065 | 05 - Southwest | 528240 | PONDEROSA | 115 | 4.0536 | 4.1248 | 0.0712
GEN-2020-065 | 05 - Southwest | 528325 | LE-WAITS | 115 | 8.8884 | 8.942 | 0.0536
GEN-2020-065 | 05 - Southwest | 528333 | LE-WEST_SUB | 115 | 8.8598 | 8.9164 | 0.0566
GEN-2020-065 | 05 - Southwest | 528334 | LE-NRTH_INT | 115 | 8.7985 | 8.8542 | 0.0557
GEN-2020-065 | 05 - Southwest | 528348 | BUCKEYE_TP | 115 | 8.2329 | 8.3045 | 0.0716
GEN-2020-065 | 05 - Southwest | 528353 | MADDOXG23 | 115 | 27.187 | 28.0021 | 0.8151
GEN-2020-065 | 05 - Southwest | 528355 | MADDOX | 115 | 27.187 | 28.0021 | 0.8151
GEN-2020-065 | 05 - Southwest | 528392 | PEARLE | 115 | 6.3552 | 6.4119 | 0.0567
GEN-2020-065 | 05 - Southwest | 528394 | QUAHADA | 115 | 8.069 | 8.2033 | 0.1343
GEN-2020-065 | 05 - Southwest | 528433 | BENSING | 115 | 8.0549 | 8.1075 | 0.0526
GEN-2020-065 | 05 - Southwest | 528434 | MILLEN_TPW | 115 | 11.8029 | 11.9556 | 0.1527
GEN-2020-065 | 05 - Southwest | 528435 | MILLEN | 115 | 11.8029 | 11.9556 | 0.1527
GEN-2020-065 | 05 - Southwest | 528436 | MILLEN_TPE | 115 | 11.8029 | 11.9556 | 0.1527
GEN-2020-065 | 05 - Southwest | 528491 | MONUMENT | 115 | 15.888 | 16.2332 | 0.3452
GEN-2020-065 | 05 - Southwest | 528533 | DRINKARD_TP | 115 | 8.1829 | 8.5694 | 0.3865
GEN-2020-065 | 05 - Southwest | 528540 | WHITTEN | 115 | 7.7204 | 7.9737 | 0.2533
GEN-2020-065 | 05 - Southwest | 528568 | MONUMNT_TP | 115 | 10.3669 | 10.5189 | 0.152
GEN-2020-065 | 05 - Southwest | 528589 | DRINKARD | 115 | 8.4597 | 8.9447 | 0.485
GEN-2020-065 | 05 - Southwest | 528596 | CARDINAL | 115 | 8.3848 | 8.9489 | 0.5641
GEN-2020-065 | 05 - Southwest | 528602 | ANDREWS | 115 | 12.8907 | 14.9121 | 2.0214
GEN-2020-065 | 05 - Southwest | 528603 | NA_ENRICH | 115 | 12.1357 | 13.7109 | 1.5752
GEN-2020-065 | 05 - Southwest | 528604 | ANDREWS | 345 | 6.5835 | 9.1206 | 2.5371
GEN-2020-065 | 05 - Southwest | 528605 | TARGA | 115 | 9.2513 | 10.0212 | 0.7699
GEN-2020-065 | 05 - Southwest | 587990 | GEN-2016-12 | 115 | 13.6576 | 14.6069 | 0.9493
GEN-2020-065 | 05 - Southwest | 588460 | A16-008SUB | 115 | 12.9681 | 13.0796 | 0.1115
GEN-2020-065 | 05 - Southwest | 599960 | EPTNP-D6 | 230 | 9.5153 | 9.9892 | 0.4739
GEN-2020-065 | 05 - Southwest | 762132 | GEN-2017-15 | 230 | 13.9303 | 13.9781 | 0.0478
GEN-2020-065 | 05 - Southwest | 762442 | G18-004-TAP | 115 | 23.4671 | 24.0705 | 0.6034
GEN-2020-065 | 05 - Southwest | 763516 | GEN-2019-01 | 345 | 10.1883 | 10.7109 | 0.5226
GEN-2020-065 | 05 - Southwest | 764840 | GEN-2020-05 | 345 | 10.4354 | 11.4535 | 1.0181
GEN-2020-065 | 05 - Southwest | 764866 | G20-059-TAP | 345 | 10.5002 | 11.5328 | 1.0326
GEN-2020-065 | 05 - Southwest | 764935 | GEN-2020-06 | 345 | 6.9264 | 7.0161 | 0.0897
GEN-2020-065 | 05 - Southwest | 764945 | G20-067-TAP | 345 | 8.4787 | 8.6182 | 0.1395
GEN-2020-065 | 05 - Southwest | 764950 | GEN-2020-06 | 345 | 8.4378 | 8.5759 | 0.1381
GEN-2020-062 | 05 - Southwest | 511553 | CHISHOLM7 | 345 | 12.7405 | 12.7423 | 0.0018
GEN-2020-062 | 05 - Southwest | 523097 | HITCHLAND | 345 | 14.6246 | 14.6258 | 0.0012
GEN-2020-062 | 05 - Southwest | 523959 | POTTER_CO | 230 | 23.0724 | 23.0856 | 0.0132
GEN-2020-062 | 05 - Southwest | 523961 | POTTER_CO | 345 | 13.9417 | 13.9531 | 0.0114
GEN-2020-062 | 05 - Southwest | 524296 | SPNSPUR_WND | 345 | 5.6839 | 5.6855 | 0.0016
GEN-2020-062 | 05 - Southwest | 524415 | AMA_SOUTH | 230 | 13.6851 | 13.6888 | 0.0037
GEN-2020-062 | 05 - Southwest | 524472 | LOPEZ | 115 | 2.2614 | 2.2635 | 0.0021
GEN-2020-062 | 05 - Southwest | 524486 | CAPROCK | 115 | 2.6362 | 2.639 | 0.0028
GEN-2020-062 | 05 - Southwest | 524502 | NORTON | 115 | 2.9188 | 2.9236 | 0.0048
GEN-2020-062 | 05 - Southwest | 524509 | FE-TUCMCARI | 115 | 2.3911 | 2.3936 | 0.0025
GEN-2020-062 | 05 - Southwest | 524623 | DEAFSMITH | 230 | 8.0033 | 8.0147 | 0.0114
GEN-2020-062 | 05 - Southwest | 524662 | PARMER_CO | 115 | 5.4661 | 5.4956 | 0.0295
GEN-2020-062 | 05 - Southwest | 524669 | DS-#20 | 115 | 6.278 | 6.3363 | 0.0583
GEN-2020-062 | 05 - Southwest | 524764 | NORRIS_TP | 115 | 11.4243 | 11.7163 | 0.292
GEN-2020-062 | 05 - Southwest | 524768 | PLSNT_HILL | 115 | 10.5433 | 10.8127 | 0.2694
GEN-2020-062 | 05 - Southwest | 524770 | PLSNT_HILL | 230 | 6.5333 | 6.7966 | 0.2633
GEN-2020-062 | 05 - Southwest | 524773 | E_CLOVIS | 115 | 8.973 | 9.1607 | 0.1877
GEN-2020-062 | 05 - Southwest | 524776 | N_CLOVIS_TP | 115 | 7.4826 | 7.6223 | 0.1397
GEN-2020-062 | 05 - Southwest | 524777 | N_CLOVIS | 115 | 6.7494 | 6.8632 | 0.1138
GEN-2020-062 | 05 - Southwest | 524783 | W_CLOVIS | 69 | 2.4407 | 2.4486 | 0.0079
GEN-2020-062 | 05 - Southwest | 524784 | W_CLOVIS | 115 | 6.3336 | 6.4388 | 0.1052
GEN-2020-062 | 05 - Southwest | 524790 | CANNON_TP | 115 | 6.0115 | 6.1115 | 0.1
GEN-2020-062 | 05 - Southwest | 524794 | CANNONAFB | 115 | 5.6385 | 5.7265 | 0.088
GEN-2020-062 | 05 - Southwest | 524797 | PERIMETER | 115 | 6.5585 | 6.6884 | 0.1299
GEN-2020-062 | 05 - Southwest | 524801 | NORRIS | 115 | 10.4255 | 10.6687 | 0.2432
GEN-2020-062 | 05 - Southwest | 524808 | FE-CLVS_INT | 115 | 6.9569 | 7.079 | 0.1221
GEN-2020-062 | 05 - Southwest | 524821 | CURRY | 69 | 4.4299 | 4.4554 | 0.0255
GEN-2020-062 | 05 - Southwest | 524822 | CURRY | 115 | 11.4571 | 11.7506 | 0.2935
GEN-2020-062 | 05 - Southwest | 524831 | FE-HOLLAND | 115 | 9.255 | 9.4559 | 0.2009
GEN-2020-062 | 05 - Southwest | 524838 | FE-CLOVIS2+ | 115 | 10.8094 | 11.0721 | 0.2627
GEN-2020-062 | 05 - Southwest | 524846 | FARWELL | 69 | 2.1361 | 2.1421 | 0.006
GEN-2020-062 | 05 - Southwest | 524863 | FE-CHZPLT | 115 | 8.0327 | 8.2088 | 0.1761
GEN-2020-062 | 05 - Southwest | 524874 | OASIS | 115 | 10.0728 | 10.409 | 0.3362
GEN-2020-062 | 05 - Southwest | 524875 | OASIS | 230 | 7.9067 | 8.5041 | 0.5974
GEN-2020-062 | 05 - Southwest | 524885 | SN_JUAN_TAP | 230 | 4.8968 | 4.971 | 0.0742
GEN-2020-062 | 05 - Southwest | 524889 | SN_JUAN_WND | 230 | 4.6787 | 4.7438 | 0.0651
GEN-2020-062 | 05 - Southwest | 524908 | ROOSEVELT | 115 | 11.1658 | 11.4769 | 0.3111
GEN-2020-062 | 05 - Southwest | 524909 | ROOSEVELT | 230 | 9.746 | 10.2326 | 0.4866
GEN-2020-062 | 05 - Southwest | 524923 | PORTALES | 69 | 7.5664 | 7.6666 | 0.1002
GEN-2020-062 | 05 - Southwest | 524924 | PORTALES | 115 | 7.5623 | 7.7319 | 0.1696
GEN-2020-062 | 05 - Southwest | 524929 | RO-PORT_MTR | 69 | 7.5664 | 7.6666 | 0.1002
GEN-2020-062 | 05 - Southwest | 524934 | ZODIAC | 69 | 5.547 | 5.6012 | 0.0542
GEN-2020-062 | 05 - Southwest | 524935 | KILGORE | 115 | 6.1553 | 6.2673 | 0.112
GEN-2020-062 | 05 - Southwest | 524941 | PORTALES#1 | 69 | 5.7543 | 5.8127 | 0.0584
GEN-2020-062 | 05 - Southwest | 524948 | PORTALES#2 | 69 | 4.863 | 4.9047 | 0.0417
GEN-2020-062 | 05 - Southwest | 524962 | S_PORTALES | 69 | 4.3156 | 4.3484 | 0.0328
GEN-2020-062 | 05 - Southwest | 524963 | S_PORTALES | 115 | 5.7765 | 5.8751 | 0.0986
GEN-2020-062 | 05 - Southwest | 524977 | GREYHOUND | 115 | 5.6918 | 5.7875 | 0.0957
GEN-2020-062 | 05 - Southwest | 525019 | MULSHVLY_TP | 115 | 5.9498 | 5.9668 | 0.017
GEN-2020-062 | 05 - Southwest | 525027 | BAILEYCO | 69 | 5.2712 | 5.2797 | 0.0085
GEN-2020-062 | 05 - Southwest | 525028 | BAILEYCO | 115 | 5.803 | 5.8202 | 0.0172
GEN-2020-062 | 05 - Southwest | 525056 | BC-EARTH | 115 | 8.2578 | 8.2649 | 0.0071
GEN-2020-062 | 05 - Southwest | 525212 | SWISHER | 115 | 11.5221 | 11.5262 | 0.0041
GEN-2020-062 | 05 - Southwest | 525213 | SWISHER | 230 | 10.434 | 10.4397 | 0.0057
GEN-2020-062 | 05 - Southwest | 525446 | RKYFORD_TP | 115 | 10.1266 | 10.1385 | 0.0119
GEN-2020-062 | 05 - Southwest | 525454 | HALE_CNTY | 115 | 10.1888 | 10.1932 | 0.0044
GEN-2020-062 | 05 - Southwest | 525460 | NEWHART | 115 | 14.9537 | 14.9641 | 0.0104
GEN-2020-062 | 05 - Southwest | 525461 | NEWHART | 230 | 11.0076 | 11.0177 | 0.0101
GEN-2020-062 | 05 - Southwest | 525480 | PLANT_X | 115 | 19.2706 | 19.3204 | 0.0498
GEN-2020-062 | 05 - Southwest | 525481 | PLANT_X | 230 | 23.9146 | 24.0384 | 0.1238
GEN-2020-062 | 05 - Southwest | 525531 | TOLK | 230 | 31.8855 | 32.177 | 0.2915
GEN-2020-062 | 05 - Southwest | 525549 | TOLK | 345 | 16.3911 | 16.4645 | 0.0734
GEN-2020-062 | 05 - Southwest | 525584 | BLUECLDCOL | 230 | 10.4896 | 10.5131 | 0.0235
GEN-2020-062 | 05 - Southwest | 525585 | BLUECLDPOI | 230 | 11.0911 | 11.1174 | 0.0263
GEN-2020-062 | 05 - Southwest | 525586 | NEEDMORE | 230 | 11.0911 | 11.1174 | 0.0263
GEN-2020-062 | 05 - Southwest | 525635 | LAMB_CNTY | 69 | 5.9235 | 5.9257 | 0.0022
GEN-2020-062 | 05 - Southwest | 525636 | LAMB_CNTY | 115 | 8.5241 | 8.5317 | 0.0076
GEN-2020-062 | 05 - Southwest | 525637 | LAMB_CNTY | 230 | 5.5618 | 5.5692 | 0.0074
GEN-2020-062 | 05 - Southwest | 525780 | FLOYD_CNTY | 115 | 6.2722 | 6.2729 | 0.0007
GEN-2020-062 | 05 - Southwest | 525816 | TUCO_INT2 | 69 | 4.663 | 4.6632 | 0.0002
GEN-2020-062 | 05 - Southwest | 525826 | TUCO_INT | 69 | 7.884 | 7.8845 | 0.0005
GEN-2020-062 | 05 - Southwest | 525828 | TUCO_INT | 115 | 19.673 | 19.6784 | 0.0054
GEN-2020-062 | 05 - Southwest | 525830 | TUCO_INT | 230 | 23.1474 | 23.1605 | 0.0131
GEN-2020-062 | 05 - Southwest | 525832 | TUCO_INT | 345 | 15.698 | 15.7032 | 0.0052
GEN-2020-062 | 05 - Southwest | 525840 | ANTELOPE_1 | 230 | 22.9377 | 22.9505 | 0.0128
GEN-2020-062 | 05 - Southwest | 525850 | ELK_CT1 | 345 | 15.5271 | 15.5321 | 0.005
GEN-2020-062 | 05 - Southwest | 525957 | HALE_WNDCL1 | 230 | 10.7489 | 10.7515 | 0.0026
GEN-2020-062 | 05 - Southwest | 526020 | HOCKLEY | 115 | 5.4315 | 5.4331 | 0.0016
GEN-2020-062 | 05 - Southwest | 526076 | STANTON_W | 115 | 8.9539 | 8.9548 | 0.0009
GEN-2020-062 | 05 - Southwest | 526160 | CARLISLE | 115 | 12.8085 | 12.8103 | 0.0018
GEN-2020-062 | 05 - Southwest | 526161 | CARLISLE | 230 | 10.4398 | 10.4424 | 0.0026
GEN-2020-062 | 05 - Southwest | 526269 | LUBBCK_STH | 230 | 15.2606 | 15.2638 | 0.0032
GEN-2020-062 | 05 - Southwest | 526298 | LUBBCK_EST | 115 | 14.5973 | 14.5991 | 0.0018
GEN-2020-062 | 05 - Southwest | 526299 | LUBBCK_EST | 230 | 11.485 | 11.4866 | 0.0016
GEN-2020-062 | 05 - Southwest | 526337 | JONES | 230 | 16.9807 | 16.984 | 0.0033
GEN-2020-062 | 05 - Southwest | 526434 | SUNDOWN | 115 | 10.8059 | 10.8088 | 0.0029
GEN-2020-062 | 05 - Southwest | 526435 | SUNDOWN | 230 | 11.0391 | 11.0455 | 0.0064
GEN-2020-062 | 05 - Southwest | 526460 | AMOCO_SS | 230 | 9.7716 | 9.7761 | 0.0045
GEN-2020-062 | 05 - Southwest | 526525 | WOLFFORTH | 230 | 12.6566 | 12.6605 | 0.0039
GEN-2020-062 | 05 - Southwest | 526677 | GRASSLAND | 230 | 6.0202 | 6.0206 | 0.0004
GEN-2020-062 | 05 - Southwest | 526934 | YOAKUM | 115 | 19.5299 | 19.5335 | 0.0036
GEN-2020-062 | 05 - Southwest | 526935 | YOAKUM | 230 | 20.6001 | 20.6089 | 0.0088
GEN-2020-062 | 05 - Southwest | 526936 | YOAKUM_345 | 345 | 11.5762 | 11.5801 | 0.0039
GEN-2020-062 | 05 - Southwest | 527009 | BRU_SUB | 230 | 16.1071 | 16.1115 | 0.0044
GEN-2020-062 | 05 - Southwest | 527028 | INK_BASIN | 230 | 11.5042 | 11.5066 | 0.0024
GEN-2020-062 | 05 - Southwest | 527149 | MUSTANG | 230 | 18.3171 | 18.3209 | 0.0038
GEN-2020-062 | 05 - Southwest | 527455 | RSWL_SLRCOL | 115 | 7.0581 | 7.0778 | 0.0197
GEN-2020-062 | 05 - Southwest | 527470 | CHVS_SLRCOL | 115 | 6.8907 | 6.9096 | 0.0189
GEN-2020-062 | 05 - Southwest | 527482 | CHAVES_CNTY | 115 | 7.1293 | 7.1495 | 0.0202
GEN-2020-062 | 05 - Southwest | 527483 | CHAVES_CNTY | 230 | 4.5576 | 4.5767 | 0.0191
GEN-2020-062 | 05 - Southwest | 527501 | URTON | 115 | 5.9292 | 5.9427 | 0.0135
GEN-2020-062 | 05 - Southwest | 527508 | PRICE | 115 | 4.8851 | 4.8944 | 0.0093
GEN-2020-062 | 05 - Southwest | 527509 | PRICE_TAP | 115 | 5.5002 | 5.512 | 0.0118
GEN-2020-062 | 05 - Southwest | 527522 | ROSWELL_CTY | 115 | 5.6337 | 5.6455 | 0.0118
GEN-2020-062 | 05 - Southwest | 527541 | CAPITAN | 115 | 4.7237 | 4.732 | 0.0083
GEN-2020-062 | 05 - Southwest | 527546 | SAMSON | 115 | 5.566 | 5.5775 | 0.0115
GEN-2020-062 | 05 - Southwest | 527564 | ROSWLL_INT | 115 | 5.8431 | 5.8554 | 0.0123
GEN-2020-062 | 05 - Southwest | 527597 | TWEEDY | 115 | 5.3822 | 5.392 | 0.0098
GEN-2020-062 | 05 - Southwest | 527610 | SAGA_SCOL | 345 | 11.0706 | 11.0808 | 0.0102
GEN-2020-062 | 05 - Southwest | 527655 | RSVLT_CC_E | 345 | 10.8331 | 10.8431 | 0.01
GEN-2020-062 | 05 - Southwest | 527656 | CROSSROADS | 345 | 12.6875 | 12.7018 | 0.0143
GEN-2020-062 | 05 - Southwest | 527711 | EAGLE_CREEK | 115 | 7.7772 | 7.781 | 0.0038
GEN-2020-062 | 05 - Southwest | 527793 | EDDY_STH | 115 | 12.4042 | 12.4148 | 0.0106
GEN-2020-062 | 05 - Southwest | 527798 | EDDY_NTH | 115 | 12.4042 | 12.4148 | 0.0106
GEN-2020-062 | 05 - Southwest | 527799 | EDDY_NORTH | 230 | 9.9763 | 9.9892 | 0.0129
GEN-2020-062 | 05 - Southwest | 527802 | EDDY_CNTY | 345 | 8.0188 | 8.026 | 0.0072
GEN-2020-062 | 05 - Southwest | 527809 | CV-8_MILE | 115 | 5.5647 | 5.5669 | 0.0022
GEN-2020-062 | 05 - Southwest | 527821 | CV-DAYTON | 115 | 7.3504 | 7.3537 | 0.0033
GEN-2020-062 | 05 - Southwest | 527865 | CUNNIGHM_N | 230 | 18.6188 | 18.6259 | 0.0071
GEN-2020-062 | 05 - Southwest | 527867 | CUNNIGHM_S | 230 | 18.6188 | 18.6259 | 0.0071
GEN-2020-062 | 05 - Southwest | 527896 | HOBBS_INT | 345 | 16.5925 | 16.6041 | 0.0116
GEN-2020-062 | 05 - Southwest | 527963 | POTASH_JCT | 230 | 7.8157 | 7.8188 | 0.0031
GEN-2020-062 | 05 - Southwest | 527965 | KIOWA | 345 | 10.2412 | 10.2483 | 0.0071
GEN-2020-062 | 05 - Southwest | 528094 | 7-RIVERS | 115 | 8.685 | 8.6887 | 0.0037
GEN-2020-062 | 05 - Southwest | 528095 | 7-RIVERS | 230 | 6.6503 | 6.6545 | 0.0042
GEN-2020-062 | 05 - Southwest | 528178 | PECOS | 115 | 12.5858 | 12.5913 | 0.0055
GEN-2020-062 | 05 - Southwest | 528179 | PECOS | 230 | 6.96 | 6.9633 | 0.0033
GEN-2020-062 | 05 - Southwest | 560022 | CRAWFISH_DR | 345 | 15.4693 | 15.4742 | 0.0049
GEN-2020-062 | 05 - Southwest | 560756 | CEILO-TAP-N | 115 | 0.4601 | 0.4602 | 0.0001
GEN-2020-062 | 05 - Southwest | 583280 | A12-02&13-0 | 115 | 1.041 | 1.042 | 0.001
GEN-2020-062 | 05 - Southwest | 583960 | G14034G1403 | 115 | 6.5148 | 6.5316 | 0.0168
GEN-2020-062 | 05 - Southwest | 599950 | LAMAR7 | 345 | 2.3192 | 2.3192 | 0
GEN-2020-062 | 05 - Southwest | 599951 | LAMAR | 345 | 12.9476 | 12.9476 | 0
GEN-2020-062 | 05 - Southwest | 599955 | PNM-DC6 | 230 | 9.746 | 10.2326 | 0.4866
GEN-2020-062 | 05 - Southwest | 599956 | PNM-DC7 | 345 | 14.6646 | 14.6646 | 0
GEN-2020-062 | 05 - Southwest | 599960 | EPTNP-D6 | 230 | 9.9763 | 9.9892 | 0.0129
GEN-2020-062 | 05 - Southwest | 599961 | EPTNP | 345 | 12.9476 | 12.9476 | 0
GEN-2020-062 | 05 - Southwest | 760494 | GEN-2017-14 | 230 | 7.4344 | 7.4443 | 0.0099
GEN-2020-062 | 05 - Southwest | 760498 | G17-146-TAP | 230 | 7.7219 | 7.7326 | 0.0107
GEN-2020-062 | 05 - Southwest | 762132 | GEN-2017-15 | 230 | 13.9298 | 13.9781 | 0.0483
GEN-2020-062 | 05 - Southwest | 763186 | GEN-2018-08 | 230 | 10.698 | 10.7075 | 0.0095
GEN-2020-062 | 05 - Southwest | 763483 | GEN-2019-00 | 230 | 8.7696 | 9.1563 | 0.3867
GEN-2020-062 | 05 - Southwest | 764825 | GEN-2020-01 | 230 | 5.5436 | 5.5509 | 0.0073
GEN-2020-062 | 05 - Southwest | 764890 | GEN-2020-06 | 230 | 6.444 | 7.0522 | 0.6082
GEN-2020-062 | 05 - Southwest | 764945 | G20-067-TAP | 345 | 8.6166 | 8.6182 | 0.0016
GEN-2020-060 | 05 - Southwest | 515458 | BORDER | 345 | 8.389 | 8.3898 | 0.0008
GEN-2020-060 | 05 - Southwest | 523959 | POTTER_CO | 230 | 23.0831 | 23.0856 | 0.0025
GEN-2020-060 | 05 - Southwest | 523961 | POTTER_CO | 345 | 13.9517 | 13.9531 | 0.0014
GEN-2020-060 | 05 - Southwest | 524044 | NICHOLS | 230 | 26.4067 | 26.409 | 0.0023
GEN-2020-060 | 05 - Southwest | 524365 | RANDALL | 230 | 14.6292 | 14.6304 | 0.0012
GEN-2020-060 | 05 - Southwest | 524414 | AMA_SOUTH | 115 | 16.8513 | 16.8521 | 0.0008
GEN-2020-060 | 05 - Southwest | 524415 | AMA_SOUTH | 230 | 13.6874 | 13.6888 | 0.0014
GEN-2020-060 | 05 - Southwest | 524770 | PLSNT_HILL | 230 | 6.7961 | 6.7966 | 0.0005
GEN-2020-060 | 05 - Southwest | 524875 | OASIS | 230 | 8.5034 | 8.5041 | 0.0007
GEN-2020-060 | 05 - Southwest | 524908 | ROOSEVELT | 115 | 11.4763 | 11.4769 | 0.0006
GEN-2020-060 | 05 - Southwest | 524909 | ROOSEVELT | 230 | 10.2315 | 10.2326 | 0.0011
GEN-2020-060 | 05 - Southwest | 525019 | MULSHVLY_TP | 115 | 5.9664 | 5.9668 | 0.0004
GEN-2020-060 | 05 - Southwest | 525056 | BC-EARTH | 115 | 8.264 | 8.2649 | 0.0009
GEN-2020-060 | 05 - Southwest | 525124 | HART_INDUST | 115 | 7.4975 | 7.4988 | 0.0013
GEN-2020-060 | 05 - Southwest | 525179 | TULIA_TP | 115 | 6.4675 | 6.4687 | 0.0012
GEN-2020-060 | 05 - Southwest | 525191 | KRESS_INT | 69 | 4.4999 | 4.5003 | 0.0004
GEN-2020-060 | 05 - Southwest | 525192 | KRESS_INT | 115 | 11.9449 | 11.9501 | 0.0052
GEN-2020-060 | 05 - Southwest | 525212 | SWISHER | 115 | 11.5214 | 11.5262 | 0.0048
GEN-2020-060 | 05 - Southwest | 525213 | SWISHER | 230 | 10.4328 | 10.4397 | 0.0069
GEN-2020-060 | 05 - Southwest | 525226 | KRS_RURL_TP | 115 | 6.4481 | 6.4501 | 0.002
GEN-2020-060 | 05 - Southwest | 525272 | KISER | 115 | 5.2749 | 5.277 | 0.0021
GEN-2020-060 | 05 - Southwest | 525291 | PLAINVW_TP | 69 | 6.4889 | 6.4905 | 0.0016
GEN-2020-060 | 05 - Southwest | 525298 | S_PLAINVEW | 69 | 2.5862 | 2.5865 | 0.0003
GEN-2020-060 | 05 - Southwest | 525325 | COX | 69 | 3.4204 | 3.4211 | 0.0007
GEN-2020-060 | 05 - Southwest | 525326 | COX | 115 | 6.2844 | 6.2881 | 0.0037
GEN-2020-060 | 05 - Southwest | 525351 | LH-AIKEN | 69 | 2.1494 | 2.1499 | 0.0005
GEN-2020-060 | 05 - Southwest | 525413 | LAMTON | 69 | 5.1716 | 5.1721 | 0.0005
GEN-2020-060 | 05 - Southwest | 525414 | LAMTON | 115 | 7.6222 | 7.6239 | 0.0017
GEN-2020-060 | 05 - Southwest | 525432 | SP-HALFWAY+ | 69 | 5.8694 | 5.8706 | 0.0012
GEN-2020-060 | 05 - Southwest | 525440 | LC-S_OLTON+ | 115 | 7.2042 | 7.2056 | 0.0014
GEN-2020-060 | 05 - Southwest | 525446 | RKYFORD_TP | 115 | 10.1366 | 10.1385 | 0.0019
GEN-2020-060 | 05 - Southwest | 525453 | HALE_CNTY | 69 | 6.9137 | 6.9155 | 0.0018
GEN-2020-060 | 05 - Southwest | 525454 | HALE_CNTY | 115 | 10.1868 | 10.1932 | 0.0064
GEN-2020-060 | 05 - Southwest | 525460 | NEWHART | 115 | 14.9596 | 14.9641 | 0.0045
GEN-2020-060 | 05 - Southwest | 525461 | NEWHART | 230 | 11.0132 | 11.0177 | 0.0045
GEN-2020-060 | 05 - Southwest | 525480 | PLANT_X | 115 | 19.3148 | 19.3204 | 0.0056
GEN-2020-060 | 05 - Southwest | 525481 | PLANT_X | 230 | 24.0255 | 24.0384 | 0.0129
GEN-2020-060 | 05 - Southwest | 525531 | TOLK | 230 | 32.1612 | 32.177 | 0.0158
GEN-2020-060 | 05 - Southwest | 525549 | TOLK | 345 | 16.4599 | 16.4645 | 0.0046
GEN-2020-060 | 05 - Southwest | 525585 | BLUECLDPOI | 230 | 11.1156 | 11.1174 | 0.0018
GEN-2020-060 | 05 - Southwest | 525586 | NEEDMORE | 230 | 11.1156 | 11.1174 | 0.0018
GEN-2020-060 | 05 - Southwest | 525636 | LAMB_CNTY | 115 | 8.5305 | 8.5317 | 0.0012
GEN-2020-060 | 05 - Southwest | 525637 | LAMB_CNTY | 230 | 5.5685 | 5.5692 | 0.0007
GEN-2020-060 | 05 - Southwest | 525723 | CNTYLINE_TP | 69 | 2.2033 | 2.2038 | 0.0005
GEN-2020-060 | 05 - Southwest | 525731 | SP-ABERNTHY | 69 | 3.0128 | 3.0138 | 0.001
GEN-2020-060 | 05 - Southwest | 525738 | HALECENTER | 69 | 2.4589 | 2.4595 | 0.0006
GEN-2020-060 | 05 - Southwest | 525745 | LH-HALECTR | 69 | 2.4312 | 2.4318 | 0.0006
GEN-2020-060 | 05 - Southwest | 525763 | CALLAHAN | 115 | 5.577 | 5.5822 | 0.0052
GEN-2020-060 | 05 - Southwest | 525779 | FLOYD_CNTY | 69 | 5.4072 | 5.4108 | 0.0036
GEN-2020-060 | 05 - Southwest | 525780 | FLOYD_CNTY | 115 | 6.2651 | 6.2729 | 0.0078
GEN-2020-060 | 05 - Southwest | 525790 | FLOYDADA_TP | 69 | 2.5184 | 2.5191 | 0.0007
GEN-2020-060 | 05 - Southwest | 525801 | LRNZ_MPT | 115 | 5.051 | 5.0581 | 0.0071
GEN-2020-060 | 05 - Southwest | 525803 | BLANCO | 115 | 5.0519 | 5.059 | 0.0071
GEN-2020-060 | 05 - Southwest | 525811 | LH-HARMONY | 69 | 4.3163 | 4.3185 | 0.0022
GEN-2020-060 | 05 - Southwest | 525816 | TUCO_INT2 | 69 | 4.6608 | 4.6632 | 0.0024
GEN-2020-060 | 05 - Southwest | 525826 | TUCO_INT | 69 | 7.8777 | 7.8845 | 0.0068
GEN-2020-060 | 05 - Southwest | 525828 | TUCO_INT | 115 | 19.6078 | 19.6784 | 0.0706
GEN-2020-060 | 05 - Southwest | 525830 | TUCO_INT | 230 | 23.0473 | 23.1605 | 0.1132
GEN-2020-060 | 05 - Southwest | 525832 | TUCO_INT | 345 | 15.6682 | 15.7032 | 0.035
GEN-2020-060 | 05 - Southwest | 525840 | ANTELOPE_1 | 230 | 22.8395 | 22.9505 | 0.111
GEN-2020-060 | 05 - Southwest | 525850 | ELK_CT1 | 345 | 15.4979 | 15.5321 | 0.0342
GEN-2020-060 | 05 - Southwest | 525853 | LH-WIL&ELN+ | 69 | 2.5428 | 2.5434 | 0.0006
GEN-2020-060 | 05 - Southwest | 525860 | SP-BECTON | 69 | 2.2564 | 2.2569 | 0.0005
GEN-2020-060 | 05 - Southwest | 525885 | SP-NEWDEAL | 69 | 3.3115 | 3.3127 | 0.0012
GEN-2020-060 | 05 - Southwest | 525892 | MONROE | 69 | 2.6502 | 2.651 | 0.0008
GEN-2020-060 | 05 - Southwest | 525906 | SP-ACUFF | 69 | 1.972 | 1.974 | 0.002
GEN-2020-060 | 05 - Southwest | 525915 | SP-CROSBY | 69 | 4.2693 | 4.2736 | 0.0043
GEN-2020-060 | 05 - Southwest | 525925 | CROSBY | 69 | 4.7877 | 4.7931 | 0.0054
GEN-2020-060 | 05 - Southwest | 525926 | CROSBY | 115 | 4.7176 | 4.7267 | 0.0091
GEN-2020-060 | 05 - Southwest | 525936 | LH-CROSBY | 69 | 3.3106 | 3.3132 | 0.0026
GEN-2020-060 | 05 - Southwest | 525943 | HENDRICKS | 69 | 3.2806 | 3.2831 | 0.0025
GEN-2020-060 | 05 - Southwest | 525957 | HALE_WNDCL1 | 230 | 10.7296 | 10.7515 | 0.0219
GEN-2020-060 | 05 - Southwest | 526075 | STANTON_E | 69 | 3.2178 | 3.223 | 0.0052
GEN-2020-060 | 05 - Southwest | 526076 | STANTON_W | 115 | 8.9337 | 8.9548 | 0.0211
GEN-2020-060 | 05 - Southwest | 526086 | SW_6786_N | 69 | 4.9556 | 4.9679 | 0.0123
GEN-2020-060 | 05 - Southwest | 526087 | SW_6786_S | 69 | 4.9556 | 4.9679 | 0.0123
GEN-2020-060 | 05 - Southwest | 526109 | SP-ERSKINE | 115 | 10.9779 | 11.0127 | 0.0348
GEN-2020-060 | 05 - Southwest | 526123 | VICKERS | 69 | 2.0804 | 2.0825 | 0.0021
GEN-2020-060 | 05 - Southwest | 526146 | INDIANA | 115 | 9.3113 | 9.3348 | 0.0235
GEN-2020-060 | 05 - Southwest | 526159 | CARLISLE | 69 | 2.5566 | 2.5578 | 0.0012
GEN-2020-060 | 05 - Southwest | 526160 | CARLISLE | 115 | 12.7616 | 12.8103 | 0.0487
GEN-2020-060 | 05 - Southwest | 526161 | CARLISLE | 230 | 10.3888 | 10.4424 | 0.0536
GEN-2020-060 | 05 - Southwest | 526162 | LP-DOUD_TP | 115 | 11.3142 | 11.3506 | 0.0364
GEN-2020-060 | 05 - Southwest | 526192 | MURPHY | 115 | 10.2423 | 10.2801 | 0.0378
GEN-2020-060 | 05 - Southwest | 526199 | SP-FRANKFRD | 115 | 9.4495 | 9.4883 | 0.0388
GEN-2020-060 | 05 - Southwest | 526205 | IVORY | 69 | 3.8971 | 3.9032 | 0.0061
GEN-2020-060 | 05 - Southwest | 526213 | ALLEN | 115 | 10.4388 | 10.4983 | 0.0595
GEN-2020-060 | 05 - Southwest | 526228 | BATTON_S | 69 | 2.6989 | 2.7019 | 0.003
GEN-2020-060 | 05 - Southwest | 526236 | LP-WHEELOCK | 115 | 8.4243 | 8.4631 | 0.0388
GEN-2020-060 | 05 - Southwest | 526243 | SP-QUAKER | 115 | 9.5395 | 9.5828 | 0.0433
GEN-2020-060 | 05 - Southwest | 526249 | ACCO | 69 | 3.1735 | 3.1776 | 0.0041
GEN-2020-060 | 05 - Southwest | 526256 | IVORY_TP | 69 | 3.8933 | 3.8994 | 0.0061
GEN-2020-060 | 05 - Southwest | 526267 | LUBBCK_STH | 69 | 4.3093 | 4.3168 | 0.0075
GEN-2020-060 | 05 - Southwest | 526268 | LUBBCK_STH | 115 | 17.613 | 17.8257 | 0.2127
GEN-2020-060 | 05 - Southwest | 526269 | LUBBCK_STH | 230 | 14.9549 | 15.2638 | 0.3089
GEN-2020-060 | 05 - Southwest | 526284 | PLANTERS | 69 | 5.7119 | 5.7282 | 0.0163
GEN-2020-060 | 05 - Southwest | 526297 | LUBBCK_EST | 69 | 7.8977 | 7.9284 | 0.0307
GEN-2020-060 | 05 - Southwest | 526298 | LUBBCK_EST | 115 | 14.4247 | 14.5991 | 0.1744
GEN-2020-060 | 05 - Southwest | 526299 | LUBBCK_EST | 230 | 11.0291 | 11.4866 | 0.4575
GEN-2020-060 | 05 - Southwest | 526310 | CLUTTER | 69 | 5.382 | 5.3965 | 0.0145
GEN-2020-060 | 05 - Southwest | 526337 | JONES | 230 | 16.5584 | 16.984 | 0.4256
GEN-2020-060 | 05 - Southwest | 526434 | SUNDOWN | 115 | 10.802 | 10.8088 | 0.0068
GEN-2020-060 | 05 - Southwest | 526435 | SUNDOWN | 230 | 11.0227 | 11.0455 | 0.0228
GEN-2020-060 | 05 - Southwest | 526460 | AMOCO_SS | 230 | 9.7611 | 9.7761 | 0.015
GEN-2020-060 | 05 - Southwest | 526475 | YUMA_INT | 115 | 10.6918 | 10.7227 | 0.0309
GEN-2020-060 | 05 - Southwest | 526524 | WOLFFORTH | 115 | 11.2652 | 11.2957 | 0.0305
GEN-2020-060 | 05 - Southwest | 526525 | WOLFFORTH | 230 | 12.5581 | 12.6605 | 0.1024
GEN-2020-060 | 05 - Southwest | 526562 | SLATON | 69 | 2.4664 | 2.4694 | 0.003
GEN-2020-060 | 05 - Southwest | 526569 | SP-SLATON | 69 | 1.2112 | 1.2119 | 0.0007
GEN-2020-060 | 05 - Southwest | 526576 | SOUTHLAND | 69 | 1.3841 | 1.3849 | 0.0008
GEN-2020-060 | 05 - Southwest | 526602 | WOODROW | 115 | 9.1224 | 9.1802 | 0.0578
GEN-2020-060 | 05 - Southwest | 526655 | LYNN_CNTY | 69 | 4.5689 | 4.578 | 0.0091
GEN-2020-060 | 05 - Southwest | 526656 | LYNN_CNTY | 115 | 5.9335 | 5.9591 | 0.0256
GEN-2020-060 | 05 - Southwest | 526676 | GRASSLAND | 115 | 6.8586 | 6.8934 | 0.0348
GEN-2020-060 | 05 - Southwest | 526677 | GRASSLAND | 230 | 5.9668 | 6.0206 | 0.0538
GEN-2020-060 | 05 - Southwest | 526679 | CIRRUS_WND | 230 | 4.6751 | 4.7081 | 0.033
GEN-2020-060 | 05 - Southwest | 526693 | GRAHAM | 69 | 3.3505 | 3.3554 | 0.0049
GEN-2020-060 | 05 - Southwest | 526694 | GRAHAM | 115 | 2.8161 | 2.8219 | 0.0058
GEN-2020-060 | 05 - Southwest | 526736 | TERRY_CNTY | 115 | 10.7218 | 10.7284 | 0.0066
GEN-2020-060 | 05 - Southwest | 526935 | YOAKUM | 230 | 20.6001 | 20.6089 | 0.0088
GEN-2020-060 | 05 - Southwest | 526936 | YOAKUM_345 | 345 | 11.5766 | 11.5801 | 0.0035
GEN-2020-060 | 05 - Southwest | 527656 | CROSSROADS | 345 | 12.7007 | 12.7018 | 0.0011
GEN-2020-060 | 05 - Southwest | 560022 | CRAWFISH_DR | 345 | 15.4411 | 15.4742 | 0.0331
GEN-2020-060 | 05 - Southwest | 599955 | PNM-DC6 | 230 | 10.2315 | 10.2326 | 0.0011
GEN-2020-060 | 05 - Southwest | 760498 | G17-146-TAP | 230 | 7.7318 | 7.7326 | 0.0008
GEN-2020-060 | 05 - Southwest | 762132 | GEN-2017-15 | 230 | 13.9756 | 13.9781 | 0.0025
GEN-2020-060 | 05 - Southwest | 762216 | G17-151TAP | 345 | 8.9256 | 8.9343 | 0.0087
GEN-2020-060 | 05 - Southwest | 762467 | G18-015-TAP | 345 | 9.4348 | 9.4398 | 0.005
GEN-2020-060 | 05 - Southwest | 763186 | GEN-2018-08 | 230 | 10.7033 | 10.7075 | 0.0042
GEN-2020-060 | 05 - Southwest | 763215 | G18-092-PRO | 345 | 9.3657 | 9.3698 | 0.0041
GEN-2020-060 | 05 - Southwest | 763483 | GEN-2019-00 | 230 | 9.1555 | 9.1563 | 0.0008
GEN-2020-060 | 05 - Southwest | 764825 | GEN-2020-01 | 230 | 5.5502 | 5.5509 | 0.0007
GEN-2020-060 | 05 - Southwest | 764875 | GEN-2020-06 | 230 | 10.8535 | 11.3113 | 0.4578
GEN-2020-060 | 05 - Southwest | 764935 | GEN-2020-06 | 345 | 7.0137 | 7.0161 | 0.0024
GEN-2020-060 | 05 - Southwest | 764945 | G20-067-TAP | 345 | 8.6144 | 8.6182 | 0.0038
GEN-2020-060 | 05 - Southwest | 764950 | GEN-2020-06 | 345 | 8.5721 | 8.5759 | 0.0038
GEN-2020-059 | 05 - Southwest | 511553 | CHISHOLM7 | 345 | 12.7407 | 12.7423 | 0.0016
GEN-2020-059 | 05 - Southwest | 515458 | BORDER | 345 | 8.3888 | 8.3898 | 0.001
GEN-2020-059 | 05 - Southwest | 523097 | HITCHLAND | 345 | 14.6253 | 14.6258 | 0.0005
GEN-2020-059 | 05 - Southwest | 523959 | POTTER_CO | 230 | 23.0818 | 23.0856 | 0.0038
GEN-2020-059 | 05 - Southwest | 523961 | POTTER_CO | 345 | 13.9487 | 13.9531 | 0.0044
GEN-2020-059 | 05 - Southwest | 524296 | SPNSPUR_WND | 345 | 5.6849 | 5.6855 | 0.0006
GEN-2020-059 | 05 - Southwest | 524909 | ROOSEVELT | 230 | 10.2283 | 10.2326 | 0.0043
GEN-2020-059 | 05 - Southwest | 525213 | SWISHER | 230 | 10.4367 | 10.4397 | 0.003
GEN-2020-059 | 05 - Southwest | 525481 | PLANT_X | 230 | 24.0148 | 24.0384 | 0.0236
GEN-2020-059 | 05 - Southwest | 525531 | TOLK | 230 | 32.13 | 32.177 | 0.047
GEN-2020-059 | 05 - Southwest | 525549 | TOLK | 345 | 16.4366 | 16.4645 | 0.0279
GEN-2020-059 | 05 - Southwest | 525584 | BLUECLDCOL | 230 | 10.5043 | 10.5131 | 0.0088
GEN-2020-059 | 05 - Southwest | 525585 | BLUECLDPOI | 230 | 11.1076 | 11.1174 | 0.0098
GEN-2020-059 | 05 - Southwest | 525586 | NEEDMORE | 230 | 11.1076 | 11.1174 | 0.0098
GEN-2020-059 | 05 - Southwest | 525637 | LAMB_CNTY | 230 | 5.5677 | 5.5692 | 0.0015
GEN-2020-059 | 05 - Southwest | 525828 | TUCO_INT | 115 | 19.6687 | 19.6784 | 0.0097
GEN-2020-059 | 05 - Southwest | 525830 | TUCO_INT | 230 | 23.1294 | 23.1605 | 0.0311
GEN-2020-059 | 05 - Southwest | 525832 | TUCO_INT | 345 | 15.6714 | 15.7032 | 0.0318
GEN-2020-059 | 05 - Southwest | 525840 | ANTELOPE_1 | 230 | 22.92 | 22.9505 | 0.0305
GEN-2020-059 | 05 - Southwest | 525850 | ELK_CT1 | 345 | 15.5011 | 15.5321 | 0.031
GEN-2020-059 | 05 - Southwest | 525957 | HALE_WNDCL1 | 230 | 10.7455 | 10.7515 | 0.006
GEN-2020-059 | 05 - Southwest | 526161 | CARLISLE | 230 | 10.4357 | 10.4424 | 0.0067
GEN-2020-059 | 05 - Southwest | 526337 | JONES | 230 | 16.9759 | 16.984 | 0.0081
GEN-2020-059 | 05 - Southwest | 526434 | SUNDOWN | 115 | 10.801 | 10.8088 | 0.0078
GEN-2020-059 | 05 - Southwest | 526435 | SUNDOWN | 230 | 11.0292 | 11.0455 | 0.0163
GEN-2020-059 | 05 - Southwest | 526460 | AMOCO_SS | 230 | 9.7602 | 9.7761 | 0.0159
GEN-2020-059 | 05 - Southwest | 526525 | WOLFFORTH | 230 | 12.6503 | 12.6605 | 0.0102
GEN-2020-059 | 05 - Southwest | 526736 | TERRY_CNTY | 115 | 10.7195 | 10.7284 | 0.0089
GEN-2020-059 | 05 - Southwest | 526784 | AMOCOWASSON | 230 | 15.9093 | 15.9881 | 0.0788
GEN-2020-059 | 05 - Southwest | 526792 | PRENTICE | 115 | 6.0473 | 6.0516 | 0.0043
GEN-2020-059 | 05 - Southwest | 526928 | PLAINS_INT | 115 | 10.074 | 10.0903 | 0.0163
GEN-2020-059 | 05 - Southwest | 526934 | YOAKUM | 115 | 19.4667 | 19.5335 | 0.0668
GEN-2020-059 | 05 - Southwest | 526935 | YOAKUM | 230 | 20.3985 | 20.6089 | 0.2104
GEN-2020-059 | 05 - Southwest | 526936 | YOAKUM_345 | 345 | 11.1557 | 11.5801 | 0.4244
GEN-2020-059 | 05 - Southwest | 526944 | LG-PLAINS | 115 | 7.9313 | 7.9407 | 0.0094
GEN-2020-059 | 05 - Southwest | 527000 | GAINES_PLNT | 345 | 12.4253 | 12.548 | 0.1227
GEN-2020-059 | 05 - Southwest | 527009 | BRU_SUB | 230 | 16.0082 | 16.1115 | 0.1033
GEN-2020-059 | 05 - Southwest | 527010 | OXYBRU | 230 | 15.8553 | 15.9566 | 0.1013
GEN-2020-059 | 05 - Southwest | 527011 | XTO_MAHONEY | 230 | 15.6746 | 15.7661 | 0.0915
GEN-2020-059 | 05 - Southwest | 527018 | BENNETT | 115 | 13.8533 | 13.8773 | 0.024
GEN-2020-059 | 05 - Southwest | 527020 | SIDEWINDER | 345 | 12.9505 | 13.1087 | 0.1582
GEN-2020-059 | 05 - Southwest | 527027 | INK_BASIN | 115 | 13.0554 | 13.0796 | 0.0242
GEN-2020-059 | 05 - Southwest | 527028 | INK_BASIN | 230 | 11.4529 | 11.5066 | 0.0537
GEN-2020-059 | 05 - Southwest | 527030 | ALRDCRTZ_TP | 115 | 12.2008 | 12.2202 | 0.0194
GEN-2020-059 | 05 - Southwest | 527041 | ARCO_TP | 115 | 13.7579 | 13.7818 | 0.0239
GEN-2020-059 | 05 - Southwest | 527047 | OXY_WILRD1 | 115 | 10.9424 | 10.9574 | 0.015
GEN-2020-059 | 05 - Southwest | 527062 | SHELL_CO2 | 115 | 16.7977 | 16.8291 | 0.0314
GEN-2020-059 | 05 - Southwest | 527130 | DENVER_N | 115 | 22.6705 | 22.723 | 0.0525
GEN-2020-059 | 05 - Southwest | 527136 | DENVER_S | 115 | 22.6705 | 22.723 | 0.0525
GEN-2020-059 | 05 - Southwest | 527146 | MUSTANG | 115 | 24.2322 | 24.2882 | 0.056
GEN-2020-059 | 05 - Southwest | 527149 | MUSTANG | 230 | 18.2322 | 18.3209 | 0.0887
GEN-2020-059 | 05 - Southwest | 527151 | GS-MUSTANG | 230 | 18.2322 | 18.3209 | 0.0887
GEN-2020-059 | 05 - Southwest | 527194 | LG-PLSHILL | 115 | 8.0004 | 8.0078 | 0.0074
GEN-2020-059 | 05 - Southwest | 527202 | SEAGRAVES | 115 | 9.2101 | 9.2189 | 0.0088
GEN-2020-059 | 05 - Southwest | 527275 | SEMINOLE | 115 | 14.7506 | 14.7752 | 0.0246
GEN-2020-059 | 05 - Southwest | 527276 | SEMINOLE | 230 | 8.2569 | 8.2736 | 0.0167
GEN-2020-059 | 05 - Southwest | 527363 | HIGG | 115 | 10.4291 | 10.4399 | 0.0108
GEN-2020-059 | 05 - Southwest | 527483 | CHAVES_CNTY | 230 | 4.5719 | 4.5767 | 0.0048
GEN-2020-059 | 05 - Southwest | 527599 | SAGA_SDCOL | 345 | 11.0246 | 11.0808 | 0.0562
GEN-2020-059 | 05 - Southwest | 527600 | SAGA_SMEAS | 345 | 11.0246 | 11.0808 | 0.0562
GEN-2020-059 | 05 - Southwest | 527610 | SAGA_SCOL | 345 | 11.0246 | 11.0808 | 0.0562
GEN-2020-059 | 05 - Southwest | 527654 | RSVLT_CC_W | 345 | 9.2859 | 9.325 | 0.0391
GEN-2020-059 | 05 - Southwest | 527655 | RSVLT_CC_E | 345 | 10.7883 | 10.8431 | 0.0548
GEN-2020-059 | 05 - Southwest | 527656 | CROSSROADS | 345 | 12.6237 | 12.7018 | 0.0781
GEN-2020-059 | 05 - Southwest | 527666 | RSVLT_COL1 | 345 | 9.2859 | 9.325 | 0.0391
GEN-2020-059 | 05 - Southwest | 527667 | RSVLT_COL2 | 345 | 9.2859 | 9.325 | 0.0391
GEN-2020-059 | 05 - Southwest | 527793 | EDDY_STH | 115 | 12.3812 | 12.4148 | 0.0336
GEN-2020-059 | 05 - Southwest | 527798 | EDDY_NTH | 115 | 12.3812 | 12.4148 | 0.0336
GEN-2020-059 | 05 - Southwest | 527799 | EDDY_NORTH | 230 | 9.9454 | 9.9892 | 0.0438
GEN-2020-059 | 05 - Southwest | 527802 | EDDY_CNTY | 345 | 7.9736 | 8.026 | 0.0524
GEN-2020-059 | 05 - Southwest | 527864 | CUNNINHAM | 115 | 28.9606 | 29.042 | 0.0814
GEN-2020-059 | 05 - Southwest | 527865 | CUNNIGHM_N | 230 | 18.5165 | 18.6259 | 0.1094
GEN-2020-059 | 05 - Southwest | 527867 | CUNNIGHM_S | 230 | 18.5165 | 18.6259 | 0.1094
GEN-2020-059 | 05 - Southwest | 527891 | HOBBS_INT | 115 | 33.095 | 33.199 | 0.104
GEN-2020-059 | 05 - Southwest | 527894 | HOBBS_INT | 230 | 20.7449 | 20.9035 | 0.1586
GEN-2020-059 | 05 - Southwest | 527896 | HOBBS_INT | 345 | 16.1988 | 16.6041 | 0.4053
GEN-2020-059 | 05 - Southwest | 527930 | PCA | 115 | 12.4501 | 12.4891 | 0.039
GEN-2020-059 | 05 - Southwest | 527961 | POTASH_JCT | 69 | 10.0733 | 10.0901 | 0.0168
GEN-2020-059 | 05 - Southwest | 527962 | POTASH_JCT | 115 | 18.3347 | 18.4308 | 0.0961
GEN-2020-059 | 05 - Southwest | 527963 | POTASH_JCT | 230 | 7.7914 | 7.8188 | 0.0274
GEN-2020-059 | 05 - Southwest | 527965 | KIOWA | 345 | 10.1351 | 10.2483 | 0.1132
GEN-2020-059 | 05 - Southwest | 527966 | KIOWA | 115 | 18.3213 | 18.4184 | 0.0971
GEN-2020-059 | 05 - Southwest | 527999 | INTREPDW_TP | 115 | 14.7254 | 14.7878 | 0.0624
GEN-2020-059 | 05 - Southwest | 528013 | PHANTOM | 115 | 13.9954 | 14.0685 | 0.0731
GEN-2020-059 | 05 - Southwest | 528015 | PHANTOM | 345 | 6.2146 | 6.259 | 0.0444
GEN-2020-059 | 05 - Southwest | 528016 | SAND_DUNES | 115 | 7.6973 | 7.7171 | 0.0198
GEN-2020-059 | 05 - Southwest | 528018 | RED_BLUFF | 115 | 10.7172 | 10.7584 | 0.0412
GEN-2020-059 | 05 - Southwest | 528020 | BOPCO_PKRLK | 115 | 13.7578 | 13.8284 | 0.0706
GEN-2020-059 | 05 - Southwest | 528024 | RR_SVC_HV | 115 | 14.7856 | 14.8681 | 0.0825
GEN-2020-059 | 05 - Southwest | 528025 | RDRUNNER | 115 | 14.7856 | 14.8681 | 0.0825
GEN-2020-059 | 05 - Southwest | 528027 | RDRUNNER | 345 | 10.2297 | 10.3653 | 0.1356
GEN-2020-059 | 05 - Southwest | 528040 | BATTLE_AXE | 115 | 3.2631 | 3.267 | 0.0039
GEN-2020-059 | 05 - Southwest | 528095 | 7-RIVERS | 230 | 6.6346 | 6.6545 | 0.0199
GEN-2020-059 | 05 - Southwest | 528160 | CARLSBAD | 115 | 11.8312 | 11.8661 | 0.0349
GEN-2020-059 | 05 - Southwest | 528182 | NORTH_LOVNG | 115 | 13.1827 | 13.2437 | 0.061
GEN-2020-059 | 05 - Southwest | 528185 | N_LOVING | 345 | 7.2487 | 7.3067 | 0.058
GEN-2020-059 | 05 - Southwest | 528192 | SOUTH_LOVNG | 115 | 9.8114 | 9.8454 | 0.034
GEN-2020-059 | 05 - Southwest | 528193 | BLACKRIVER | 115 | 10.8229 | 10.8642 | 0.0413
GEN-2020-059 | 05 - Southwest | 528194 | MALAGABEND | 115 | 8.2097 | 8.2342 | 0.0245
GEN-2020-059 | 05 - Southwest | 528195 | AGAVE_PDURO | 115 | 8.35 | 8.3744 | 0.0244
GEN-2020-059 | 05 - Southwest | 528222 | CHINA_DRAW | 115 | 11.628 | 11.678 | 0.05
GEN-2020-059 | 05 - Southwest | 528223 | CHINA_DRAW | 345 | 6.3793 | 6.425 | 0.0457
GEN-2020-059 | 05 - Southwest | 528226 | HOPI_SUB | 115 | 7.5044 | 7.5199 | 0.0155
GEN-2020-059 | 05 - Southwest | 528228 | WOOD_DRAW | 115 | 8.5576 | 8.5846 | 0.027
GEN-2020-059 | 05 - Southwest | 528230 | AGAVE_RHILL | 115 | 13.154 | 13.2193 | 0.0653
GEN-2020-059 | 05 - Southwest | 528231 | AGAVE_RHIL2 | 115 | 12.3273 | 12.3846 | 0.0573
GEN-2020-059 | 05 - Southwest | 528232 | OCHOA | 115 | 12.3901 | 12.448 | 0.0579
GEN-2020-059 | 05 - Southwest | 528235 | WOLFCAMP_TP | 115 | 12.9483 | 13.0106 | 0.0623
GEN-2020-059 | 05 - Southwest | 528239 | CUSTERMTN | 115 | 7.9696 | 7.9871 | 0.0175
GEN-2020-059 | 05 - Southwest | 528240 | PONDEROSA | 115 | 4.1201 | 4.1248 | 0.0047
GEN-2020-059 | 05 - Southwest | 528325 | LE-WAITS | 115 | 8.9319 | 8.942 | 0.0101
GEN-2020-059 | 05 - Southwest | 528333 | LE-WEST_SUB | 115 | 8.9091 | 8.9164 | 0.0073
GEN-2020-059 | 05 - Southwest | 528334 | LE-NRTH_INT | 115 | 8.8469 | 8.8542 | 0.0073
GEN-2020-059 | 05 - Southwest | 528348 | BUCKEYE_TP | 115 | 8.2979 | 8.3045 | 0.0066
GEN-2020-059 | 05 - Southwest | 528353 | MADDOXG23 | 115 | 27.931 | 28.0021 | 0.0711
GEN-2020-059 | 05 - Southwest | 528355 | MADDOX | 115 | 27.931 | 28.0021 | 0.0711
GEN-2020-059 | 05 - Southwest | 528392 | PEARLE | 115 | 6.407 | 6.4119 | 0.0049
GEN-2020-059 | 05 - Southwest | 528394 | QUAHADA | 115 | 8.1917 | 8.2033 | 0.0116
GEN-2020-059 | 05 - Southwest | 528433 | BENSING | 115 | 8.1013 | 8.1075 | 0.0062
GEN-2020-059 | 05 - Southwest | 528434 | MILLEN_TPW | 115 | 11.942 | 11.9556 | 0.0136
GEN-2020-059 | 05 - Southwest | 528435 | MILLEN | 115 | 11.942 | 11.9556 | 0.0136
GEN-2020-059 | 05 - Southwest | 528436 | MILLEN_TPE | 115 | 11.942 | 11.9556 | 0.0136
GEN-2020-059 | 05 - Southwest | 528491 | MONUMENT | 115 | 16.2075 | 16.2332 | 0.0257
GEN-2020-059 | 05 - Southwest | 528540 | WHITTEN | 115 | 7.9582 | 7.9737 | 0.0155
GEN-2020-059 | 05 - Southwest | 528568 | MONUMNT_TP | 115 | 10.5066 | 10.5189 | 0.0123
GEN-2020-059 | 05 - Southwest | 528602 | ANDREWS | 115 | 14.8529 | 14.9121 | 0.0592
GEN-2020-059 | 05 - Southwest | 528603 | NA_ENRICH | 115 | 13.6629 | 13.7109 | 0.048
GEN-2020-059 | 05 - Southwest | 528604 | ANDREWS | 345 | 9.0461 | 9.1206 | 0.0745
GEN-2020-059 | 05 - Southwest | 528626 | LE-PLNSINT | 69 | 3.6418 | 3.6431 | 0.0013
GEN-2020-059 | 05 - Southwest | 560022 | CRAWFISH_DR | 345 | 15.4441 | 15.4742 | 0.0301
GEN-2020-059 | 05 - Southwest | 587990 | GEN-2016-12 | 115 | 14.5273 | 14.6069 | 0.0796
GEN-2020-059 | 05 - Southwest | 588460 | A16-008SUB | 115 | 13.0554 | 13.0796 | 0.0242
GEN-2020-059 | 05 - Southwest | 599960 | EPTNP-D6 | 230 | 9.9454 | 9.9892 | 0.0438
GEN-2020-059 | 05 - Southwest | 761355 | GEN-2017-23 | 230 | 14.0509 | 14.1234 | 0.0725
GEN-2020-059 | 05 - Southwest | 762132 | GEN-2017-15 | 230 | 13.9704 | 13.9781 | 0.0077
GEN-2020-059 | 05 - Southwest | 762216 | G17-151TAP | 345 | 8.9264 | 8.9343 | 0.0079
GEN-2020-059 | 05 - Southwest | 762442 | G18-004-TAP | 115 | 24.018 | 24.0705 | 0.0525
GEN-2020-059 | 05 - Southwest | 762467 | G18-015-TAP | 345 | 9.4352 | 9.4398 | 0.0046
GEN-2020-059 | 05 - Southwest | 763215 | G18-092-PRO | 345 | 9.3661 | 9.3698 | 0.0037
GEN-2020-059 | 05 - Southwest | 763516 | GEN-2019-01 | 345 | 10.3467 | 10.7109 | 0.3642
GEN-2020-059 | 05 - Southwest | 764840 | GEN-2020-05 | 345 | 10.6598 | 11.4535 | 0.7937
GEN-2020-059 | 05 - Southwest | 764866 | G20-059-TAP | 345 | 10.7395 | 11.5328 | 0.7933
GEN-2020-059 | 05 - Southwest | 764935 | GEN-2020-06 | 345 | 6.9564 | 7.0161 | 0.0597
GEN-2020-059 | 05 - Southwest | 764945 | G20-067-TAP | 345 | 8.5253 | 8.6182 | 0.0929
GEN-2020-059 | 05 - Southwest | 764948 | G20-068-SS1 | 345 | 6.8488 | 6.9074 | 0.0586
GEN-2020-059 | 05 - Southwest | 764949 | G20-068-SS2 | 345 | 6.8468 | 6.9054 | 0.0586
GEN-2020-059 | 05 - Southwest | 764950 | GEN-2020-06 | 345 | 8.4839 | 8.5759 | 0.092
GEN-2020-017 | 05 - Southwest | 511553 | CHISHOLM7 | 345 | 12.7416 | 12.7423 | 0.0007
GEN-2020-017 | 05 - Southwest | 511557 | CHISHOLM6 | 230 | 12.2697 | 12.27 | 0.0003
GEN-2020-017 | 05 - Southwest | 515458 | BORDER | 345 | 8.3895 | 8.3898 | 0.0003
GEN-2020-017 | 05 - Southwest | 515554 | BVRCNTY7 | 345 | 14.525 | 14.5253 | 0.0003
GEN-2020-017 | 05 - Southwest | 516059 | BECKHAM7 | 345 | 12.6405 | 12.6411 | 0.0006
GEN-2020-017 | 05 - Southwest | 523095 | HITCHLAND | 230 | 14.4144 | 14.4147 | 0.0003
GEN-2020-017 | 05 - Southwest | 523097 | HITCHLAND | 345 | 14.6254 | 14.6258 | 0.0004
GEN-2020-017 | 05 - Southwest | 523101 | NOBLE_WND | 345 | 14.5672 | 14.5676 | 0.0004
GEN-2020-017 | 05 - Southwest | 523112 | NOVUS1 | 345 | 14.3398 | 14.3403 | 0.0005
GEN-2020-017 | 05 - Southwest | 523323 | MCDWL_CREEK | 230 | 9.0465 | 9.047 | 0.0005
GEN-2020-017 | 05 - Southwest | 523823 | CARPENTER | 345 | 6.6928 | 6.6928 | 0
GEN-2020-017 | 05 - Southwest | 523869 | CHAN+TASCOS | 230 | 4.2648 | 4.2649 | 0.0001
GEN-2020-017 | 05 - Southwest | 523959 | POTTER_CO | 230 | 23.0811 | 23.0856 | 0.0045
GEN-2020-017 | 05 - Southwest | 523961 | POTTER_CO | 345 | 13.9488 | 13.9531 | 0.0043
GEN-2020-017 | 05 - Southwest | 523979 | HARRNG_EST | 230 | 27.3043 | 27.3078 | 0.0035
GEN-2020-017 | 05 - Southwest | 524010 | ROLLHILLS | 230 | 20.5315 | 20.5341 | 0.0026
GEN-2020-017 | 05 - Southwest | 524044 | NICHOLS | 230 | 26.4058 | 26.409 | 0.0032
GEN-2020-017 | 05 - Southwest | 524267 | BUSHLAND | 230 | 10.127 | 10.1285 | 0.0015
GEN-2020-017 | 05 - Southwest | 524296 | SPNSPUR_WND | 345 | 5.6849 | 5.6855 | 0.0006
GEN-2020-017 | 05 - Southwest | 524299 | SPNSPUR_COL | 345 | 5.6849 | 5.6855 | 0.0006
GEN-2020-017 | 05 - Southwest | 524365 | RANDALL | 230 | 14.6291 | 14.6304 | 0.0013
GEN-2020-017 | 05 - Southwest | 524414 | AMA_SOUTH | 115 | 16.8512 | 16.8521 | 0.0009
GEN-2020-017 | 05 - Southwest | 524415 | AMA_SOUTH | 230 | 13.6875 | 13.6888 | 0.0013
GEN-2020-017 | 05 - Southwest | 524502 | NORTON | 115 | 2.9235 | 2.9236 | 0.0001
GEN-2020-017 | 05 - Southwest | 524619 | DFSMTH_EST | 115 | 11.9939 | 11.9967 | 0.0028
GEN-2020-017 | 05 - Southwest | 524622 | DFSMTH_WST | 115 | 11.9945 | 11.9973 | 0.0028
GEN-2020-017 | 05 - Southwest | 524623 | DEAFSMITH | 230 | 8.0122 | 8.0147 | 0.0025
GEN-2020-017 | 05 - Southwest | 524669 | DS-#20 | 115 | 6.3351 | 6.3363 | 0.0012
GEN-2020-017 | 05 - Southwest | 524746 | CASTRO_CNTY | 115 | 9.8232 | 9.8259 | 0.0027
GEN-2020-017 | 05 - Southwest | 524764 | NORRIS_TP | 115 | 11.7118 | 11.7163 | 0.0045
GEN-2020-017 | 05 - Southwest | 524768 | PLSNT_HILL | 115 | 10.8091 | 10.8127 | 0.0036
GEN-2020-017 | 05 - Southwest | 524770 | PLSNT_HILL | 230 | 6.7936 | 6.7966 | 0.003
GEN-2020-017 | 05 - Southwest | 524773 | E_CLOVIS | 115 | 9.1581 | 9.1607 | 0.0026
GEN-2020-017 | 05 - Southwest | 524776 | N_CLOVIS_TP | 115 | 7.6206 | 7.6223 | 0.0017
GEN-2020-017 | 05 - Southwest | 524797 | PERIMETER | 115 | 6.6871 | 6.6884 | 0.0013
GEN-2020-017 | 05 - Southwest | 524821 | CURRY | 69 | 4.455 | 4.4554 | 0.0004
GEN-2020-017 | 05 - Southwest | 524822 | CURRY | 115 | 11.7461 | 11.7506 | 0.0045
GEN-2020-017 | 05 - Southwest | 524831 | FE-HOLLAND | 115 | 9.4531 | 9.4559 | 0.0028
GEN-2020-017 | 05 - Southwest | 524838 | FE-CLOVIS2+ | 115 | 11.0681 | 11.0721 | 0.004
GEN-2020-017 | 05 - Southwest | 524863 | FE-CHZPLT | 115 | 8.2067 | 8.2088 | 0.0021
GEN-2020-017 | 05 - Southwest | 524874 | OASIS | 115 | 10.4056 | 10.409 | 0.0034
GEN-2020-017 | 05 - Southwest | 524875 | OASIS | 230 | 8.4998 | 8.5041 | 0.0043
GEN-2020-017 | 05 - Southwest | 524885 | SN_JUAN_TAP | 230 | 4.9704 | 4.971 | 0.0006
GEN-2020-017 | 05 - Southwest | 524889 | SN_JUAN_WND | 230 | 4.7433 | 4.7438 | 0.0005
GEN-2020-017 | 05 - Southwest | 524908 | ROOSEVELT | 115 | 11.4725 | 11.4769 | 0.0044
GEN-2020-017 | 05 - Southwest | 524909 | ROOSEVELT | 230 | 10.2253 | 10.2326 | 0.0073
GEN-2020-017 | 05 - Southwest | 524923 | PORTALES | 69 | 7.6655 | 7.6666 | 0.0011
GEN-2020-017 | 05 - Southwest | 524924 | PORTALES | 115 | 7.73 | 7.7319 | 0.0019
GEN-2020-017 | 05 - Southwest | 524935 | KILGORE | 115 | 6.2661 | 6.2673 | 0.0012
GEN-2020-017 | 05 - Southwest | 524977 | GREYHOUND | 115 | 5.7864 | 5.7875 | 0.0011
GEN-2020-017 | 05 - Southwest | 525018 | MULESHVALLY | 115 | 5.5541 | 5.5564 | 0.0023
GEN-2020-017 | 05 - Southwest | 525019 | MULSHVLY_TP | 115 | 5.9642 | 5.9668 | 0.0026
GEN-2020-017 | 05 - Southwest | 525027 | BAILEYCO | 69 | 5.2785 | 5.2797 | 0.0012
GEN-2020-017 | 05 - Southwest | 525028 | BAILEYCO | 115 | 5.8177 | 5.8202 | 0.0025
GEN-2020-017 | 05 - Southwest | 525050 | BC-KELLEY | 115 | 7.7821 | 7.7852 | 0.0031
GEN-2020-017 | 05 - Southwest | 525056 | BC-EARTH | 115 | 8.2608 | 8.2649 | 0.0041
GEN-2020-017 | 05 - Southwest | 525124 | HART_INDUST | 115 | 7.4972 | 7.4988 | 0.0016
GEN-2020-017 | 05 - Southwest | 525179 | TULIA_TP | 115 | 6.4681 | 6.4687 | 0.0006
GEN-2020-017 | 05 - Southwest | 525191 | KRESS_INT | 69 | 4.5001 | 4.5003 | 0.0002
GEN-2020-017 | 05 - Southwest | 525192 | KRESS_INT | 115 | 11.9478 | 11.9501 | 0.0023
GEN-2020-017 | 05 - Southwest | 525212 | SWISHER | 115 | 11.5242 | 11.5262 | 0.002
GEN-2020-017 | 05 - Southwest | 525213 | SWISHER | 230 | 10.4371 | 10.4397 | 0.0026
GEN-2020-017 | 05 - Southwest | 525226 | KRS_RURL_TP | 115 | 6.4495 | 6.4501 | 0.0006
GEN-2020-017 | 05 - Southwest | 525272 | KISER | 115 | 5.2765 | 5.277 | 0.0005
GEN-2020-017 | 05 - Southwest | 525291 | PLAINVW_TP | 69 | 6.4898 | 6.4905 | 0.0007
GEN-2020-017 | 05 - Southwest | 525298 | S_PLAINVEW | 69 | 2.5864 | 2.5865 | 0.0001
GEN-2020-017 | 05 - Southwest | 525325 | COX | 69 | 3.421 | 3.4211 | 0.0001
GEN-2020-017 | 05 - Southwest | 525326 | COX | 115 | 6.2874 | 6.2881 | 0.0007
GEN-2020-017 | 05 - Southwest | 525393 | ROCKYFORD | 115 | 9.046 | 9.0525 | 0.0065
GEN-2020-017 | 05 - Southwest | 525413 | LAMTON | 69 | 5.1714 | 5.1721 | 0.0007
GEN-2020-017 | 05 - Southwest | 525414 | LAMTON | 115 | 7.6215 | 7.6239 | 0.0024
GEN-2020-017 | 05 - Southwest | 525432 | SP-HALFWAY+ | 69 | 5.8701 | 5.8706 | 0.0005
GEN-2020-017 | 05 - Southwest | 525440 | LC-S_OLTON+ | 115 | 7.2027 | 7.2056 | 0.0029
GEN-2020-017 | 05 - Southwest | 525446 | RKYFORD_TP | 115 | 10.1303 | 10.1385 | 0.0082
GEN-2020-017 | 05 - Southwest | 525453 | HALE_CNTY | 69 | 6.9147 | 6.9155 | 0.0008
GEN-2020-017 | 05 - Southwest | 525454 | HALE_CNTY | 115 | 10.1906 | 10.1932 | 0.0026
GEN-2020-017 | 05 - Southwest | 525460 | NEWHART | 115 | 14.9593 | 14.9641 | 0.0048
GEN-2020-017 | 05 - Southwest | 525461 | NEWHART | 230 | 11.0131 | 11.0177 | 0.0046
GEN-2020-017 | 05 - Southwest | 525480 | PLANT_X | 115 | 19.2854 | 19.3204 | 0.035
GEN-2020-017 | 05 - Southwest | 525481 | PLANT_X | 230 | 23.9822 | 24.0384 | 0.0562
GEN-2020-017 | 05 - Southwest | 525531 | TOLK | 230 | 32.0572 | 32.177 | 0.1198
GEN-2020-017 | 05 - Southwest | 525549 | TOLK | 345 | 16.4357 | 16.4645 | 0.0288
GEN-2020-017 | 05 - Southwest | 525584 | BLUECLDCOL | 230 | 10.5034 | 10.5131 | 0.0097
GEN-2020-017 | 05 - Southwest | 525585 | BLUECLDPOI | 230 | 11.1065 | 11.1174 | 0.0109
GEN-2020-017 | 05 - Southwest | 525586 | NEEDMORE | 230 | 11.1065 | 11.1174 | 0.0109
GEN-2020-017 | 05 - Southwest | 525599 | LC-SANDHLL+ | 69 | 2.0999 | 2.1031 | 0.0032
GEN-2020-017 | 05 - Southwest | 525606 | AMHERST | 69 | 2.3412 | 2.3451 | 0.0039
GEN-2020-017 | 05 - Southwest | 525613 | W_LITTLFLD | 69 | 2.969 | 2.9754 | 0.0064
GEN-2020-017 | 05 - Southwest | 525620 | LTFLD_S&CTY | 69 | 4.1738 | 4.1864 | 0.0126
GEN-2020-017 | 05 - Southwest | 525635 | LAMB_CNTY | 69 | 5.9018 | 5.9257 | 0.0239
GEN-2020-017 | 05 - Southwest | 525636 | LAMB_CNTY | 115 | 8.4474 | 8.5317 | 0.0843
GEN-2020-017 | 05 - Southwest | 525637 | LAMB_CNTY | 230 | 5.4147 | 5.5692 | 0.1545
GEN-2020-017 | 05 - Southwest | 525650 | LC-LTTLFLD+ | 69 | 4.9337 | 4.9506 | 0.0169
GEN-2020-017 | 05 - Southwest | 525657 | W_ANTON_TP | 69 | 4.1091 | 4.1209 | 0.0118
GEN-2020-017 | 05 - Southwest | 525664 | LC-SPD&HART | 69 | 2.6549 | 2.6599 | 0.005
GEN-2020-017 | 05 - Southwest | 525671 | BAINER | 69 | 3.5064 | 3.5151 | 0.0087
GEN-2020-017 | 05 - Southwest | 525687 | LC-LUMSCHAP | 69 | 4.6141 | 4.6291 | 0.015
GEN-2020-017 | 05 - Southwest | 525694 | HOBGOOD | 69 | 3.4389 | 3.4474 | 0.0085
GEN-2020-017 | 05 - Southwest | 525697 | PUMP/YH_TP | 69 | 3.1827 | 3.19 | 0.0073
GEN-2020-017 | 05 - Southwest | 525731 | SP-ABERNTHY | 69 | 3.0137 | 3.0138 | 0.0001
GEN-2020-017 | 05 - Southwest | 525738 | HALECENTER | 69 | 2.4595 | 2.4595 | 0
GEN-2020-017 | 05 - Southwest | 525763 | CALLAHAN | 115 | 5.5818 | 5.5822 | 0.0004
GEN-2020-017 | 05 - Southwest | 525779 | FLOYD_CNTY | 69 | 5.4106 | 5.4108 | 0.0002
GEN-2020-017 | 05 - Southwest | 525780 | FLOYD_CNTY | 115 | 6.2725 | 6.2729 | 0.0004
GEN-2020-017 | 05 - Southwest | 525803 | BLANCO | 115 | 5.0588 | 5.059 | 0.0002
GEN-2020-017 | 05 - Southwest | 525816 | TUCO_INT2 | 69 | 4.6631 | 4.6632 | 0.0001
GEN-2020-017 | 05 - Southwest | 525826 | TUCO_INT | 69 | 7.8842 | 7.8845 | 0.0003
GEN-2020-017 | 05 - Southwest | 525828 | TUCO_INT | 115 | 19.6754 | 19.6784 | 0.003
GEN-2020-017 | 05 - Southwest | 525830 | TUCO_INT | 230 | 23.1539 | 23.1605 | 0.0066
GEN-2020-017 | 05 - Southwest | 525832 | TUCO_INT | 345 | 15.7007 | 15.7032 | 0.0025
GEN-2020-017 | 05 - Southwest | 525840 | ANTELOPE_1 | 230 | 22.9441 | 22.9505 | 0.0064
GEN-2020-017 | 05 - Southwest | 525850 | ELK_CT1 | 345 | 15.5297 | 15.5321 | 0.0024
GEN-2020-017 | 05 - Southwest | 525853 | LH-WIL&ELN+ | 69 | 2.5434 | 2.5434 | 0
GEN-2020-017 | 05 - Southwest | 525885 | SP-NEWDEAL | 69 | 3.3127 | 3.3127 | 0
GEN-2020-017 | 05 - Southwest | 525926 | CROSBY | 115 | 4.7265 | 4.7267 | 0.0002
GEN-2020-017 | 05 - Southwest | 525957 | HALE_WNDCL1 | 230 | 10.7502 | 10.7515 | 0.0013
GEN-2020-017 | 05 - Southwest | 526002 | LC-WHITHRRL | 69 | 2.8654 | 2.8673 | 0.0019
GEN-2020-017 | 05 - Southwest | 526009 | LC-LEVLND#2 | 69 | 4.263 | 4.2672 | 0.0042
GEN-2020-017 | 05 - Southwest | 526019 | HOCKLEY | 69 | 5.1085 | 5.1145 | 0.006
GEN-2020-017 | 05 - Southwest | 526020 | HOCKLEY | 115 | 5.4217 | 5.4331 | 0.0114
GEN-2020-017 | 05 - Southwest | 526030 | LC-PETTIT | 69 | 1.8822 | 1.883 | 0.0008
GEN-2020-017 | 05 - Southwest | 526036 | LC-OPDYKE | 115 | 5.7073 | 5.7169 | 0.0096
GEN-2020-017 | 05 - Southwest | 526042 | COBLE | 69 | 2.261 | 2.2622 | 0.0012
GEN-2020-017 | 05 - Southwest | 526048 | LVLNDCTY_TP | 69 | 4.263 | 4.2672 | 0.0042
GEN-2020-017 | 05 - Southwest | 526049 | LVLAND_CITY | 69 | 3.8805 | 3.884 | 0.0035
GEN-2020-017 | 05 - Southwest | 526056 | E_LEVELLAND | 69 | 1.6696 | 1.6696 | 0
GEN-2020-017 | 05 - Southwest | 526076 | STANTON_W | 115 | 8.9542 | 8.9548 | 0.0006
GEN-2020-017 | 05 - Southwest | 526109 | SP-ERSKINE | 115 | 11.0117 | 11.0127 | 0.001
GEN-2020-017 | 05 - Southwest | 526146 | INDIANA | 115 | 9.3342 | 9.3348 | 0.0006
GEN-2020-017 | 05 - Southwest | 526159 | CARLISLE | 69 | 2.5578 | 2.5578 | 0
GEN-2020-017 | 05 - Southwest | 526160 | CARLISLE | 115 | 12.809 | 12.8103 | 0.0013
GEN-2020-017 | 05 - Southwest | 526161 | CARLISLE | 230 | 10.4407 | 10.4424 | 0.0017
GEN-2020-017 | 05 - Southwest | 526162 | LP-DOUD_TP | 115 | 11.3495 | 11.3506 | 0.0011
GEN-2020-017 | 05 - Southwest | 526192 | MURPHY | 115 | 10.2794 | 10.2801 | 0.0007
GEN-2020-017 | 05 - Southwest | 526268 | LUBBCK_STH | 115 | 17.8241 | 17.8257 | 0.0016
GEN-2020-017 | 05 - Southwest | 526269 | LUBBCK_STH | 230 | 15.2617 | 15.2638 | 0.0021
GEN-2020-017 | 05 - Southwest | 526297 | LUBBCK_EST | 69 | 7.9282 | 7.9284 | 0.0002
GEN-2020-017 | 05 - Southwest | 526298 | LUBBCK_EST | 115 | 14.598 | 14.5991 | 0.0011
GEN-2020-017 | 05 - Southwest | 526299 | LUBBCK_EST | 230 | 11.4856 | 11.4866 | 0.001
GEN-2020-017 | 05 - Southwest | 526337 | JONES | 230 | 16.9819 | 16.984 | 0.0021
GEN-2020-017 | 05 - Southwest | 526424 | PACIFIC | 115 | 9.1395 | 9.1447 | 0.0052
GEN-2020-017 | 05 - Southwest | 526434 | SUNDOWN | 115 | 10.8011 | 10.8088 | 0.0077
GEN-2020-017 | 05 - Southwest | 526435 | SUNDOWN | 230 | 11.0401 | 11.0455 | 0.0054
GEN-2020-017 | 05 - Southwest | 526445 | AMOCO_TP | 115 | 10.1402 | 10.1467 | 0.0065
GEN-2020-017 | 05 - Southwest | 526460 | AMOCO_SS | 230 | 9.7724 | 9.7761 | 0.0037
GEN-2020-017 | 05 - Southwest | 526524 | WOLFFORTH | 115 | 11.2945 | 11.2957 | 0.0012
GEN-2020-017 | 05 - Southwest | 526525 | WOLFFORTH | 230 | 12.6577 | 12.6605 | 0.0028
GEN-2020-017 | 05 - Southwest | 526676 | GRASSLAND | 115 | 6.8932 | 6.8934 | 0.0002
GEN-2020-017 | 05 - Southwest | 526677 | GRASSLAND | 230 | 6.0203 | 6.0206 | 0.0003
GEN-2020-017 | 05 - Southwest | 526679 | CIRRUS_WND | 230 | 4.7079 | 4.7081 | 0.0002
GEN-2020-017 | 05 - Southwest | 526784 | AMOCOWASSON | 230 | 15.9864 | 15.9881 | 0.0017
GEN-2020-017 | 05 - Southwest | 526792 | PRENTICE | 115 | 6.0512 | 6.0516 | 0.0004
GEN-2020-017 | 05 - Southwest | 526928 | PLAINS_INT | 115 | 10.0894 | 10.0903 | 0.0009
GEN-2020-017 | 05 - Southwest | 526934 | YOAKUM | 115 | 19.5311 | 19.5335 | 0.0024
GEN-2020-017 | 05 - Southwest | 526935 | YOAKUM | 230 | 20.6045 | 20.6089 | 0.0044
GEN-2020-017 | 05 - Southwest | 526936 | YOAKUM_345 | 345 | 11.5787 | 11.5801 | 0.0014
GEN-2020-017 | 05 - Southwest | 527009 | BRU_SUB | 230 | 16.1093 | 16.1115 | 0.0022
GEN-2020-017 | 05 - Southwest | 527010 | OXYBRU | 230 | 15.9545 | 15.9566 | 0.0021
GEN-2020-017 | 05 - Southwest | 527011 | XTO_MAHONEY | 230 | 15.7642 | 15.7661 | 0.0019
GEN-2020-017 | 05 - Southwest | 527020 | SIDEWINDER | 345 | 13.1078 | 13.1087 | 0.0009
GEN-2020-017 | 05 - Southwest | 527027 | INK_BASIN | 115 | 13.0791 | 13.0796 | 0.0005
GEN-2020-017 | 05 - Southwest | 527028 | INK_BASIN | 230 | 11.5057 | 11.5066 | 0.0009
GEN-2020-017 | 05 - Southwest | 527041 | ARCO_TP | 115 | 13.781 | 13.7818 | 0.0008
GEN-2020-017 | 05 - Southwest | 527146 | MUSTANG | 115 | 24.2865 | 24.2882 | 0.0017
GEN-2020-017 | 05 - Southwest | 527149 | MUSTANG | 230 | 18.319 | 18.3209 | 0.0019
GEN-2020-017 | 05 - Southwest | 527151 | GS-MUSTANG | 230 | 18.319 | 18.3209 | 0.0019
GEN-2020-017 | 05 - Southwest | 527194 | LG-PLSHILL | 115 | 8.0074 | 8.0078 | 0.0004
GEN-2020-017 | 05 - Southwest | 527276 | SEMINOLE | 230 | 8.2732 | 8.2736 | 0.0004
GEN-2020-017 | 05 - Southwest | 527483 | CHAVES_CNTY | 230 | 4.5764 | 4.5767 | 0.0003
GEN-2020-017 | 05 - Southwest | 527599 | SAGA_SDCOL | 345 | 11.078 | 11.0808 | 0.0028
GEN-2020-017 | 05 - Southwest | 527610 | SAGA_SCOL | 345 | 11.078 | 11.0808 | 0.0028
GEN-2020-017 | 05 - Southwest | 527654 | RSVLT_CC_W | 345 | 9.323 | 9.325 | 0.002
GEN-2020-017 | 05 - Southwest | 527655 | RSVLT_CC_E | 345 | 10.8403 | 10.8431 | 0.0028
GEN-2020-017 | 05 - Southwest | 527656 | CROSSROADS | 345 | 12.6978 | 12.7018 | 0.004
GEN-2020-017 | 05 - Southwest | 527799 | EDDY_NORTH | 230 | 9.9885 | 9.9892 | 0.0007
GEN-2020-017 | 05 - Southwest | 527802 | EDDY_CNTY | 345 | 8.0252 | 8.026 | 0.0008
GEN-2020-017 | 05 - Southwest | 527894 | HOBBS_INT | 230 | 20.902 | 20.9035 | 0.0015
GEN-2020-017 | 05 - Southwest | 527896 | HOBBS_INT | 345 | 16.6017 | 16.6041 | 0.0024
GEN-2020-017 | 05 - Southwest | 527965 | KIOWA | 345 | 10.2473 | 10.2483 | 0.001
GEN-2020-017 | 05 - Southwest | 528027 | RDRUNNER | 345 | 10.3644 | 10.3653 | 0.0009
GEN-2020-017 | 05 - Southwest | 560022 | CRAWFISH_DR | 345 | 15.4719 | 15.4742 | 0.0023
GEN-2020-017 | 05 - Southwest | 560078 | G16-037-TAP | 345 | 9.4124 | 9.4126 | 0.0002
GEN-2020-017 | 05 - Southwest | 576397 | G10014G1102 | 345 | 10.2273 | 10.2275 | 0.0002
GEN-2020-017 | 05 - Southwest | 599951 | LAMAR | 345 | 12.9476 | 12.9476 | 0
GEN-2020-017 | 05 - Southwest | 599955 | PNM-DC6 | 230 | 10.2253 | 10.2326 | 0.0073
GEN-2020-017 | 05 - Southwest | 599956 | PNM-DC7 | 345 | 14.6646 | 14.6646 | 0
GEN-2020-017 | 05 - Southwest | 599961 | EPTNP | 345 | 12.9476 | 12.9476 | 0
GEN-2020-017 | 05 - Southwest | 760494 | GEN-2017-14 | 230 | 7.4416 | 7.4443 | 0.0027
GEN-2020-017 | 05 - Southwest | 760498 | G17-146-TAP | 230 | 7.7297 | 7.7326 | 0.0029
GEN-2020-017 | 05 - Southwest | 762132 | GEN-2017-15 | 230 | 13.9583 | 13.9781 | 0.0198
GEN-2020-017 | 05 - Southwest | 762216 | G17-151TAP | 345 | 8.9337 | 8.9343 | 0.0006
GEN-2020-017 | 05 - Southwest | 762467 | G18-015-TAP | 345 | 9.4394 | 9.4398 | 0.0004
GEN-2020-017 | 05 - Southwest | 763186 | GEN-2018-08 | 230 | 10.7032 | 10.7075 | 0.0043
GEN-2020-017 | 05 - Southwest | 763215 | G18-092-PRO | 345 | 9.3695 | 9.3698 | 0.0003
GEN-2020-017 | 05 - Southwest | 763483 | GEN-2019-00 | 230 | 9.1505 | 9.1563 | 0.0058
GEN-2020-017 | 05 - Southwest | 763516 | GEN-2019-01 | 345 | 10.7097 | 10.7109 | 0.0012
GEN-2020-017 | 05 - Southwest | 764825 | GEN-2020-01 | 230 | 5.3964 | 5.5509 | 0.1545
GEN-2020-017 | 05 - Southwest | 764866 | G20-059-TAP | 345 | 11.5316 | 11.5328 | 0.0012
GEN-2020-017 | 05 - Southwest | 764875 | GEN-2020-06 | 230 | 11.3104 | 11.3113 | 0.0009
GEN-2020-017 | 05 - Southwest | 764890 | GEN-2020-06 | 230 | 7.0494 | 7.0522 | 0.0028
GEN-2020-017 | 05 - Southwest | 764935 | GEN-2020-06 | 345 | 7.0157 | 7.0161 | 0.0004
GEN-2020-017 | 05 - Southwest | 764945 | G20-067-TAP | 345 | 8.6175 | 8.6182 | 0.0007
GEN-2020-017 | 05 - Southwest | 764950 | GEN-2020-06 | 345 | 8.5752 | 8.5759 | 0.0007
GEN-2020-009 | 05 - Southwest | 511409 | TREASILD7 | 345 | 15.0039 | 15.2041 | 0.2002
GEN-2020-009 | 05 - Southwest | 511422 | FLETCHR4 | 138 | 7.8261 | 7.8424 | 0.0163
GEN-2020-009 | 05 - Southwest | 511423 | FLE | 138 | 8.5533 | 8.5728 | 0.0195
GEN-2020-009 | 05 - Southwest | 511428 | LG-YEAR4 | 138 | 11.9992 | 12.07 | 0.0708
GEN-2020-009 | 05 - Southwest | 511431 | LWS | 138 | 11.1463 | 11.2102 | 0.0639
GEN-2020-009 | 05 - Southwest | 511436 | COMANC-2 | 69 | 9.2158 | 9.2281 | 0.0123
GEN-2020-009 | 05 - Southwest | 511437 | COMANC-4 | 138 | 18.3262 | 18.4958 | 0.1696
GEN-2020-009 | 05 - Southwest | 511439 | LWSTAP | 138 | 11.6283 | 11.6978 | 0.0695
GEN-2020-009 | 05 - Southwest | 511451 | CYRIL--2 | 69 | 4.6371 | 4.6396 | 0.0025
GEN-2020-009 | 05 - Southwest | 511453 | DUNCAN-4 | 138 | 6.357 | 6.3681 | 0.0111
GEN-2020-009 | 05 - Southwest | 511456 | O.K.U.-7 | 345 | 7.1908 | 7.442 | 0.2512
GEN-2020-009 | 05 - Southwest | 511461 | FT.SILL2 | 69 | 5.9193 | 5.9262 | 0.0069
GEN-2020-009 | 05 - Southwest | 511466 | L.E.S.-2 | 69 | 16.4043 | 16.4656 | 0.0613
GEN-2020-009 | 05 - Southwest | 511467 | L.E.S.-4 | 138 | 25.2713 | 25.6514 | 0.3801
GEN-2020-009 | 05 - Southwest | 511468 | L.E.S.-7 | 345 | 14.8059 | 15.4119 | 0.606
GEN-2020-009 | 05 - Southwest | 511469 | LGORE-N2 | 69 | 7.9672 | 7.9808 | 0.0136
GEN-2020-009 | 05 - Southwest | 511470 | LGORE-S2 | 69 | 6.9072 | 6.9182 | 0.011
GEN-2020-009 | 05 - Southwest | 511471 | LWS-NTP4 | 138 | 11.7554 | 11.8271 | 0.0717
GEN-2020-009 | 05 - Southwest | 511473 | PO.HILL2 | 69 | 5.8035 | 5.8091 | 0.0056
GEN-2020-009 | 05 - Southwest | 511474 | SHERID4 | 138 | 12.4287 | 12.5124 | 0.0837
GEN-2020-009 | 05 - Southwest | 511477 | S.W.S.-4 | 138 | 31.8244 | 31.8982 | 0.0738
GEN-2020-009 | 05 - Southwest | 511486 | ELGINJT4 | 138 | 9.9775 | 10.0078 | 0.0303
GEN-2020-009 | 05 - Southwest | 511487 | ELGINJT2 | 69 | 8.4827 | 8.4934 | 0.0107
GEN-2020-009 | 05 - Southwest | 511488 | 112GORE4 | 138 | 12.801 | 12.8816 | 0.0806
GEN-2020-009 | 05 - Southwest | 511494 | COMMTAP4 | 138 | 21.9531 | 22.227 | 0.2739
GEN-2020-009 | 05 - Southwest | 511503 | LAW | 69 | 4.5176 | 4.5223 | 0.0047
GEN-2020-009 | 05 - Southwest | 511509 | 53CACHE4 | 138 | 11.7918 | 11.8648 | 0.073
GEN-2020-009 | 05 - Southwest | 511510 | LAIRGST4 | 138 | 12.3914 | 12.4661 | 0.0747
GEN-2020-009 | 05 - Southwest | 511512 | RPPAPER4 | 138 | 12.0525 | 12.1255 | 0.073
GEN-2020-009 | 05 - Southwest | 511524 | L-DISTP2 | 69 | 8.5391 | 8.5495 | 0.0104
GEN-2020-009 | 05 - Southwest | 511537 | ARTVLTP4 | 138 | 11.8117 | 11.8852 | 0.0735
GEN-2020-009 | 05 - Southwest | 511538 | ARTVILL4 | 138 | 8.5207 | 8.5589 | 0.0382
GEN-2020-009 | 05 - Southwest | 511563 | ELSWORTH | 138 | 9.9014 | 9.9306 | 0.0292
GEN-2020-009 | 05 - Southwest | 511565 | OKLAUN | 345 | 7.1627 | 7.4119 | 0.2492
GEN-2020-009 | 05 - Southwest | 511568 | TERRYRD7 | 345 | 9.6322 | 9.7765 | 0.1443
GEN-2020-009 | 05 - Southwest | 511571 | RUSHSPR7 | 345 | 5.6686 | 5.7183 | 0.0497
GEN-2020-009 | 05 - Southwest | 514801 | MINCO | 345 | 22.9523 | 23.0245 | 0.0722
GEN-2020-009 | 05 - Southwest | 515136 | SUNNYSD7 | 345 | 10.3741 | 10.4219 | 0.0478
GEN-2020-009 | 05 - Southwest | 515458 | BORDER | 345 | 8.3819 | 8.3898 | 0.0079
GEN-2020-009 | 05 - Southwest | 515800 | GRACMNT7 | 345 | 18.1763 | 18.3371 | 0.1608
GEN-2020-009 | 05 - Southwest | 515802 | GRACMNT4 | 138 | 31.532 | 31.6117 | 0.0797
GEN-2020-009 | 05 - Southwest | 516059 | BECKHAM7 | 345 | 12.6257 | 12.6411 | 0.0154
GEN-2020-009 | 05 - Southwest | 525830 | TUCO_INT | 230 | 23.1086 | 23.1605 | 0.0519
GEN-2020-009 | 05 - Southwest | 525832 | TUCO_INT | 345 | 15.6253 | 15.7032 | 0.0779
GEN-2020-009 | 05 - Southwest | 525850 | ELK_CT1 | 345 | 15.456 | 15.5321 | 0.0761
GEN-2020-009 | 05 - Southwest | 529304 | OMDUNCN4 | 138 | 6.6037 | 6.6176 | 0.0139
GEN-2020-009 | 05 - Southwest | 560022 | CRAWFISH_DR | 345 | 15.3943 | 15.4742 | 0.0799
GEN-2020-009 | 05 - Southwest | 560078 | G16-037-TAP | 345 | 9.3916 | 9.4126 | 0.021
GEN-2020-009 | 05 - Southwest | 563259 | GEN-2015-09 | 345 | 5.4891 | 5.5357 | 0.0466
GEN-2020-009 | 05 - Southwest | 563269 | GEN-2015-09 | 345 | 9.8469 | 9.894 | 0.0471
GEN-2020-009 | 05 - Southwest | 587740 | GEN-2016-09 | 345 | 10.2332 | 10.3259 | 0.0927
GEN-2020-009 | 05 - Southwest | 587770 | GEN-2016-09 | 345 | 10.6057 | 10.7054 | 0.0997
GEN-2020-009 | 05 - Southwest | 587790 | GEN-2016-09 | 138 | 8.5348 | 8.5461 | 0.0113
GEN-2020-009 | 05 - Southwest | 587794 | G16-097-TAP | 138 | 10.6448 | 10.6623 | 0.0175
GEN-2020-009 | 05 - Southwest | 588760 | GEN-2017-03 | 345 | 4.8282 | 4.9338 | 0.1056
GEN-2020-009 | 05 - Southwest | 590001 | OKLEHV24 | 138 | 4.7903 | 4.7903 | 0
GEN-2020-009 | 05 - Southwest | 590003 | OKLEHV14 | 138 | 4.8014 | 4.8014 | 0
GEN-2020-009 | 05 - Southwest | 599891 | OKLAUN | 345 | 4.0421 | 4.0421 | 0
GEN-2020-009 | 05 - Southwest | 760938 | G17-171-TAP | 345 | 11.0549 | 11.3107 | 0.2558
GEN-2020-009 | 05 - Southwest | 760939 | GEN-2017-17 | 345 | 10.9884 | 11.2411 | 0.2527
GEN-2020-009 | 05 - Southwest | 762216 | G17-151TAP | 345 | 8.8932 | 8.9343 | 0.0411
GEN-2020-009 | 05 - Southwest | 762217 | GEN-2017-15 | 345 | 6.3639 | 6.3839 | 0.02
GEN-2020-009 | 05 - Southwest | 762460 | GEN-2018-01 | 345 | 9.2707 | 9.4054 | 0.1347
GEN-2020-009 | 05 - Southwest | 762467 | G18-015-TAP | 345 | 9.3041 | 9.4398 | 0.1357
GEN-2020-009 | 05 - Southwest | 762900 | GEN-2018-05 | 345 | 3.9322 | 3.956 | 0.0238
GEN-2020-009 | 05 - Southwest | 763215 | G18-092-PRO | 345 | 9.174 | 9.3698 | 0.1958
GEN-2020-009 | 05 - Southwest | 763318 | GEN-2018-11 | 345 | 14.4861 | 15.0657 | 0.5796
GEN-2020-009 | 05 - Southwest | 764105 | GEN-2020-07 | 345 | 9.6859 | 9.7496 | 0.0637
GEN-2020-009 | 05 - Southwest | 764115 | G20-074-TAP | 345 | 9.6902 | 9.754 | 0.0638
GEN-2020-009 | 05 - Southwest | 764540 | GEN-2020-07 | 345 | 14.0368 | 14.385 | 0.3482
GEN-2020-009 | 05 - Southwest | 764550 | G20-075-TAP | 345 | 14.0475 | 14.3962 | 0.3487
GEN-2020-009 | 05 - Southwest | 764555 | GEN-2020-08 | 345 | 14.038 | 14.3862 | 0.3482
GEN-2020-009 | 05 - Southwest | 764945 | G20-067-TAP | 345 | 8.6121 | 8.6182 | 0.0061
GEN-2020-009 | 05 - Southwest | 766290 | GEN-2020-00 | 345 | 8.7002 | 9.4725 | 0.7723
GEN-2020-009 | 05 - Southwest | 766291 | G20-009-TAP | 345 | 8.7002 | 9.4725 | 0.7723

## SCRCCT
Study | Case Type | Region Name | Season Year | Season | Contingency Definition | SCR | Critical_Clearing_Time | POI Bus | Stability Margin | Pg Out | Pg Rated
2001 | TC | 01 - North | 25 | SP | base | 4.3898 | 34.6497 | GEN-2020-006 | 34549.7148 | 250 | 267.12
2001 | TC | 01 - North | 25 | SP | 659105-659424 | 4.4835 | 1.5401 | GEN-2020-021 | 1440.0802 | 125.4 | 140.51
2001 | TC | 01 - North | 25 | SP | 659105-659424 | 4.4835 | 1.5593 | GEN-2020-021 | 1459.3456 | 109.6 | 122.95
2001 | TC | 01 - North | 25 | SP | 659130-659428 | 4.0267 | 1.5659 | GEN-2020-021 | 1465.9236 | 125.4 | 140.51
2001 | TC | 01 - North | 25 | SP | 659130-659428 | 4.0267 | 1.5797 | GEN-2020-021 | 1479.6915 | 109.6 | 122.95
2001 | TC | 01 - North | 25 | SP | 652421-652651 | 5.0024 | 7.0734 | GEN-2020-083 | 6973.397 | 56.06 | 86.4
2001 | TC | 01 - North | 25 | SP | 652421-652651 | 5.0024 | 6.3687 | GEN-2020-083 | 6268.6912 | 18.44 | 31.5
2001 | TC | 01 - North | 25 | SP | 659130-652806 | 3.8005 | 1.5312 | GEN-2020-021 | 1431.1712 | 125.4 | 140.51
2001 | TC | 01 - North | 25 | SP | 659130-652806 | 3.8005 | 1.5533 | GEN-2020-021 | 1453.3319 | 109.6 | 122.95
2001 | TC | 01 - North | 25 | SP | 659151-652651 | 4.8073 | 5.6722 | GEN-2020-083 | 5572.2042 | 56.06 | 86.4
2001 | TC | 01 - North | 25 | SP | 659151-652651 | 4.8073 | 6.8781 | GEN-2020-083 | 6778.0786 | 18.44 | 31.5
2001 | TC | 01 - North | 25 | SP | 659424-764220 | 4.5985 | 1.5327 | GEN-2020-021 | 1432.7245 | 125.4 | 140.51
2001 | TC | 01 - North | 25 | SP | 659424-764220 | 4.5985 | 1.5541 | GEN-2020-021 | 1454.095 | 109.6 | 122.95
2001 | TC | 01 - North | 25 | SP | 659428-764220 | 3.9912 | 1.5692 | GEN-2020-021 | 1469.2278 | 125.4 | 140.51
2001 | TC | 01 - North | 25 | SP | 659428-764220 | 3.9912 | 1.5821 | GEN-2020-021 | 1482.0919 | 109.6 | 122.95
2001 | TC | 01 - North | 25 | WP | base | 4.4917 | 151.8904 | GEN-2020-006 | 151790.4035 | 250 | 267.12
2001 | TC | 01 - North | 25 | WP | 659105-659424 | 4.5121 | 1.5396 | GEN-2020-021 | 1439.5836 | 125.4 | 140.51
2001 | TC | 01 - North | 25 | WP | 659105-659424 | 4.5121 | 1.5589 | GEN-2020-021 | 1458.943 | 109.6 | 122.95
2001 | TC | 01 - North | 25 | WP | 659130-659428 | 4.0297 | 1.5658 | GEN-2020-021 | 1465.8171 | 125.4 | 140.51
2001 | TC | 01 - North | 25 | WP | 659130-659428 | 4.0297 | 1.5796 | GEN-2020-021 | 1479.6024 | 109.6 | 122.95
2001 | TC | 01 - North | 25 | WP | 652421-652651 | 5.0008 | 6.7635 | GEN-2020-083 | 6663.5188 | 56.06 | 86.4
2001 | TC | 01 - North | 25 | WP | 652421-652651 | 5.0008 | 6.4482 | GEN-2020-083 | 6348.1571 | 18.44 | 31.5
2001 | TC | 01 - North | 25 | WP | 659130-652806 | 3.8051 | 1.5312 | GEN-2020-021 | 1431.1833 | 125.4 | 140.51
2001 | TC | 01 - North | 25 | WP | 659130-652806 | 3.8051 | 1.5533 | GEN-2020-021 | 1453.3245 | 109.6 | 122.95
2001 | TC | 01 - North | 25 | WP | 659151-652651 | 4.8159 | 5.5815 | GEN-2020-083 | 5481.5311 | 56.06 | 86.4
2001 | TC | 01 - North | 25 | WP | 659151-652651 | 4.8159 | 6.9351 | GEN-2020-083 | 6835.0556 | 18.44 | 31.5
2001 | TC | 01 - North | 25 | WP | 659424-764220 | 4.6275 | 1.5323 | GEN-2020-021 | 1432.3106 | 125.4 | 140.51
2001 | TC | 01 - North | 25 | WP | 659424-764220 | 4.6275 | 1.5538 | GEN-2020-021 | 1453.7534 | 109.6 | 122.95
2001 | TC | 01 - North | 25 | WP | 659428-764220 | 3.9942 | 1.5691 | GEN-2020-021 | 1469.1165 | 125.4 | 140.51
2001 | TC | 01 - North | 25 | WP | 659428-764220 | 3.9942 | 1.582 | GEN-2020-021 | 1481.9989 | 109.6 | 122.95
2001 | TC | 02 - Nebraska | 25 | SP | base | 5.4547 | 173.0229 | GEN-2020-013 | 172922.8807 | 71.66 | 81.9
2001 | TC | 02 - Nebraska | 25 | SP | base | 5.4547 | 167.2372 | GEN-2020-013 | 167137.2429 | 71.66 | 81.9
2001 | TC | 02 - Nebraska | 25 | SP | base | 5.4547 | 142.32 | GEN-2020-013 | 142219.9845 | 71.66 | 81.9
2001 | TC | 02 - Nebraska | 25 | SP | base | 4.1238 | 0.1629 | GEN-2020-069 | 62.8846 | 52.85 | 63
2001 | TC | 02 - Nebraska | 25 | SP | base | 12.0166 | 0.1197 | GEN-2020-070 | 19.7286 | 255 | 323.3
2001 | TC | 02 - Nebraska | 25 | SP | base | 5.9867 | 0.117 | GEN-2020-077 | 16.983 | 151.2 | 156
2001 | TC | 02 - Nebraska | 25 | SP | 647014-647846 | 4.401 | 24.0758 | GEN-2020-002 | 23975.7502 | 81 | 93.6
2001 | TC | 02 - Nebraska | 25 | WP | base | 5.2506 | 131.0171 | GEN-2020-013 | 130917.0525 | 71.66 | 81.9
2001 | TC | 02 - Nebraska | 25 | WP | base | 5.2506 | 127.1631 | GEN-2020-013 | 127063.0788 | 71.66 | 81.9
2001 | TC | 02 - Nebraska | 25 | WP | base | 5.2506 | 113.559 | GEN-2020-013 | 113458.9795 | 71.66 | 81.9
2001 | TC | 02 - Nebraska | 25 | WP | base | 4.0706 | 0.164 | GEN-2020-069 | 64.0074 | 52.85 | 63
2001 | TC | 02 - Nebraska | 25 | WP | base | 11.2939 | 0.1188 | GEN-2020-070 | 18.836 | 255 | 323.3
2001 | TC | 02 - Nebraska | 25 | WP | base | 5.4467 | 0.1189 | GEN-2020-077 | 18.8554 | 151.2 | 156
2001 | TC | 02 - Nebraska | 25 | WP | 647014-647846 | 4.3169 | 24.2833 | GEN-2020-002 | 24183.3095 | 81 | 93.6
2001 | TC | 03 - Central | 25 | WP | base | 14.9514 | 0.1252 | GEN-2020-071 | 25.2272 | 252 | 270
2001 | TC | 03 - Central | 25 | WP | base | 5.0292 | 0.1896 | GEN-2020-089 | 89.6111 | 103.99 | 113.41
2001 | TC | 03 - Central | 25 | WP | 300071-541217 | 2.9357 | 13.4316 | GEN-2020-072 | 13331.6308 | 72.23 | 170.4
2001 | TC | 03 - Central | 25 | WP | 300071-541217 | 2.9357 | 10.9774 | GEN-2020-072 | 10877.4042 | 77.77 | 181.05
2001 | TC | 03 - Central | 25 | WP | 300117-541209 | 4.6799 | 18.5846 | GEN-2020-072 | 18484.5737 | 72.23 | 170.4
2001 | TC | 03 - Central | 25 | WP | 300117-541209 | 4.6799 | 13.3834 | GEN-2020-072 | 13283.351 | 77.77 | 181.05
2001 | TC | 03 - Central | 25 | WP | 542966-543077 | 4.4403 | 14.3128 | GEN-2020-073 | 14212.7711 | 66.64 | 170.4
2001 | TC | 03 - Central | 25 | WP | 542966-543077 | 4.4403 | 11.6501 | GEN-2020-073 | 11550.0528 | 83.36 | 181.05
2001 | TC | 03 - Central | 25 | WP | 300071-761278 | 5.8644 | 18.1874 | GEN-2020-072 | 18087.4418 | 72.23 | 170.4
2001 | TC | 03 - Central | 25 | WP | 300071-761278 | 5.8644 | 13.1492 | GEN-2020-072 | 13049.1605 | 77.77 | 181.05
2001 | TC | 03 - Central | 25 | WP | 300117-764355 | 3.8578 | 17.3016 | GEN-2020-072 | 17201.5772 | 72.23 | 170.4
2001 | TC | 03 - Central | 25 | WP | 300117-764355 | 3.8578 | 12.9117 | GEN-2020-072 | 12811.6526 | 77.77 | 181.05
2001 | TC | 03 - Central | 25 | WP | 505488-547479 | 5.1081 | 4.9604 | GEN-2020-088 | 4860.4332 | 150 | 165.6
2001 | TC | 03 - Central | 25 | WP | 523097-523823 | 4.1956 | 28.9657 | GEN-2020-008 | 28865.6946 | 166.67 | 267.12
2001 | TC | 03 - Central | 25 | WP | 523097-523823 | 4.1956 | 37.5694 | GEN-2020-008 | 37469.4203 | 83.33 | 133.56
2001 | TC | 03 - Central | 25 | WP | 523853-523823 | 5.909 | 21.3125 | GEN-2020-008 | 21212.4812 | 166.67 | 267.12
2001 | TC | 03 - Central | 25 | WP | 523853-523823 | 5.909 | 30.7686 | GEN-2020-008 | 30668.5833 | 83.33 | 133.56
2001 | TC | 03 - Central | 25 | WP | 532791-765155 | 2.8085 | 1.0444 | GEN-2020-076 | 944.424 | 200 | 216.84
2001 | TC | 03 - Central | 25 | WP | 532791-765155 | 2.8085 | 1.6986 | GEN-2020-086 | 1598.6086 | 250 | 270
2001 | TC | 03 - Central | 25 | WP | 532791-765155 | 2.8085 | 1.6986 | GEN-2020-086 | 1598.6086 | 250 | 270
2001 | TC | 03 - Central | 25 | WP | 541217-764355 | 2.9295 | 13.6893 | GEN-2020-072 | 13589.3495 | 72.23 | 170.4
2001 | TC | 03 - Central | 25 | WP | 541217-764355 | 2.9295 | 11.1312 | GEN-2020-072 | 11031.2021 | 77.77 | 181.05
2001 | TC | 03 - Central | 25 | WP | 542965-542940 | 5.3299 | 15.9225 | GEN-2020-058 | 15822.4875 | 138.21 | 151.2
2001 | TC | 03 - Central | 25 | WP | 542965-542940 | 5.3299 | 14.4273 | GEN-2020-058 | 14327.3473 | 138.21 | 151.2
2001 | TC | 03 - Central | 25 | WP | 542965-542940 | 5.3299 | 12.8972 | GEN-2020-058 | 12797.2372 | 148.08 | 162
2001 | TC | 03 - Central | 25 | WP | 542965-542940 | 5.3299 | 7.961 | GEN-2020-057 | 7861.0026 | 141.5 | 160
2001 | TC | 03 - Central | 25 | WP | 542965-542940 | 5.3299 | 7.7146 | GEN-2020-057 | 7614.5806 | 141.5 | 160
2001 | TC | 03 - Central | 25 | WP | 542965-542940 | 5.3299 | 7.4835 | GEN-2020-057 | 7383.541 | 141.5 | 160
2001 | TC | 03 - Central | 25 | WP | 542981-766261 | 2.1347 | 19.1929 | GEN-2020-007 | 19092.9045 | 90.24 | 176.4
2001 | TC | 03 - Central | 25 | WP | 542981-766261 | 2.1347 | 19.2146 | GEN-2020-007 | 19114.6001 | 94.53 | 176.4
2001 | TC | 03 - Central | 25 | WP | 542981-766261 | 2.1347 | 19.2039 | GEN-2020-007 | 19103.9263 | 92.38 | 176.4
2001 | TC | 03 - Central | 25 | WP | 542981-766261 | 2.1347 | 18.8889 | GEN-2020-007 | 18788.8695 | 90.24 | 189
2001 | TC | 03 - Central | 25 | WP | 542981-766261 | 2.1347 | 19.8202 | GEN-2020-007 | 19720.2123 | 73.82 | 147
2001 | TC | 03 - Central | 25 | WP | 542981-766261 | 2.1347 | 19.8117 | GEN-2020-007 | 19711.7285 | 73.82 | 147
2001 | TC | 03 - Central | 25 | WP | 542981-766261 | 2.1347 | 19.816 | GEN-2020-007 | 19715.9828 | 73.82 | 147
2001 | TC | 03 - Central | 25 | WP | 542981-766261 | 2.1347 | 21.1046 | GEN-2020-007 | 21004.6111 | 61.16 | 113.4
2001 | TC | 03 - Central | 25 | WP | 543077-764400 | 4.4961 | 15.1237 | GEN-2020-073 | 15023.6703 | 66.64 | 170.4
2001 | TC | 03 - Central | 25 | WP | 543077-764400 | 4.4961 | 12.1119 | GEN-2020-073 | 12011.8708 | 83.36 | 181.05
2001 | TC | 03 - Central | 25 | WP | 547469-764310 | 3.1543 | 22.3785 | GEN-2020-079 | 22278.4762 | 56.25 | 121.8
2001 | TC | 03 - Central | 25 | WP | 547469-764310 | 3.1543 | 25.4564 | GEN-2020-079 | 25356.4098 | 55.46 | 147
2001 | TC | 03 - Central | 25 | WP | 547469-764310 | 3.1543 | 19.6281 | GEN-2020-079 | 19528.0709 | 56.25 | 121.8
2001 | TC | 03 - Central | 25 | SP | base | 15.882 | 0.1247 | GEN-2020-071 | 24.7112 | 252 | 270
2001 | TC | 03 - Central | 25 | SP | base | 5.1739 | 0.1893 | GEN-2020-089 | 89.2888 | 103.99 | 113.41
2001 | TC | 03 - Central | 25 | SP | 300071-541217 | 2.9392 | 13.3482 | GEN-2020-072 | 13248.1545 | 72.23 | 170.4
2001 | TC | 03 - Central | 25 | SP | 300071-541217 | 2.9392 | 10.9225 | GEN-2020-072 | 10822.4855 | 77.77 | 181.05
2001 | TC | 03 - Central | 25 | SP | 300117-541209 | 4.7054 | 18.8655 | GEN-2020-072 | 18765.5154 | 72.23 | 170.4
2001 | TC | 03 - Central | 25 | SP | 300117-541209 | 4.7054 | 13.4949 | GEN-2020-072 | 13394.8803 | 77.77 | 181.05
2001 | TC | 03 - Central | 25 | SP | 542966-543077 | 4.8092 | 14.7565 | GEN-2020-073 | 14656.5176 | 66.64 | 170.4
2001 | TC | 03 - Central | 25 | SP | 542966-543077 | 4.8092 | 11.878 | GEN-2020-073 | 11777.9961 | 83.36 | 181.05
2001 | TC | 03 - Central | 25 | SP | 300071-761278 | 5.8914 | 18.325 | GEN-2020-072 | 18225.0482 | 72.23 | 170.4
2001 | TC | 03 - Central | 25 | SP | 300071-761278 | 5.8914 | 13.204 | GEN-2020-072 | 13103.9978 | 77.77 | 181.05
2001 | TC | 03 - Central | 25 | SP | 300117-764355 | 3.8769 | 17.404 | GEN-2020-072 | 17304.0489 | 72.23 | 170.4
2001 | TC | 03 - Central | 25 | SP | 300117-764355 | 3.8769 | 12.9563 | GEN-2020-072 | 12856.2915 | 77.77 | 181.05
2001 | TC | 03 - Central | 25 | SP | 523097-523823 | 4.4085 | 27.6848 | GEN-2020-008 | 27584.839 | 166.67 | 267.12
2001 | TC | 03 - Central | 25 | SP | 523097-523823 | 4.4085 | 36.3491 | GEN-2020-008 | 36249.1318 | 83.33 | 133.56
2001 | TC | 03 - Central | 25 | SP | 532791-765155 | 2.651 | 1.0425 | GEN-2020-076 | 942.4821 | 200 | 216.84
2001 | TC | 03 - Central | 25 | SP | 532791-765155 | 2.651 | 1.6107 | GEN-2020-086 | 1510.7234 | 250 | 270
2001 | TC | 03 - Central | 25 | SP | 532791-765155 | 2.651 | 1.6107 | GEN-2020-086 | 1510.7234 | 250 | 270
2001 | TC | 03 - Central | 25 | SP | 541217-764355 | 2.9315 | 13.6589 | GEN-2020-072 | 13558.9351 | 72.23 | 170.4
2001 | TC | 03 - Central | 25 | SP | 541217-764355 | 2.9315 | 11.1085 | GEN-2020-072 | 11008.5297 | 77.77 | 181.05
2001 | TC | 03 - Central | 25 | SP | 542965-542940 | 5.5562 | 15.7115 | GEN-2020-058 | 15611.4791 | 138.21 | 151.2
2001 | TC | 03 - Central | 25 | SP | 542965-542940 | 5.5562 | 14.2518 | GEN-2020-058 | 14151.8151 | 138.21 | 151.2
2001 | TC | 03 - Central | 25 | SP | 542965-542940 | 5.5562 | 12.7515 | GEN-2020-058 | 12651.5024 | 148.08 | 162
2001 | TC | 03 - Central | 25 | SP | 542965-542940 | 5.5562 | 7.8698 | GEN-2020-057 | 7769.8001 | 141.5 | 160
2001 | TC | 03 - Central | 25 | SP | 542965-542940 | 5.5562 | 7.6283 | GEN-2020-057 | 7528.2713 | 141.5 | 160
2001 | TC | 03 - Central | 25 | SP | 542965-542940 | 5.5562 | 7.4017 | GEN-2020-057 | 7301.693 | 141.5 | 160
2001 | TC | 03 - Central | 25 | SP | 542981-766261 | 2.1415 | 19.4172 | GEN-2020-007 | 19317.165 | 90.24 | 176.4
2001 | TC | 03 - Central | 25 | SP | 542981-766261 | 2.1415 | 19.4392 | GEN-2020-007 | 19339.1764 | 94.53 | 176.4
2001 | TC | 03 - Central | 25 | SP | 542981-766261 | 2.1415 | 19.4283 | GEN-2020-007 | 19328.3482 | 92.38 | 176.4
2001 | TC | 03 - Central | 25 | SP | 542981-766261 | 2.1415 | 19.1129 | GEN-2020-007 | 19012.8511 | 90.24 | 189
2001 | TC | 03 - Central | 25 | SP | 542981-766261 | 2.1415 | 20.0222 | GEN-2020-007 | 19922.2417 | 73.82 | 147
2001 | TC | 03 - Central | 25 | SP | 542981-766261 | 2.1415 | 20.0136 | GEN-2020-007 | 19913.6321 | 73.82 | 147
2001 | TC | 03 - Central | 25 | SP | 542981-766261 | 2.1415 | 20.0179 | GEN-2020-007 | 19917.9496 | 73.82 | 147
2001 | TC | 03 - Central | 25 | SP | 542981-766261 | 2.1415 | 21.2802 | GEN-2020-007 | 21180.1545 | 61.16 | 113.4
2001 | TC | 03 - Central | 25 | SP | 543077-764400 | 4.8573 | 15.643 | GEN-2020-073 | 15543.0219 | 66.64 | 170.4
2001 | TC | 03 - Central | 25 | SP | 543077-764400 | 4.8573 | 12.3666 | GEN-2020-073 | 12266.5686 | 83.36 | 181.05
2001 | TC | 03 - Central | 25 | SP | 547469-764310 | 3.1848 | 22.4388 | GEN-2020-079 | 22338.8486 | 56.25 | 121.8
2001 | TC | 03 - Central | 25 | SP | 547469-764310 | 3.1848 | 25.562 | GEN-2020-079 | 25461.9799 | 55.46 | 147
2001 | TC | 03 - Central | 25 | SP | 547469-764310 | 3.1848 | 19.6777 | GEN-2020-079 | 19577.6597 | 56.25 | 121.8
2001 | TC | 04 - Southeast | 25 | SP | base | 23.0699 | 0.0491 | GEN-2020-081 | -50.8866 | 200 | 237.6
2001 | TC | 04 - Southeast | 25 | SP | 511409-515800 | 5.2049 | 15.3976 | GEN-2020-075 | 15297.5805 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | SP | 511409-515800 | 5.2049 | 1.5955 | GEN-2020-087 | 1495.5066 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 511409-515800 | 5.2049 | 1.5955 | GEN-2020-087 | 1495.5066 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 511435-521052 | 4.2279 | 14.7431 | GEN-2020-016 | 14643.0543 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | SP | 511435-588779 | 5.2586 | 14.3885 | GEN-2020-016 | 14288.4559 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | SP | 511468-760938 | 4.0894 | 14.8134 | GEN-2020-074 | 14713.3517 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | SP | 511468-760938 | 4.0894 | 6.4531 | GEN-2020-085 | 6353.1089 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 511468-760938 | 4.0894 | 1.6349 | GEN-2020-085 | 1534.8677 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 511568-760938 | 4.2636 | 14.9738 | GEN-2020-074 | 14873.8281 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | SP | 511568-760938 | 4.2636 | 6.5143 | GEN-2020-085 | 6414.3422 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 511568-760938 | 4.2636 | 1.6355 | GEN-2020-085 | 1535.5431 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 520404-521190 | 4.5041 | 14.6829 | GEN-2020-016 | 14582.917 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | SP | 510419-764160 | 5.4998 | 26.3134 | GEN-2020-092 | 26213.4149 | 100 | 110
2001 | TC | 04 - Southeast | 25 | SP | 511409-764550 | 5.4175 | 16.026 | GEN-2020-075 | 15925.9987 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | SP | 511409-764550 | 5.4175 | 1.5888 | GEN-2020-087 | 1488.811 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 511409-764550 | 5.4175 | 1.5888 | GEN-2020-087 | 1488.811 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 511435-765230 | 4.2885 | 9.5266 | GEN-2020-012 | 9426.5983 | 57.88 | 66.15
2001 | TC | 04 - Southeast | 25 | SP | 511435-765230 | 4.2885 | 4081.8321 | GEN-2020-012 | 4081732.132 | 55.12 | 63
2001 | TC | 04 - Southeast | 25 | SP | 511468-764550 | 5.4991 | 16.1363 | GEN-2020-075 | 16036.2638 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | SP | 511468-764550 | 5.4991 | 1.5878 | GEN-2020-087 | 1487.7633 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 511468-764550 | 5.4991 | 1.5878 | GEN-2020-087 | 1487.7633 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 511568-764115 | 4.5504 | 17.1523 | GEN-2020-074 | 17052.3428 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | SP | 511568-764115 | 4.5504 | 7.299 | GEN-2020-085 | 7199.0148 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 511568-764115 | 4.5504 | 1.6261 | GEN-2020-085 | 1526.0922 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 515136-764115 | 2.9352 | 16.0239 | GEN-2020-074 | 15923.8779 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | SP | 515136-764115 | 2.9352 | 6.9234 | GEN-2020-085 | 6823.3669 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 515136-764115 | 2.9352 | 1.6738 | GEN-2020-085 | 1573.8341 | 250 | 270
2001 | TC | 04 - Southeast | 25 | SP | 520404-521024 | 4.5145 | 14.5959 | GEN-2020-016 | 14495.9184 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | SP | 521052-764505 | 3.7374 | 15.1284 | GEN-2020-016 | 15028.3923 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | SP | 521065-765215 | 4.9753 | 30.8719 | GEN-2020-010 | 30771.8727 | 70 | 85.05
2001 | TC | 04 - Southeast | 25 | SP | 521065-765215 | 4.9753 | 31.0088 | GEN-2020-010 | 30908.7696 | 70 | 85.05
2001 | TC | 04 - Southeast | 25 | SP | 521190-764505 | 4.033 | 15.1838 | GEN-2020-016 | 15083.8402 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | SP | 588779-511500 | 5.2582 | 14.3902 | GEN-2020-016 | 14290.2087 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | WP | base | 22.9899 | 0.0485 | GEN-2020-081 | -51.5346 | 200 | 237.6
2001 | TC | 04 - Southeast | 25 | WP | 511409-515800 | 4.9224 | 15.3983 | GEN-2020-075 | 15298.3123 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | WP | 511409-515800 | 4.9224 | 1.5969 | GEN-2020-087 | 1496.8695 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 511409-515800 | 4.9224 | 1.5969 | GEN-2020-087 | 1496.8695 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 511435-521052 | 4.181 | 14.7715 | GEN-2020-016 | 14671.5429 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | WP | 511435-588779 | 5.1673 | 14.4794 | GEN-2020-016 | 14379.4456 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | WP | 511468-760938 | 4.0427 | 14.4283 | GEN-2020-074 | 14328.322 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | WP | 511468-760938 | 4.0427 | 6.3175 | GEN-2020-085 | 6217.5471 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 511468-760938 | 4.0427 | 1.6383 | GEN-2020-085 | 1538.3236 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 511568-760938 | 4.2083 | 14.796 | GEN-2020-074 | 14696.0482 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | WP | 511568-760938 | 4.2083 | 6.4207 | GEN-2020-085 | 6320.7402 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 511568-760938 | 4.2083 | 1.6377 | GEN-2020-085 | 1537.6904 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 520404-521190 | 4.4581 | 14.783 | GEN-2020-016 | 14683.0443 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | WP | 520410-521190 | 5.9796 | 14.633 | GEN-2020-016 | 14532.9985 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | WP | 510419-764160 | 5.4948 | 23.6071 | GEN-2020-092 | 23507.0904 | 100 | 110
2001 | TC | 04 - Southeast | 25 | WP | 511409-764550 | 5.1211 | 16.049 | GEN-2020-075 | 15949.0018 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | WP | 511409-764550 | 5.1211 | 1.5901 | GEN-2020-087 | 1490.1272 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 511409-764550 | 5.1211 | 1.5901 | GEN-2020-087 | 1490.1272 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 511435-765230 | 4.2358 | 500.893 | GEN-2020-012 | 500792.9603 | 56.5 | 66.15
2001 | TC | 04 - Southeast | 25 | WP | 511435-765230 | 4.2358 | 352.6591 | GEN-2020-012 | 352559.1375 | 56.5 | 63
2001 | TC | 04 - Southeast | 25 | WP | 511468-764550 | 5.3401 | 16.2118 | GEN-2020-075 | 16111.8051 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | WP | 511468-764550 | 5.3401 | 1.5877 | GEN-2020-087 | 1487.7368 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 511468-764550 | 5.3401 | 1.5877 | GEN-2020-087 | 1487.7368 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 511568-764115 | 4.5079 | 16.7934 | GEN-2020-074 | 16693.3565 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | WP | 511568-764115 | 4.5079 | 7.1108 | GEN-2020-085 | 7010.7882 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 511568-764115 | 4.5079 | 1.6296 | GEN-2020-085 | 1529.6179 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 515136-514809 | 5.9781 | 15.694 | GEN-2020-074 | 15593.987 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | WP | 515136-514809 | 5.9781 | 6.3815 | GEN-2020-085 | 6281.5302 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 515136-514809 | 5.9781 | 1.6189 | GEN-2020-085 | 1518.8613 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 515136-764115 | 2.8432 | 16.0656 | GEN-2020-074 | 15965.5652 | 200 | 216.84
2001 | TC | 04 - Southeast | 25 | WP | 515136-764115 | 2.8432 | 6.9451 | GEN-2020-085 | 6845.0798 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 515136-764115 | 2.8432 | 1.6748 | GEN-2020-085 | 1574.782 | 250 | 270
2001 | TC | 04 - Southeast | 25 | WP | 520404-521024 | 4.4693 | 14.6637 | GEN-2020-016 | 14563.6574 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | WP | 520410-520954 | 5.9863 | 14.6056 | GEN-2020-016 | 14505.6014 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | WP | 521052-764505 | 3.7121 | 15.0937 | GEN-2020-016 | 14993.7238 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | WP | 521065-765215 | 4.9625 | 31.0384 | GEN-2020-010 | 30938.36 | 70 | 85.05
2001 | TC | 04 - Southeast | 25 | WP | 521065-765215 | 4.9625 | 31.1784 | GEN-2020-010 | 31078.4162 | 70 | 85.05
2001 | TC | 04 - Southeast | 25 | WP | 521190-764505 | 3.9942 | 15.3137 | GEN-2020-016 | 15213.6955 | 202 | 225.58
2001 | TC | 04 - Southeast | 25 | WP | 588779-511500 | 5.1729 | 14.484 | GEN-2020-016 | 14384.0058 | 202 | 225.58
2001 | TC | 05 - Southwest | 25 | SP | base | 5.4458 | 0.2604 | GEN-2020-067 | 160.4119 | 176.25 | 200.51
2001 | TC | 05 - Southwest | 25 | SP | base | 5.4458 | 0.2589 | GEN-2020-067 | 158.922 | 176.25 | 200.51
2001 | TC | 05 - Southwest | 25 | SP | base | 5.4458 | 0.0439 | GEN-2020-068 | -56.0732 | 201.87 | 237.6
2001 | TC | 05 - Southwest | 25 | SP | 511468-764550 | 5.9322 | 15.1317 | GEN-2020-009 | 15031.7022 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 511468-764550 | 5.9322 | 16.5306 | GEN-2020-009 | 16430.5648 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 511468-764550 | 5.9322 | 17.965 | GEN-2020-009 | 17865.0008 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 511468-764550 | 5.9322 | 17.2324 | GEN-2020-009 | 17132.4187 | 28.85 | 63
2001 | TC | 05 - Southwest | 25 | SP | 511468-764550 | 5.9322 | 18.7717 | GEN-2020-009 | 18671.7022 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 511468-764550 | 5.9322 | 18.8931 | GEN-2020-009 | 18793.1345 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 511468-764550 | 5.9322 | 18.9513 | GEN-2020-009 | 18851.295 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 511468-764550 | 5.9322 | 18.0017 | GEN-2020-009 | 17901.6888 | 28.85 | 66.3
2001 | TC | 05 - Southwest | 25 | SP | 511468-766291 | 2.3891 | 16.0445 | GEN-2020-009 | 15944.4819 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 511468-766291 | 2.3891 | 17.6574 | GEN-2020-009 | 17557.3735 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 511468-766291 | 2.3891 | 19.347 | GEN-2020-009 | 19247.0004 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 511468-766291 | 2.3891 | 18.1037 | GEN-2020-009 | 18003.6903 | 28.85 | 63
2001 | TC | 05 - Southwest | 25 | SP | 511468-766291 | 2.3891 | 20.2802 | GEN-2020-009 | 20180.1939 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 511468-766291 | 2.3891 | 20.4463 | GEN-2020-009 | 20346.2702 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 511468-766291 | 2.3891 | 20.5272 | GEN-2020-009 | 20427.2155 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 511468-766291 | 2.3891 | 18.9902 | GEN-2020-009 | 18890.1999 | 28.85 | 66.3
2001 | TC | 05 - Southwest | 25 | SP | 526337-526299 | 4.9113 | 0.156 | GEN-2020-060 | 55.9543 | 199.98 | 222.09
2001 | TC | 05 - Southwest | 25 | SP | 527896-764866 | 5.4405 | 1.7135 | GEN-2020-059 | 1613.5291 | 62.5 | 141.53
2001 | TC | 05 - Southwest | 25 | SP | 527896-764866 | 5.4405 | 12.9265 | GEN-2020-059 | 12826.461 | 62.5 | 141.53
2001 | TC | 05 - Southwest | 25 | SP | 527896-764866 | 5.4405 | 1.7135 | GEN-2020-059 | 1613.5282 | 62.5 | 141.53
2001 | TC | 05 - Southwest | 25 | SP | 527896-764866 | 5.4405 | 12.9264 | GEN-2020-059 | 12826.4179 | 62.5 | 141.53
2001 | TC | 05 - Southwest | 25 | SP | 764550-511409 | 5.8533 | 15.1335 | GEN-2020-009 | 15033.4966 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 764550-511409 | 5.8533 | 16.5203 | GEN-2020-009 | 16420.2728 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 764550-511409 | 5.8533 | 17.9402 | GEN-2020-009 | 17840.2068 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 764550-511409 | 5.8533 | 17.2555 | GEN-2020-009 | 17155.5106 | 28.85 | 63
2001 | TC | 05 - Southwest | 25 | SP | 764550-511409 | 5.8533 | 18.7419 | GEN-2020-009 | 18641.8817 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 764550-511409 | 5.8533 | 18.8596 | GEN-2020-009 | 18759.57 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 764550-511409 | 5.8533 | 18.9159 | GEN-2020-009 | 18815.8782 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | SP | 764550-511409 | 5.8533 | 18.0225 | GEN-2020-009 | 17922.4841 | 28.85 | 66.3
2001 | TC | 05 - Southwest | 25 | WP | base | 5.0998 | 0.2607 | GEN-2020-067 | 160.6943 | 176.25 | 200.51
2001 | TC | 05 - Southwest | 25 | WP | base | 5.0998 | 0.2592 | GEN-2020-067 | 159.1912 | 176.25 | 200.51
2001 | TC | 05 - Southwest | 25 | WP | base | 5.0998 | 0.0425 | GEN-2020-068 | -57.5338 | 201.87 | 237.6
2001 | TC | 05 - Southwest | 25 | WP | 511468-764550 | 5.5678 | 15.0988 | GEN-2020-009 | 14998.7594 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 511468-764550 | 5.5678 | 16.497 | GEN-2020-009 | 16396.9582 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 511468-764550 | 5.5678 | 17.9314 | GEN-2020-009 | 17831.3703 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 511468-764550 | 5.5678 | 17.1885 | GEN-2020-009 | 17088.5377 | 28.85 | 63
2001 | TC | 05 - Southwest | 25 | WP | 511468-764550 | 5.5678 | 18.7367 | GEN-2020-009 | 18636.6768 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 511468-764550 | 5.5678 | 18.8585 | GEN-2020-009 | 18758.5237 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 511468-764550 | 5.5678 | 18.9174 | GEN-2020-009 | 18817.3766 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 511468-764550 | 5.5678 | 17.9542 | GEN-2020-009 | 17854.2408 | 28.85 | 66.3
2001 | TC | 05 - Southwest | 25 | WP | 511468-766291 | 2.2964 | 16.0245 | GEN-2020-009 | 15924.4552 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 511468-766291 | 2.2964 | 17.6422 | GEN-2020-009 | 17542.1951 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 511468-766291 | 2.2964 | 19.3382 | GEN-2020-009 | 19238.1755 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 511468-766291 | 2.2964 | 18.0623 | GEN-2020-009 | 17962.3482 | 28.85 | 63
2001 | TC | 05 - Southwest | 25 | WP | 511468-766291 | 2.2964 | 20.2717 | GEN-2020-009 | 20171.6895 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 511468-766291 | 2.2964 | 20.4404 | GEN-2020-009 | 20340.4354 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 511468-766291 | 2.2964 | 20.5229 | GEN-2020-009 | 20422.9096 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 511468-766291 | 2.2964 | 18.9472 | GEN-2020-009 | 18847.1566 | 28.85 | 66.3
2001 | TC | 05 - Southwest | 25 | WP | 526337-526299 | 4.8814 | 0.1789 | GEN-2020-060 | 78.8741 | 199.98 | 222.09
2001 | TC | 05 - Southwest | 25 | WP | 527896-764866 | 5.2215 | 1.7153 | GEN-2020-059 | 1615.3213 | 62.5 | 141.53
2001 | TC | 05 - Southwest | 25 | WP | 527896-764866 | 5.2215 | 12.5785 | GEN-2020-059 | 12478.4841 | 62.5 | 141.53
2001 | TC | 05 - Southwest | 25 | WP | 527896-764866 | 5.2215 | 1.7153 | GEN-2020-059 | 1615.3205 | 62.5 | 141.53
2001 | TC | 05 - Southwest | 25 | WP | 527896-764866 | 5.2215 | 12.5784 | GEN-2020-059 | 12478.4459 | 62.5 | 141.53
2001 | TC | 05 - Southwest | 25 | WP | 764550-511409 | 5.5384 | 15.0863 | GEN-2020-009 | 14986.2666 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 764550-511409 | 5.5384 | 16.4672 | GEN-2020-009 | 16367.2169 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 764550-511409 | 5.5384 | 17.881 | GEN-2020-009 | 17780.9787 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 764550-511409 | 5.5384 | 17.1983 | GEN-2020-009 | 17098.2656 | 28.85 | 63
2001 | TC | 05 - Southwest | 25 | WP | 764550-511409 | 5.5384 | 18.6777 | GEN-2020-009 | 18577.6763 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 764550-511409 | 5.5384 | 18.7949 | GEN-2020-009 | 18694.9404 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 764550-511409 | 5.5384 | 18.8516 | GEN-2020-009 | 18751.5932 | 40.38 | 88.2
2001 | TC | 05 - Southwest | 25 | WP | 764550-511409 | 5.5384 | 17.9591 | GEN-2020-009 | 17859.1219 | 28.85 | 66.3

## WSCR
Study | Case Type | Region | Season Year | Season | Contingency Definition | WSCR Group | WSCR Value | Bus 1 | Bus 2 | Bus 3 | Bus 4 | Bus 5
2001 | TC | 01 - North | 25 | SP | base | 1-25SP-1 | 3.0268 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | SP | base | 1-25SP-2 | 4.5148 | GEN-2020-006 | GEN-2020-091 | GEN-2020-083
2001 | TC | 01 - North | 25 | SP | 659428-764220 | 1-25SP-2 | 2.4886 | GEN-2020-083 | GEN-2020-006 | GEN-2020-091 | GEN-2020-021
2001 | TC | 01 - North | 25 | SP | 659101-659384 | 1-25SP-1 | 4.0921 | GEN-2020-083 | GEN-2020-091 | GEN-2020-006
2001 | TC | 01 - North | 25 | SP | 659130-659428 | 1-25SP-2 | 4.5653 | GEN-2020-083 | GEN-2020-091 | GEN-2020-021
2001 | TC | 01 - North | 25 | SP | 659130-659428 | 1-25SP-4 | 2.4924 | GEN-2020-006 | GEN-2020-091 | GEN-2020-021 | GEN-2020-083
2001 | TC | 01 - North | 25 | SP | 659333-659600 | 1-25SP-1 | 4.2188 | GEN-2020-083 | GEN-2020-091 | GEN-2020-006
2001 | TC | 01 - North | 25 | SP | 652421-652651 | 1-25SP-2 | 2.6451 | GEN-2020-006 | GEN-2020-083
2001 | TC | 01 - North | 25 | SP | 659101-659576 | 1-25SP-1 | 4.4252 | GEN-2020-083 | GEN-2020-091 | GEN-2020-006
2001 | TC | 01 - North | 25 | SP | 659105-763703 | 1-25SP-1 | 4.5155 | GEN-2020-083 | GEN-2020-091 | GEN-2020-006
2001 | TC | 01 - North | 25 | SP | 659130-652806 | 1-25SP-4 | 2.4647 | GEN-2020-083 | GEN-2020-006 | GEN-2020-021 | GEN-2020-091
2001 | TC | 01 - North | 25 | SP | 659130-659433 | 1-25SP-1 | 4.5153 | GEN-2020-083 | GEN-2020-091 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | base | 1-25WP-1 | 4.7694 | GEN-2020-083 | GEN-2020-091 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659101-659105 | 1-25WP-1 | 3.0808 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659428-764220 | 1-25WP-2 | 4.8006 | GEN-2020-083 | GEN-2020-091 | GEN-2020-021
2001 | TC | 01 - North | 25 | WP | 659428-764220 | 1-25WP-4 | 2.6084 | GEN-2020-006 | GEN-2020-091 | GEN-2020-021 | GEN-2020-083
2001 | TC | 01 - North | 25 | WP | 659448-652425 | 1-25WP-1 | 2.1644 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659448-659450 | 1-25WP-1 | 3.0864 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659600-659427 | 1-25WP-1 | 3.0756 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 661048-655730 | 1-25WP-1 | 2.93 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 661048-661050 | 1-25WP-1 | 3.0823 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 661056-661055 | 1-25WP-1 | 2.989 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659101-659105 | 1-25WP-1 | 3.0808 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 661056-661104 | 1-25WP-1 | 3.0554 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 661988-661987 | 1-25WP-1 | 3.0835 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 661988-661989 | 1-25WP-1 | 3.0804 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659101-659212(1):659101-659212(2) | 1-25WP-1 | 3.0804 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659391-659349(1):659391-659349(2) | 1-25WP-1 | 3.0749 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659130-659428 | 1-25WP-2 | 4.8093 | GEN-2020-083 | GEN-2020-091 | GEN-2020-021
2001 | TC | 01 - North | 25 | WP | 659130-659428 | 1-25WP-4 | 2.6121 | GEN-2020-006 | GEN-2020-091 | GEN-2020-021 | GEN-2020-083
2001 | TC | 01 - North | 25 | WP | 659151-659186 | 1-25WP-1 | 3.0111 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659182-659183-659211 | 1-25WP-1 | 3.0586 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659183-659384 | 1-25WP-1 | 3.0577 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652391-652421 | 1-25WP-1 | 3.0526 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659183-659302-659318 | 1-25WP-1 | 3.0814 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659183-659302-659319 | 1-25WP-1 | 3.0804 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659266-659267 | 1-25WP-1 | 3.0573 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659266-659448 | 1-25WP-1 | 2.2158 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659333-659334-659335 | 1-25WP-1 | 3.0759 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659340-659341 | 1-25WP-1 | 3.0746 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659384-659387 | 1-25WP-1 | 3.0769 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652400-659334 | 1-25WP-1 | 3.0759 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659387-659388-659389 | 1-25WP-1 | 3.08 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659387-659388-659394 | 1-25WP-1 | 3.08 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659391-659466 | 1-25WP-1 | 3.081 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659391-659467 | 1-25WP-1 | 3.081 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 661047-661048-661902 | 1-25WP-1 | 2.909 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652391-655935 | 1-25WP-1 | 3.0802 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652391-655940 | 1-25WP-1 | 3.0773 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652391-661089 | 1-25WP-1 | 3.0793 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652400-652421-652621 | 1-25WP-1 | 3.0746 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652391-652400-652622 | 1-25WP-1 | 3.0747 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652400-652216 | 1-25WP-1 | 3.078 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652400-659362 | 1-25WP-1 | 3.0794 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652421-652651 | 1-25WP-1 | 2.7024 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652424-652425-652221 | 1-25WP-1 | 3.0293 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652424-652425-652220 | 1-25WP-1 | 3.0297 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 655791-652651 | 1-25WP-1 | 3.0832 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 655792-652651 | 1-25WP-1 | 3.0809 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 655925-655924 | 1-25WP-1 | 3.0748 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 655925-655926 | 1-25WP-1 | 3.0816 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652421-655793 | 1-25WP-1 | 3.0816 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659101-659212 | 1-25WP-1 | 3.0816 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659101-659212 | 1-25WP-1 | 3.0816 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659101-659218 | 1-25WP-1 | 3.0814 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659101-659420 | 1-25WP-1 | 3.0811 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659105-659060 | 1-25WP-1 | 3.0791 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659105-659111 | 1-25WP-1 | 3.0798 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652421-655925 | 1-25WP-1 | 3.075 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659105-659422 | 1-25WP-1 | 3.0808 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659105-763703 | 1-25WP-1 | 3.0816 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659105-659106-659201 | 1-25WP-1 | 3.0814 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659105-659106-659202 | 1-25WP-1 | 3.0814 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659130-652806 | 1-25WP-6 | 2.5876 | GEN-2020-083 | GEN-2020-006 | GEN-2020-021 | GEN-2020-091
2001 | TC | 01 - North | 25 | WP | 659130-659433 | 1-25WP-1 | 3.0821 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659182-652419 | 1-25WP-1 | 3.0794 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659182-655833 | 1-25WP-1 | 3.0814 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659182-659184 | 1-25WP-1 | 3.0169 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652421-659262 | 1-25WP-1 | 3.0741 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659182-659185 | 1-25WP-1 | 3.0812 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659183-659390 | 1-25WP-1 | 3.0701 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659186-659180 | 1-25WP-1 | 3.0112 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659262-659112 | 1-25WP-1 | 3.0706 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659265-659263 | 1-25WP-1 | 3.0741 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 652424-659183 | 1-25WP-1 | 2.6984 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659340-659339 | 1-25WP-1 | 3.0746 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659351-659350 | 1-25WP-1 | 3.0816 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659351-659352 | 1-25WP-1 | 3.0715 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659384-659385-659386 | 1-25WP-1 | 3.0811 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659388-655849 | 1-25WP-1 | 3.0815 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659388-655873 | 1-25WP-1 | 3.0814 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659388-655881 | 1-25WP-1 | 3.0817 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659388-655882 | 1-25WP-1 | 3.0824 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 655790-659151 | 1-25WP-1 | 3.081 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659388-655899 | 1-25WP-1 | 3.0817 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659388-659584 | 1-25WP-1 | 3.0741 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659391-655844 | 1-25WP-1 | 3.0817 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659391-655856 | 1-25WP-1 | 3.0822 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659391-655889 | 1-25WP-1 | 3.0814 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659391-659349 | 1-25WP-1 | 3.0805 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659391-659349 | 1-25WP-1 | 3.0807 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659392-659390-659466 | 1-25WP-1 | 3.081 | GEN-2020-083 | GEN-2020-006
2001 | TC | 01 - North | 25 | WP | 659393-659390-659467 | 1-25WP-1 | 3.081 | GEN-2020-083 | GEN-2020-006
2001 | TC | 02 - Nebraska | 25 | SP | 530583-765035 | 2-25SP-1 | 4.9595 | GEN-2020-070 | GEN-2020-011
2001 | TC | 02 - Nebraska | 25 | WP | 530583-765035 | 2-25WP-1 | 4.7289 | GEN-2020-070 | GEN-2020-011
2001 | TC | 03 - Central | 25 | WP | 532934-543650 | 3-25WP-1 | 2.0409 | GEN-2020-089,GEN-2015-016 | GEN-2020-073
2001 | TC | 03 - Central | 25 | SP | 532934-543650 | 3-25SP-1 | 2.2276 | GEN-2020-089,GEN-2015-016 | GEN-2020-073
2001 | TC | 04 - Southeast | 25 | SP | base | 4-25SP-1 | 4.1083 | GEN-2020-016 | GEN-2020-012
2001 | TC | 04 - Southeast | 25 | WP | base | 4-25WP-1 | 4.043 | GEN-2020-016 | GEN-2020-012
2001 | TC | 05 - Southwest | 25 | SP | 525549-523961 | 5-25SP-1 | 3.8476 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 525549-523961 | 5-25SP-1 | 3.8476 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 525832-764945 | 5-25SP-1 | 2.6762 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 527020-527000 | 5-25SP-1 | 3.6149 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 527896-764866 | 5-25SP-1 | 2.4951 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 560022-515458 | 5-25SP-1 | 3.8259 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 760938-511568 | 5-25SP-1 | 3.8505 | GEN-2020-059 | GEN-2020-067, GEN-2020-068
2001 | TC | 05 - Southwest | 25 | SP | 525549-523961(1):525549-523961(2) | 5-25SP-1 | 5.4816 | GEN-2020-062 | GEN-2020-059 | GEN-2020-017
2001 | TC | 05 - Southwest | 25 | SP | 525549-523961(1):525549-523961(2) | 5-25SP-10 | 3.8154 | GEN-2020-059 | GEN-2020-067, GEN-2020-068
2001 | TC | 05 - Southwest | 25 | SP | 525549-523961(1):525549-523961(2) | 5-25SP-2 | 2.9284 | GEN-2020-062 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 525549-527656 | 5-25SP-1 | 3.7501 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 511456-763215 | 5-25SP-1 | 3.8421 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 526935-526936-526937 | 5-25SP-1 | 3.1403 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 511468-760938 | 5-25SP-1 | 3.8506 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 560022-762467 | 5-25SP-1 | 3.8483 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 560022-763215 | 5-25SP-1 | 3.8429 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 511468-762467 | 5-25SP-1 | 3.8432 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 511456-766291 | 5-25SP-1 | 3.8407 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 511468-763215 | 5-25SP-1 | 3.8478 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | SP | 511468-766291 | 5-25SP-1 | 3.835 | GEN-2020-067, GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 525549-523961 | 5-25WP-1 | 3.6685 | GEN-2020-059 | GEN-2020-067,GEN-2020-068
2001 | TC | 05 - Southwest | 25 | WP | 525549-523961 | 5-25WP-1 | 3.6685 | GEN-2020-059 | GEN-2020-067,GEN-2020-068
2001 | TC | 05 - Southwest | 25 | WP | 525832-764945 | 5-25WP-1 | 2.6338 | GEN-2020-067,GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 527020-527000 | 5-25WP-1 | 3.4403 | GEN-2020-067,GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 527896-764866 | 5-25WP-1 | 2.3363 | GEN-2020-067,GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 560022-515458 | 5-25WP-1 | 3.6292 | GEN-2020-067,GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 760938-511568 | 5-25WP-1 | 3.6691 | GEN-2020-067,GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 764550-511409 | 5-25WP-1 | 3.6611 | GEN-2020-067,GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 525549-523961(1):525549-523961(2) | 5-25WP-1 | 5.3241 | GEN-2020-062 | GEN-2020-059 | GEN-2020-017
2001 | TC | 05 - Southwest | 25 | WP | 525549-523961(1):525549-523961(2) | 5-25WP-10 | 3.6295 | GEN-2020-059 | GEN-2020-067,GEN-2020-068
2001 | TC | 05 - Southwest | 25 | WP | 525549-523961(1):525549-523961(2) | 5-25WP-2 | 2.7932 | GEN-2020-062 | GEN-2020-067,GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 525549-527656 | 5-25WP-1 | 3.5762 | GEN-2020-067,GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 511456-763215 | 5-25WP-1 | 3.6553 | GEN-2020-067,GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 526935-526936-526937 | 5-25WP-1 | 2.9995 | GEN-2020-067,GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 511468-760938 | 5-25WP-1 | 3.6691 | GEN-2020-067,GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 511456-766291 | 5-25WP-1 | 3.6532 | GEN-2020-067,GEN-2020-068 | GEN-2020-059
2001 | TC | 05 - Southwest | 25 | WP | 511468-766291 | 5-25WP-1 | 3.6439 | GEN-2020-067,GEN-2020-068 | GEN-2020-059