## Executive Summary
Executive Summary: DISIS-2020-001 Phase 2 of Power Flow, Stability, and Short-Circuit
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on April 30, 2020. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 2.2 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2020-001 Phase 2 includes study requests in the following cluster groups: ( 01 - North, 02 - Nebraska, 03 - Central, 04 - Southeast, 05 - Southwest)
DISIS Manual Version 2.2
https://www.spp.org/documents/71111/disis-study-manual.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
14,441.39 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $1,274,487,606.39 Steady State Network Upgrade $460,020,358.25 Stability Network Upgrade $17,200,000.00 Steady State/Stability Network Upgrade $70,410,000.00 Interconnection Costs: $726,857,248.14
Models Used in Steady State Study
2022 ITP Series
Winter: 2027
Summer: 2024, 2027
Light: 2027
Models Used in Stability Study
2020 MDWG
Winter: 2025, Summer: 2025
By: SPP Generator Interconnection Department
Published: February 16, 2024
Costs for Solar/Battery Requests were allocated using the 27SP (summer peak) model.
Costs for Wind Requests were allocated using the 27L (light load) model.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.

## Revision History
Revision History
Date | Author | Change Description
4532400% | SPP | Phase 2 Draft Posting
4533800% | SPP | Phase 2 Final Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4533800% | LOIS/Service Type | 4 | Requests | Updated LOIS amounts based on constraints, aligned correct service type for ER/NR requests, update GEN-2020-059 MW size studied.
4533800% | Upgrade Details | 6 | Assigned Upgrade Cost | Updated GEN-2020-059 MW size in the Upgrade Details
4533800% | Upgrade Details | 7 | Upgrade Summary | Updated GEN-2020-059 MW size in the Upgrade Details
4533800% | Upgrade Assigned | 5 | Constraints Summary | Removed the 70th & Bluff - Sub 1214 161 kV Rebuild and Transformer Replacement contingent upgrade (2023 ITP project) due to duplicate mitigation
4533800% | Upgrade Assigned | 6 | Assigned Upgrade Cost | Removed the 70th & Bluff - Sub 1214 161 kV Rebuild and Transformer Replacement contingent upgrade (2023 ITP project) due to duplicate mitigation
4533800% | Upgrade Assigned | 7 | Upgrade Summary | Removed the 70th & Bluff - Sub 1214 161 kV Rebuild and Transformer Replacement contingent upgrade (2023 ITP project) due to duplicate mitigation
4533800% | Upgrade Name | 5 | Constraints Summary | Updated the Sunnyside transformer upgrade name and description, replacing "3rd transformer" with "Circuit ID 3"
4533800% | Upgrade Name | 6 | Assigned Upgrade Cost | Updated the Sunnyside transformer upgrade name and description, replacing "3rd transformer" with "Circuit ID 3"
4533800% | Upgrade Name | 7 | Upgrade Summary | Updated the Sunnyside transformer upgrade name and description, replacing "3rd transformer" with "Circuit ID 3"
4533800% | TO Name | 7 | Upgrade Summary | Updated TO owner from KCPL to EDE
4533800% | Interconnection Costs | 6 | Upgrade Summary | Updated interconnection costs for NPPD Non-Shared Network Upgrades (GEN-2020-069, GEN-2020-007, and GEN-2020-013)
4533800% | Interconnection Costs | 7 | Assigned Upgrade Cost | Updated interconnection costs for NPPD Non-Shared Network Upgrades (GEN-2020-069, GEN-2020-007, and GEN-2020-013)
4533800% | Upgrade Name | 5 | Constraints Summary | Updated upgrade name and description for the rebuild of the MORRILL7 to GERINGT_-TS7 115kV line to indicate it is not a SPP facility
4533800% | Upgrade Name/Allocated Cost | 6 | Assigned Upgrade Cost | Updated upgrade name and description for the rebuild of the MORRILL7 to GERINGT_-TS7 115kV line to indicate it is not a SPP facility. Update the allocated cost to 0
4533800% | Upgrade Name/TO Name | 7 | Upgrade Summary | Updated upgrade name and description for the rebuild of the MORRILL7 to GERINGT_-TS7 115kV line to indicate it is not a SPP facility. Update the TO owner from WAPA to WAPA RMR
4533800% | Upgrade Assigned | 7 | Assigned Upgrade Cost | Removed the OGALALA4 to SIDNEY___TS4 230kV Rebuild upgrade from GEN-2020-070, updated the allocated cost to the remaining queue
4533800% | Upgrade Details | 6 | Assigned Upgrade Cost | Updated the mileage for the HOLDREG7 to G20-013-TAP 115kV rebuild from 0.4 miles to 19 miles
4533800% | Upgrade Details | 7 | Upgrade Summary | Updated the mileage for the HOLDREG7 to G20-013-TAP 115kV rebuild from 0.4 miles to 19 miles
4533800% | Interconnection Costs | 6 | Upgrade Summary | Updated the interconnection cost for UID 156980 from $1,381,735.00 to $21,693,802.00
4533800% | Interconnection Costs | 7 | Assigned Upgrade Cost | Updated the interconnection cost for UID 156980 from $1,381,735.00 to $21,693,802.00
4533800% | Upgrade Details | 6 | Assigned Upgrade Cost | Updated the upgrade details for the contingent upgrade - HOLT.CO3 to ANTELOPE 3 345kV line
4533800% | Upgrade Details | 7 | Upgrade Summary | Updated the upgrade details for the contingent upgrade - HOLT.CO3 to ANTELOPE 3 345kV line
4533800% | Network Upgrade Costs | 1 | Executive Summary | Updated the Steady State Network Upgrade, Interconnection Costs, and total Network Upgrade costs

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2020-006 | 01 - North | 22 | DIS-20-1 | Solar | 250 | 0 | Stability | -48.9 | ER/NR | BEPC | Bowman 230kV substation | DISIS STAGE
GEN-2020-014 | 01 - North | 22 | DIS-20-1 | Thermal | 45 | 0 | Stability | 0 | ER/NR | BEPC | Lonesome Creek 115kV | DISIS STAGE
GEN-2020-021 | 01 - North | 22 | DIS-20-1 | Wind | 235 | 235 | None | -40.01 | ER/NR | BEPC | LeLand Olds-Chapelle Creek 345kV line | DISIS STAGE
GEN-2020-083 | 01 - North | 22 | DIS-20-1 | Hybrid | 74.5 | 0 | Stability | -1.92 | ER/NR | WAPA | Fairview 115kV Substation | DISIS STAGE
GEN-2020-091 | 01 - North | 22 | DIS-20-1 | Solar | 150 | 0 | Stability | -1.64 | ER/NR | BEPC | Patent Gate Substation 345 kV | DISIS STAGE
GEN-2020-001 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 200 | 200 | None | -36.23 | ER/NR | BEPC | Sidney 345 kV Substation | DISIS STAGE
GEN-2020-002 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 81 | 74.2619 | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 ftlo P23:345:ITCGP:SV_BRK382:::EHV: | -7.76 | ER | OPPD | 6846 Substation 69 kV | DISIS STAGE
GEN-2020-011 | 02 - Nebraska | 22 | DIS-20-1 | Hybrid | 320 | 320 | None | -64.9 | ER/NR | NPPD | Axtell-Sweetwater Substation 345kV | DISIS STAGE
GEN-2020-013 | 02 - Nebraska | 22 | DIS-20-1 | Hybrid | 215 | 215 | None | -49.8 | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | DISIS STAGE
GEN-2020-025 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 255 | 206.39 | 646254 S1254 5 161 646281 S1281 5 161 1 ftlo 646362 S1362 5 161 646363 S1363 5 161 1 | 0 | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-027 | 02 - Nebraska | 22 | DIS-20-1 | Hybrid | 50 | 45.8407 | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 ftlo P23:345:ITCGP:SV_BRK382:::EHV: | -0.2 | ER | OPPD | S1281 - S1362 161kV (S1363) | DISIS STAGE
GEN-2020-028 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 255 | 206.39 | 646254 S1254 5 161 646281 S1281 5 161 1 ftlo 646362 S1362 5 161 646363 S1363 5 161 1 | 0 | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-030 | 02 - Nebraska | 22 | DIS-20-1 | Hybrid | 50 | 45.8407 | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 ftlo P23:345:ITCGP:SV_BRK382:::EHV: | -0.4 | ER | OPPD | S1281 - S1362 161kV (S1363) | DISIS STAGE
GEN-2020-031 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 303 | 245.25 | 646254 S1254 5 161 646281 S1281 5 161 1 ftlo 646362 S1362 5 161 646363 S1363 5 161 1 | 0 | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-033 | 02 - Nebraska | 22 | DIS-20-1 | Hybrid | 50 | 45.8407 | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 ftlo P23:345:ITCGP:SV_BRK382:::EHV: | -0.2 | ER | OPPD | S1281 - S1362 161kV (S1363) | DISIS STAGE
GEN-2020-036 | 02 - Nebraska | 22 | DIS-20-1 | Hybrid | 303 | 277.7946 | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 ftlo P23:345:ITCGP:SV_BRK382:::EHV: | -32.47 | ER | OPPD | Substation 3740; 345kV | DISIS STAGE
GEN-2020-038 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 303 | 303 | None | 0 | ER | OPPD | Substation 3740; 345kV | DISIS STAGE
GEN-2020-043 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 56.52 | 56.52 | None | -0.58 | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-044 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 56.52 | 56.52 | None | -0.58 | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-045 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 56.52 | 56.52 | None | -0.58 | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-069 | 02 - Nebraska | 22 | DIS-20-1 | Wind | 52.85 | 52.85 | None | -0.64 | ER/NR | NPPD | Cody to Valentine 115kV line | DISIS STAGE
GEN-2020-070 | 02 - Nebraska | 22 | DIS-20-1 | Wind | 255 | 109.6934 | 530582 S HAYS6 230 539679 GRTBEND6 230 1 ftlo P23:345:ITCGP:SV_BRK382:::EHV: | -10.09 | ER | ITCGP | Postrock to Axtell 345 KV line | DISIS STAGE
GEN-2020-077 | 02 - Nebraska | 22 | DIS-20-1 | Wind | 151.2 | 61.1358 | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 ftlo 530583 POSTROCK7 345 765035 G20-070-TAP 345 1 | -5.67 | ER | NPPD | North Hebron to Fairbury 115 kV | DISIS STAGE
GEN-2020-078 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 100 | 100 | None | -2.57 | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | DISIS STAGE
GEN-2020-084 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 350 | 320.8848 | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 ftlo P23:345:ITCGP:SV_BRK382:::EHV: | -3 | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | DISIS STAGE
GEN-2020-094 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 250 | 250 | None | -7.13 | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | DISIS STAGE
ASGI-2020-001 | 03 - Central | 22 | DIS-20-1 | Hybrid | 35 | 17.1586 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 ftlo P12:345:WERE:ROSE-WOLF-345:::EHV: | -0.28 | ER | KCPL | South Waverly 69 kV Substation | DISIS STAGE
ASGI-2020-003 | 03 - Central | 22 | DIS-20-1 | Hybrid | 35 | 17.1586 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 ftlo P12:345:WERE:ROSE-WOLF-345:::EHV: | -0.28 | ER | KCPL | Caroltown 161 kV Substation | DISIS STAGE
GEN-2020-003 | 03 - Central | 22 | DIS-20-1 | Thermal | 58 | 58 | None | 0 | ER/NR | WERE | East Substation 69 kV | DISIS STAGE
GEN-2020-007 | 03 - Central | 22 | DIS-20-1 | Hybrid | 650 | 215.3178 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 ftlo 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | -11.21 | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | DISIS STAGE
GEN-2020-008 | 03 - Central | 22 | DIS-20-1 | Hybrid | 250 | 250 | None | -49.82 | ER | SPS | Corporation Carpenter 345kV Substation | DISIS STAGE
GEN-2020-052 | 03 - Central | 22 | DIS-20-1 | Wind | 251 | 251 | None | -7.33 | ER/NR | WERE | Neosho-Delaware 345 kV | DISIS STAGE
GEN-2020-056 | 03 - Central | 22 | DIS-20-1 | Solar | 20 | 20 | None | -1.01 | ER/NR | SUNC | Russell 115 kV Substation | DISIS STAGE
GEN-2020-057 | 03 - Central | 22 | DIS-20-1 | Battery/Storage | 424.5 | 122.0446 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 ftlo 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | -63.07 | ER/NR | KCPL | Atlantic 345 kV Substation | DISIS STAGE
GEN-2020-058 | 03 - Central | 22 | DIS-20-1 | Solar | 424.5 | 122.0446 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 ftlo 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | -95.36 | ER/NR | KCPL | Atlantic 345 kV Substation | DISIS STAGE
GEN-2020-061 | 03 - Central | 22 | DIS-20-1 | Thermal | 29 | 29 | None | 0 | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | DISIS STAGE
GEN-2020-064 | 03 - Central | 22 | DIS-20-1 | Thermal | 64 | 64 | None | 0 | ER/NR | EDE | 4544 Stateline CC 161kV Substation | DISIS STAGE
GEN-2020-071 | 03 - Central | 22 | DIS-20-1 | Wind | 252 | 176.5042 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | -7.56 | ER | WERE | Swissvale to Morris 230 KV line | DISIS STAGE
GEN-2020-072 | 03 - Central | 22 | DIS-20-1 | Hybrid | 150 | 150 | None | -3.59 | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | DISIS STAGE
GEN-2020-073 | 03 - Central | 22 | DIS-20-1 | Hybrid | 150 | 13.4014 | 543067 CENTENL5 161 543069 PAOLA 5 161 1 ftlo P12:161:WERE:MARM-KCPL-161:::HV: | -3.69 | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | DISIS STAGE
GEN-2020-076 | 03 - Central | 22 | DIS-20-1 | Battery/Storage | 200 | 147.2796 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 ftlo 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | -44.59 | ER/NR | WERE | Benton to Wolf Creek 345 kV Line | DISIS STAGE
GEN-2020-079 | 03 - Central | 22 | DIS-20-1 | Hybrid | 225 | 225 | None | 3.74 | ER/NR | EDE | Riverton-Neosho 161kV line | DISIS STAGE
GEN-2020-086 | 03 - Central | 22 | DIS-20-1 | Solar | 500 | 368.1989 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 ftlo 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | -124.98 | ER/NR | WERE | Benton to Wolf Creek 345 kV Line | DISIS STAGE
GEN-2020-088 | 03 - Central | 22 | DIS-20-1 | Solar | 150 | 150 | None | -28.08 | ER/NR | EDE | La Russell 161 kV Substation | DISIS STAGE
GEN-2020-089 | 03 - Central | 22 | DIS-20-1 | Solar | 104 | 9.2916 | 543067 CENTENL5 161 543069 PAOLA 5 161 1 ftlo P12:161:WERE:MARM-KCPL-161:::HV: | -10.83 | ER/NR | KCPL | Dakota 161 kV Substation | DISIS STAGE
GEN-2020-090 | 03 - Central | 22 | DIS-20-1 | Solar | 204.3 | 204.3 | None | -19.06 | ER/NR | WERE | Wolf Creek- Blackberry 345 kV Substation | DISIS STAGE
GEN-2020-010 | 04 - Southeast | 22 | DIS-20-1 | Hybrid | 140 | 140 | None | -1.55 | ER/NR | WFEC | Seiling-Taloga Substations 138kV | DISIS STAGE
GEN-2020-012 | 04 - Southeast | 22 | DIS-20-1 | Hybrid | 113 | 113 | None | -1.4 | ER/NR | AEPW | Snyder-Altus Jct. 138kV | DISIS STAGE
GEN-2020-015 | 04 - Southeast | 22 | DIS-20-1 | Solar | 104 | 25.7613 | 505602 S BROWN4 138 521044 RUSSETT4 138 1 ftlo P23:345:AEPW:PITTSBURG CB 3429A NBTB:::: | -0.8 | ER/NR | OGE | Johnston County 345 kV Substation | DISIS STAGE
GEN-2020-016 | 04 - Southeast | 22 | DIS-20-1 | Wind | 202 | 202 | None | -7.1 | ER/NR | WFEC | Snyder SW-Cache 138 kV line | DISIS STAGE
GEN-2020-020 | 04 - Southeast | 22 | DIS-20-1 | Hybrid | 201.6 | 201.6 | None | -3.1 | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | DISIS STAGE
GEN-2020-023 | 04 - Southeast | 22 | DIS-20-1 | Battery/Storage | 202 | 202 | None | -1.6 | ER/NR | OGE | Woodring 345 KV Station | DISIS STAGE
GEN-2020-054 | 04 - Southeast | 22 | DIS-20-1 | Solar | 298 | 298 | None | -4.8 | ER/NR | AEPW | Lydia 345 kV Station | DISIS STAGE
GEN-2020-074 | 04 - Southeast | 22 | DIS-20-1 | Battery/Storage | 200 | 175.4827 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 ftlo 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | -0.6 | ER/NR | AEPW | Lawton to Sunnyside 345 kV Substation | DISIS STAGE
GEN-2020-075 | 04 - Southeast | 22 | DIS-20-1 | Battery/Storage | 200 | 175.4827 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 ftlo 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | -0.6 | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-081 | 04 - Southeast | 22 | DIS-20-1 | Battery/Storage | 200 | 200 | None | -6 | ER/NR | AEPW | Tenaska Switching Substation 345kV | DISIS STAGE
GEN-2020-085 | 04 - Southeast | 22 | DIS-20-1 | Solar | 500 | 438.7067 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 ftlo 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | -0.3 | ER/NR | AEPW | Lawton to Sunnyside 345 kV Line | DISIS STAGE
GEN-2020-087 | 04 - Southeast | 22 | DIS-20-1 | Solar | 500 | 438.7067 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 ftlo 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | -0.3 | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-092 | 04 - Southeast | 22 | DIS-20-1 | Solar | 100 | 100 | None | -1.8 | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | DISIS STAGE
GEN-2020-009 | 05 - Southwest | 22 | DIS-20-1 | Hybrid | 300 | 263.224 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 ftlo 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | -9.4 | ER/NR | AEPW | Lawton East Side to Oklaunion 345kV | DISIS STAGE
GEN-2020-017 | 05 - Southwest | 22 | DIS-20-1 | Solar | 74.88 | 74.88 | None | -0.7 | ER/NR | SPS | 230kV Lamb County Interchange | DISIS STAGE
GEN-2020-059 | 05 - Southwest | 22 | DIS-20-1 | Hybrid | 250 | 250 | None | -3.6 | ER | SPS | Tuco-Yoakum-Hobbs 345 kV | DISIS STAGE
GEN-2020-060 | 05 - Southwest | 22 | DIS-20-1 | Battery/Storage | 200 | 200 | None | -1 | ER | SPS | Lubbock East Substation 230 kV | DISIS STAGE
GEN-2020-062 | 05 - Southwest | 22 | DIS-20-1 | Solar | 256 | 256 | None | -5.5 | ER | SPS | OASIS 230kV Substation | DISIS STAGE
GEN-2020-065 | 05 - Southwest | 22 | DIS-20-1 | Thermal | 1003 | 0 | Non-Converged ftlo 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 | 6.4 | ER | SPS | Hobbs-Andrews 345 kV Line | DISIS STAGE
GEN-2020-067 | 05 - Southwest | 22 | DIS-20-1 | Wind | 352.5 | 352.5 | None | -116.7 | ER | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2020-068 | 05 - Southwest | 22 | DIS-20-1 | Solar | 400 | 400 | None | -11.4 | ER | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2018-067 | 01 - North | 21 | DIS-18-2 | Wind | 255 |  |  |  | ER | BEPC | 115kV Strandahl sub | DISIS STAGE
GEN-2018-069 | 01 - North | 21 | DIS-18-2 | Wind | 125 |  |  |  | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2018-074 | 01 - North | 21 | DIS-18-2 | Wind | 78 |  |  |  | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2019-019 | 01 - North | 21 | DIS-19-1 | Thermal | 15.15 |  |  |  | ER/NR | BEPC | Siouxland 69kV | DISIS STAGE
GEN-2019-023 | 01 - North | 21 | DIS-19-1 | Wind | 110 |  |  |  | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2019-037 | 01 - North | 21 | DIS-19-1 | Solar | 150 |  |  |  | ER/NR | BEPC | Leland Olds 345kV substation | DISIS STAGE
GEN-2018-065 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 19.8 |  |  |  | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-068 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 302.4 |  |  |  | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-083 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 250 |  |  |  | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | DISIS STAGE
GEN-2018-125 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 231 |  |  |  | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | DISIS STAGE
GEN-2018-131 | 02 - Nebraska | 21 | DIS-18-2 | Solar | 221.4 |  |  |  | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2018-132 | 02 - Nebraska | 21 | DIS-18-2 | Solar | 201.6 |  |  |  | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2019-009 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 100 |  |  |  | ER | OPPD | S1263 Brock 161kV substation | DISIS STAGE
GEN-2019-039 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 174.5 |  |  |  | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | DISIS STAGE
GEN-2019-041 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 78 |  |  |  | ER/NR | NPPD | 115kV Monolith Substation | DISIS STAGE
GEN-2019-069 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 100 |  |  |  | ER | NPPD | Shell Creek-Hoskins 345kV Line | DISIS STAGE
GEN-2019-070 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 50 |  |  |  | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2019-073 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 100 |  |  |  | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2018-063 | 03 - Central | 21 | DIS-18-2 | Solar | 57 |  |  |  | ER | EMDE | Sedalia Marshfield Springfield Nichols Street 69kV circuit | DISIS STAGE
GEN-2018-108 | 03 - Central | 21 | DIS-18-2 | Storage | 95 |  |  |  | ER | SUNC | Thistle 345kV substation | DISIS STAGE
GEN-2018-116 | 03 - Central | 21 | DIS-18-2 | Solar | 150 |  |  |  | ER/NR | SUNC | Frey Street 115kV bus | DISIS STAGE
GEN-2018-128 | 03 - Central | 21 | DIS-18-2 | Wind | 200.22 |  |  |  | ER/NR | WERE | Renfrow-Viola 345 kV | DISIS STAGE
GEN-2019-001 | 03 - Central | 21 | DIS-19-1 | Wind | 25 |  |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-014 | 03 - Central | 21 | DIS-19-1 | Solar | 125 |  |  |  | ER/NR | SUNC | Holcomb 115kV substation | DISIS STAGE
GEN-2019-016 | 03 - Central | 21 | DIS-19-1 | Solar | 200 |  |  |  | ER | EMDE | Dadeville 161kV Substation | DISIS STAGE
GEN-2019-018 | 03 - Central | 21 | DIS-19-1 | Thermal | 15.56 |  |  |  | ER/NR | MIDW | Saxman 115kV substation | DISIS STAGE
GEN-2019-030 | 03 - Central | 21 | DIS-19-1 | Wind | 252 |  |  |  | ER/NR | SUNC | Spearville to Clark County 345 kV line | DISIS STAGE
GEN-2019-035 | 03 - Central | 21 | DIS-19-1 | Solar | 80 |  |  |  | ER/NR | EMDE | Reeds Spring-Aurora 161kV Line | DISIS STAGE
GEN-2019-044 | 03 - Central | 21 | DIS-19-1 | Solar | 100 |  |  |  | ER | SUNC | North Fort Dodge 115kV Substation | DISIS STAGE
GEN-2019-048 | 03 - Central | 21 | DIS-19-1 | Storage | 50 |  |  |  | ER | AEPW | Duncan 69kV substation | DISIS STAGE
GEN-2019-051 | 03 - Central | 21 | DIS-19-1 | Storage | 40 |  |  |  | ER/NR | SUNC | Frey St 115kV bus | DISIS STAGE
GEN-2019-053 | 03 - Central | 21 | DIS-19-1 | Storage | 50 |  |  |  | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-054 | 03 - Central | 21 | DIS-19-1 | Solar | 150 |  |  |  | ER/NR | SUNC | Great Bend- Circle 230kV line | DISIS STAGE
GEN-2019-055 | 03 - Central | 21 | DIS-19-1 | Solar | 150 |  |  |  | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-058 | 03 - Central | 21 | DIS-19-1 | Solar | 150 |  |  |  | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-063 | 03 - Central | 21 | DIS-19-1 | Storage | 50 |  |  |  | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-068 | 03 - Central | 21 | DIS-19-1 | Storage | 50 |  |  |  | ER/NR | SUNC | Great Bend - Circle 230kV line | DISIS STAGE
GEN-2018-064 | 04 - Southeast | 21 | DIS-18-2 | Solar | 80 |  |  |  | ER/NR | GRDA | Tonnece Substation 69kV | DISIS STAGE
GEN-2018-071 | 04 - Southeast | 21 | DIS-18-2 | Storage | 151 |  |  |  | ER/NR | OGE | Ranch Road 345 kV | DISIS STAGE
GEN-2018-072 | 04 - Southeast | 21 | DIS-18-2 | Storage | 151 |  |  |  | ER/NR | OGE | Ranch Road 345 kV | DISIS STAGE
GEN-2018-079 | 04 - Southeast | 21 | DIS-18-2 | Solar | 148 |  |  |  | ER | AEPW | Farmland-Delaware 138kV line | DISIS STAGE
GEN-2018-082 | 04 - Southeast | 21 | DIS-18-2 | Wind | 215 |  |  |  | ER | AEPW | Pittsburg 345kV Substation | DISIS STAGE
GEN-2018-088 | 04 - Southeast | 21 | DIS-18-2 | Solar | 130 |  |  |  | ER | AEPW | Lydia 345kV substation | DISIS STAGE
GEN-2018-106 | 04 - Southeast | 21 | DIS-18-2 | Solar | 165 |  |  |  | ER | AEPW | Longwood 345kV substation | DISIS STAGE
GEN-2018-115 | 04 - Southeast | 21 | DIS-18-2 | Solar | 250 |  |  |  | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | DISIS STAGE
GEN-2019-002 | 04 - Southeast | 21 | DIS-19-1 | Storage | 100 |  |  |  | ER | GRDA | Maid 161kV substation | DISIS STAGE
GEN-2019-012 | 04 - Southeast | 21 | DIS-19-1 | Storage | 200 |  |  |  | ER/NR | OGE | Woodward 345kV substation | DISIS STAGE
GEN-2019-013 | 04 - Southeast | 21 | DIS-19-1 | Storage | 50 |  |  |  | ER/NR | AEPW | Dempsey 230kV sub/Sweetwater 230kV | DISIS STAGE
GEN-2019-045 | 04 - Southeast | 21 | DIS-19-1 | Solar | 155 |  |  |  | ER | OGE | DeGrasse 138kV Substation | DISIS STAGE
GEN-2019-065 | 04 - Southeast | 21 | DIS-19-1 | Storage | 180 |  |  |  | ER | AEPW | Overton-Northwest Henderson 138kV | DISIS STAGE
GEN-2018-089 | 05 - Southwest | 21 | DIS-18-2 | Wind | 196 |  |  |  | ER | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2018-099 | 05 - Southwest | 21 | DIS-18-2 | Wind | 300 |  |  |  | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2019-003 | 05 - Southwest | 21 | DIS-19-1 | Solar | 150 |  |  |  | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-011 | 05 - Southwest | 21 | DIS-19-1 | Storage | 230 |  |  |  | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2019-021 | 05 - Southwest | 21 | DIS-19-1 | Solar | 50 |  |  |  | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
ASGI-2017-013 | 01 - North | 20 | DIS-18-1 | Wind | 40 |  |  |  | ER | WAPA | Wolsey 69kV Substation | DISIS STAGE
GEN-2018-008 | 01 - North | 20 | DIS-18-1 | Wind | 252 |  |  |  | ER/NR | WAPA | Groton-Leland Olds 345kV Line | FACILITY STUDY STAGE
GEN-2018-010 | 01 - North | 20 | DIS-18-1 | Storage | 74.1 |  |  |  | ER/NR | WAPA | Neset 230kV Substation | FACILITY STUDY STAGE
GEN-2018-039 | 01 - North | 20 | DIS-18-1 | Solar | 72 |  |  |  | ER/NR | WAPA | Edgeley 115kV substation | FACILITY STUDY STAGE
GEN-2018-012 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 74.1 |  |  |  | ER/NR | NPPD | Antelope 345kV Substation | FACILITY STUDY STAGE
GEN-2018-025 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 200 |  |  |  | ER | OPPD | Fort Calhoun 345kV Substation | FACILITY STUDY STAGE
GEN-2018-033 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 200 |  |  |  | ER | OPPD | Cass County 345kV Substation | FACILITY STUDY STAGE
GEN-2018-037 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 100 |  |  |  | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | FACILITY STUDY STAGE
GEN-2018-043 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 500 |  |  |  | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | FACILITY STUDY STAGE
GEN-2018-056 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 102.6 |  |  |  | ER/NR | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | FACILITY STUDY STAGE
GEN-2018-060 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 50 |  |  |  | ER/NR | NPPD | Axtell-Post Rock 345 kV | FACILITY STUDY STAGE
ASGI-2018-003 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  |  | ER | KCPL | AP City 69kV Substation | DISIS STAGE
ASGI-2018-006 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  |  | ER | KCPL | Metz 69kV Substation | DISIS STAGE
ASGI-2018-007 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  |  | ER | KCPL | Salisbury 161kV Substation | DISIS STAGE
ASGI-2018-010 | 03 - Central | 20 | DIS-18-1 | Solar | 35 |  |  |  | ER | KCPL | Pleasant Valley 161kV Substation | DISIS STAGE
ASGI-2018-011 | 03 - Central | 20 | DIS-18-1 | Solar | 35 |  |  |  | ER | KCPL | South Ottawa 161kV Substation | DISIS STAGE
GEN-2018-009 | 03 - Central | 20 | DIS-18-1 | Wind | 150 |  |  |  | ER | SUNC | Cimarron 115kV Substation | FACILITY STUDY STAGE
GEN-2018-013 | 03 - Central | 20 | DIS-18-1 | Wind | 74.1 |  |  |  | ER | WERE | Abilene Energy Center-Northview 115kV Line | FACILITY STUDY STAGE
GEN-2018-022 | 03 - Central | 20 | DIS-18-1 | Solar | 300 |  |  |  | ER/NR | KCPL | Mullen Creek 345kV Substation | FACILITY STUDY STAGE
GEN-2018-030 | 03 - Central | 20 | DIS-18-1 | Storage | 200 |  |  |  | ER | SPS | Lamar-Finney 345kV Substation | FACILITY STUDY STAGE
GEN-2018-031 | 03 - Central | 20 | DIS-18-1 | Storage | 50 |  |  |  | ER | KCPL | Blue Valley 161kV Substation | FACILITY STUDY STAGE
GEN-2018-032 | 03 - Central | 20 | DIS-18-1 | Wind | 310 |  |  |  | ER | WERE | Neosho 345kV Substation | FACILITY STUDY STAGE
GEN-2018-049 | 03 - Central | 20 | DIS-18-1 | Solar | 120 |  |  |  | ER | SUNC | Thistle 345kV Substation | FACILITY STUDY STAGE
GEN-2018-057 | 03 - Central | 20 | DIS-18-1 | Solar | 203.4 |  |  |  | ER/NR | WERE | Gordon Evans 138kV | FACILITY STUDY STAGE
GEN-2018-062 | 03 - Central | 20 | DIS-18-1 | Solar | 75.6 |  |  |  | ER/NR | KACY | Nearman 161kV substation | FACILITY STUDY STAGE
GEN-2018-003 | 04 - Southeast | 20 | DIS-18-1 | Solar | 150 |  |  |  | ER/NR | AEPW | North Boston-Bann 138kV Line | FACILITY STUDY STAGE
GEN-2018-011 | 04 - Southeast | 20 | DIS-18-1 | Storage | 74.1 |  |  |  | ER/NR | WFEC | Dover 138 kV Switching Station | FACILITY STUDY STAGE
GEN-2018-021 | 04 - Southeast | 20 | DIS-18-1 | Solar | 74.1 |  |  |  | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | FACILITY STUDY STAGE
GEN-2018-024 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 |  |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2018-026 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 |  |  |  | ER | OKGE | Mustang 138kV Substation | FACILITY STUDY STAGE
GEN-2018-027 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 |  |  |  | ER | AEPW | Tulsa Power Station 38kV Substation | FACILITY STUDY STAGE
GEN-2018-028 | 04 - Southeast | 20 | DIS-18-1 | Storage | 200 |  |  |  | ER | AEPW | Tulsa North 138kV Substation | FACILITY STUDY STAGE
GEN-2018-029 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 |  |  |  | ER | OKGE | Horseshoe Lake 138kV Substation | FACILITY STUDY STAGE
GEN-2018-048 | 04 - Southeast | 20 | DIS-18-1 | Solar | 300 |  |  |  | ER | OKGE | Pecan Creek 345kV Substation | FACILITY STUDY STAGE
GEN-2018-050 | 04 - Southeast | 20 | DIS-18-1 | Solar | 200 |  |  |  | ER | AEPW | Longwood 345kV Substation | FACILITY STUDY STAGE
GEN-2018-055 | 04 - Southeast | 20 | DIS-18-1 | Solar | 252 |  |  |  | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | FACILITY STUDY STAGE
GEN-2018-004 | 05 - Southwest | 20 | DIS-18-1 | Solar | 74.99 |  |  |  | ER | SPS | T14 Circuit 115kV line | FACILITY STUDY STAGE
GEN-2018-015 | 05 - Southwest | 20 | DIS-18-1 | Solar | 252 |  |  |  | ER/NR | SPS | Tuco-Oklaunion 345kV Line | FACILITY STUDY STAGE
GEN-2018-052 | 05 - Southwest | 20 | DIS-18-1 | Storage | 70 |  |  |  | ER | SPS | Roadrunner 115kV Substation | FACILITY STUDY STAGE
J1040 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  |  | ER/NR | MDU | Wishek Junction 230 kV Substation | IA PENDING
J1045 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 20 |  |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | IA PENDING
J1072 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | XEL | Adams 345 kV Substation | IA PENDING
J1092 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Three Lakes 115 kV Substation | IA PENDING
J1124 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Byron 345kV Substation | IA PENDING
J1164 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER | ALTW | Magnolia 161 kV Substation | IA PENDING
J1169 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER | XEL | Grant 115 kV Substation | IA PENDING
J1181 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER | ALTW | Hazleton - Mitchell county 345 kV line | IA PENDING
J1221 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | GRE | Wing River- Riverton 230kV line | IA PENDING
J1298 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | ALTW | Hayward - Murphy Creek 161kV Line | IA PENDING
J1312 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | XEL | Grant 115 kV Substation | IA PENDING
J1314 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | DPC | Apple River 161 kV Substation | IA PENDING
J1325 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER/NR | ALTW | Magnolia 161 kV substation | IA PENDING
J1426 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Benton County 115kV Substation | IA PENDING
J1445 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Mayhew Lake 115kV Substation | IA PENDING
J1474 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  |  | ER/NR | XEL | Pine Lake - Eagle Point 115kV Line | IA PENDING
J1485 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  |  | ER | OTP | Astoria 345 kV Substation (J493/J510) | IA PENDING
J1494 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  |  | ER/NR | XEL | Chisago 115kV | NOT STARTED
J1495 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  |  | ER/NR | XEL | North Rochester 161kV | NOT STARTED
J1498 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  |  | ER/NR | XEL | Chanarambie 115 kV Substation | NOT STARTED
J1503 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | ALTW | Huntley 345 kV | NOT STARTED
J1504 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | ALTW | Huntley 345 kV | NOT STARTED
J1534 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Byron 345kV | NOT STARTED
J1566 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | ALTW | Rutland Substation 161kV | NOT STARTED
J1572 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | XEL | Huntley to Blue Earth 161kV | NOT STARTED
J1575 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 70 |  |  |  | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | NOT STARTED
J1581 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | XEL | Nobles County 345 kV Substation | NOT STARTED
J1582 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 160 |  |  |  | ER/NR | XEL | Pine Lake to Three Lakes 115 kV | NOT STARTED
J1588 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | XEL | Bison 345kV | NOT STARTED
J1605 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | XEL | Sherburne 345kV | NOT STARTED
J1611 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 120 |  |  |  | ER/NR | XEL | Langola 115kV Tap | NOT STARTED
J1620 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  |  | ER | XEL | Pipestone to Split Rock 115kV | NOT STARTED
J1622 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | OTP | Harvey-Underwood 230kV | NOT STARTED
J1657 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER | XEL | Pine Lake to Apple River 161 kV | NOT STARTED
J1730 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  |  | ER/NR | XEL | Eau Claire to AS King 345 kV | NOT STARTED
J1754 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER/NR | GRE | McHenry ND | NOT STARTED
J1769 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 80 |  |  |  | ER | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | NOT STARTED
J1808 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 148 |  |  |  | ER | DPC | Barron 161 kV | NOT STARTED
J1826 | 01 - North | 19.5 | DIS-18-1-PQ | Hydro | 4 |  |  |  | ER | XEL | Cannon Falls Transmission 69 kV | NOT STARTED
J967 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 150 |  |  |  | ER | XEL | Adams 345kV Substation | IA PENDING
MPC3600 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line
MPC3700 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line
MPC3800 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  |  | ER/NR | OTP | Center-Prairie 345 kV Line
MPC3900 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 151.2 |  |  |  | ER/NR | OTP | Center-Prairie 345 kV Line
MPC4000 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  |  | ER/NR | OTP | Square Butte 230 kV Substation
IR39 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 151.88 |  |  |  | ER/NR | ALTW | Dundee 161 kV Substation
J1050 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 225 |  |  |  | ER/NR | ALTW | Doud Tap 161 kV Substation | IA PENDING
J1132 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER | ALTW | Creston East 69 kV Substation | IA PENDING
J1174 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | IA PENDING
J1175 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 165 |  |  |  | ER | ALTW | Ledyard - Colby 345kV Line Tap | IA PENDING
J1270 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER | MEC | Kossuth - O'Brien 345 kV Line Tap | IA PENDING
J1313 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | ALTW | 161kV bus at Karma substation | IA PENDING
J1359 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Gas | 95 |  |  |  | ER/NR | ALTW | Oakridge 69 kV Substation | IA PENDING
J1365 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 169.4 |  |  |  | ER | ALTW | Traer 161-kV Substation | IA PENDING
J1444 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | ALTW | Duane Arnold 345kV Substation | IA PENDING
J1520 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV | NOT STARTED
J1529 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | NOT STARTED
J1530 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | NOT STARTED
J1532 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | MEC | Clarinda-Coburg 69 kV | NOT STARTED
J1590 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER/NR | MEC | O'Brien - Raun 345 kV | NOT STARTED
J982 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  |  | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | IA PENDING
GIA-96 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 97.5 |  |  |  | ER | AECI | Stroud 138kV
J1025 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 290 |  |  |  | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | IA PENDING
J1026 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 380 |  |  |  | ER/NR | AMMO | Maywood - Spencer Creek 345 kV Line Tap | IA PENDING
J1145 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  |  | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | IA PENDING
J1182 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  |  | ER/NR | AMMO | Zachary Substation 345 kV Bus | IA PENDING
J1191 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 64 |  |  |  | ER/NR | CWLD | Bolstad 69 kV Substation | IA PENDING
J1202 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 68 |  |  |  | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | IA PENDING
J1208 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1209 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1213 | 03 - Central | 19.5 | DIS-18-1-PQ | Hydro | 60 |  |  |  | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | IA PENDING
J1216 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 185 |  |  |  | ER/NR | AMIL | Ashley 138 kV Substation | IA PENDING
J1241 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  |  | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | IA PENDING
J1268 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | AMMO | Pike - Troy 161kV Line | IA PENDING
J1303 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  |  | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | IA PENDING
J1306 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMIL | Commodore-Jordan 345kV Line | IA PENDING
J1311 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | IA PENDING
J1352 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | AMMO | Spencer Creek - Montgomery 345kV Line | IA PENDING
J1488 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 500 |  |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J1490 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 1000 |  |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J956 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMMO | Spencer Creek 345kV Substation | IA PENDING
J976 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  |  | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | IA PENDING
J987 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | AMMO | Montgomery 161kV Substation | IA PENDING
J994 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | AMMO | Guthrie 161 kV Substation | IA PENDING
J1007 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  |  | ER/NR | EES-EAI | Marion - Marked Tree 161 kV | IA PENDING
J1030 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER | EES | Poco - Menard 138 kV | IA PENDING
J1034 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 225 |  |  |  | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | IA PENDING
J1060 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 450 |  |  |  | ER/NR | EES-EAI | West Memphis - Keo 500 kV | IA PENDING
J1087 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | IA PENDING
J1107 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | IA PENDING
J1125 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  |  | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV | IA PENDING
J1155 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | EES-EAI | Driver 230 kV | IA PENDING
J1205 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  |  | ER | CLEC | Centennial - West Bay 138 kV | IA PENDING
J1215 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 155 |  |  |  | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | IA PENDING
J1231 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  |  | ER/NR | BREC | Barkley - Caldwell 161kV Line | IA PENDING
J1239 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER | EES | Rilla 115 kV | IA PENDING
J1258 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1281 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 75 |  |  |  | ER/NR | EES-EAI | Crossett - Monticello East 115 kV | IA PENDING
J1299 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 149 |  |  |  | ER/NR | AMMO | Miner - Kelso 161kV Line | IA PENDING
J1373 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  |  | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | IA PENDING
J1402 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 0 |  |  |  | ER/NR | EES-EAI | Cash - Newport AB161kV Line | IA PENDING
J1415 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1424 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER | CLEC | Cooper - Penton Road 230 kV | IA PENDING
J1434 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | IA PENDING
J1436 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER | EES | Oak Ridge 115 kV | IA PENDING
J1437 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 180 |  |  |  | ER/NR | EES-EAI | AECC Dry Creek 161 kV | IA PENDING
J1442 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 105 |  |  |  | ER | EES | Rich (SHECO) - Livingston 138 kV | IA PENDING
J1509 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EMI | Greenwood - Pickens 115 kV | NOT STARTED
J1514 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | Driver 230kV | NOT STARTED
J1558 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | NOT STARTED
J1559 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | NOT STARTED
J1562 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | NOT STARTED
J1577 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | Hardin West SS to Sheridan 115 kV | NOT STARTED
J1598 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 325 |  |  |  | ER | EES | Solac - Chalkley 230kV | NOT STARTED
J1602 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 25 |  |  |  | ER/NR | EES | Rilla 115kV substation (Same as J1239) | NOT STARTED
J1612 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | NOT STARTED
J1669 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  |  | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | NOT STARTED
J1670 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | NOT STARTED
J1671 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER | EES | Rocky Creek to Lewis Creek 230kV | NOT STARTED
J1672 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | EES-EMI | Tinnin Road 230kV | NOT STARTED
J1673 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | NOT STARTED
J1709 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 100 |  |  |  | ER | EES | 138 kV Grimes | NOT STARTED
J1710 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  |  | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | NOT STARTED
J1723 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 10 |  |  |  | ER/NR | EES-EAI | Wynne East to Wynne South 161kV line (J1125 sub) | NOT STARTED
J1747 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | EES-EMI | J830 POI | NOT STARTED
J1748 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EMI | Twinkletown 230 kV | NOT STARTED
J1760 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 205 |  |  |  | ER/NR | EES | Timberland 230kV | NOT STARTED
J1816 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  |  | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | NOT STARTED
J1820 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | NOT STARTED
J1827 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 90 |  |  |  | ER/NR | EES | Bastrop tap point | NOT STARTED
J1834 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Gas | 126 |  |  |  | ER/NR | EES | Sabine 138/230 kV Substation | NOT STARTED
J1842 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 135 |  |  |  | ER | EES-EAI | Forrest City to Wynne S 161 KV | NOT STARTED
GEN-2017-175 | 01 - North | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA PENDING
GEN-2017-214 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  |  | ER/NR | WAPA | Logan 230kV Substation | IA PENDING
GEN-2017-215 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  |  | ER/NR | WAPA | Logan 230kV Substation | IA PENDING
GEN-2017-222 | 01 - North | 19 | DIS-17-2 | Wind | 180 |  |  |  | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 75 |  |  |  | ER/NR | NPPD | Tekamah - Raun 161 kV Line | IA PENDING
GEN-2017-144 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 200 |  |  |  | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 128 |  |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 - Nebraska | 19 | DIS-17-2 | Storage | 20 |  |  |  | ER | OPPD | Jones St. No 1201 69kV substation | IA PENDING
GEN-2017-201 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 250 |  |  |  | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 - Nebraska | 19 | DIS-17-2 | Storage | 310 |  |  |  | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-234 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 115 |  |  |  | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-014 | 03 - Central | 19 | DIS-17-2 | Solar | 40 |  |  |  | ER/NR | KCPL | Post Oak 69 kV
GEN-2017-108 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  |  | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA PENDING
GEN-2017-115 | 03 - Central | 19 | DIS-17-2 | Wind | 244 |  |  |  | ER | KCPL | Holt County 345 kV | IA PENDING
GEN-2017-119 | 03 - Central | 19 | DIS-17-2 | Wind | 180 |  |  |  | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 - Central | 19 | DIS-17-2 | Wind | 260 |  |  |  | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 - Central | 19 | DIS-17-2 | Wind | 200 |  |  |  | ER/NR | WERE | Sumner 138kV | IA PENDING
GEN-2017-125 | 03 - Central | 19 | DIS-17-2 | Wind | 252 |  |  |  | ER/NR | WERE | Swissvale 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-131 | 03 - Central | 19 | DIS-17-2 | Storage | 29.6 |  |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 - Central | 19 | DIS-17-2 | Wind | 400 |  |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | IA PENDING
GEN-2017-184 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | IA PENDING
GEN-2017-188 | 03 - Central | 19 | DIS-17-2 | Solar | 130 |  |  |  | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 - Central | 19 | DIS-17-2 | Solar | 500.4 |  |  |  | ER/NR | KCPL | West Gardner 345kV | IA PENDING
GEN-2017-196 | 03 - Central | 19 | DIS-17-2 | Storage | 128 |  |  |  | ER/NR | KCPL | West Gardner 345kV | IA PENDING
GEN-2017-202 | 03 - Central | 19 | DIS-17-2 | Solar | 200 |  |  |  | ER/NR | SWPA | New Madrid - Sikeston 161kV | IA PENDING
GEN-2017-209 | 03 - Central | 19 | DIS-17-2 | Solar | 300 |  |  |  | ER | KCPL | LaCygne - Neosho 345kV | IA PENDING
GEN-2017-220 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 - Central | 19 | DIS-17-2 | Storage | 152 |  |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | IA PENDING
GEN-2017-227 | 03 - Central | 19 | DIS-17-2 | Storage | 201.6 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 - Southeast | 19 | DIS-17-2 | Storage | 19.8 |  |  |  | ER/NR | WFEC | El Reno SW 138kV | IA PENDING
GEN-2017-132 | 04 - Southeast | 19 | DIS-17-2 | Wind | 400 |  |  |  | ER/NR | OKGE | Arcadia 345kV | IA PENDING
GEN-2017-133 | 04 - Southeast | 19 | DIS-17-2 | Wind | 200 |  |  |  | ER/NR | OKGE | Arcadia 345kV | IA PENDING
GEN-2017-134 | 04 - Southeast | 19 | DIS-17-2 | Wind | 250 |  |  |  | ER/NR | OKGE | Arcadia 345kV | IA PENDING
GEN-2017-137 | 04 - Southeast | 19 | DIS-17-2 | Wind | 295 |  |  |  | ER/NR | OKGE | Arcadia 345kV | IA PENDING
GEN-2017-140 | 04 - Southeast | 19 | DIS-17-2 | Solar | 160 |  |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | IA PENDING
GEN-2017-141 | 04 - Southeast | 19 | DIS-17-2 | Solar | 241.7 |  |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | IA PENDING
GEN-2017-149 | 04 - Southeast | 19 | DIS-17-2 | Wind | 258 |  |  |  | ER/NR | OKGE | Johnson County 345kV Substation | IA PENDING
GEN-2017-150 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | Minco 345kV | IA PENDING
GEN-2017-152 | 04 - Southeast | 19 | DIS-17-2 | Wind | 252 |  |  |  | ER/NR | OKGE | McClain 138kV | IA PENDING
GEN-2017-154 | 04 - Southeast | 19 | DIS-17-2 | Wind | 255 |  |  |  | ER/NR | OKGE | Johnson County 345kV Substation | IA PENDING
GEN-2017-164 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | Woodring 345kV Substation | IA PENDING
GEN-2017-166 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | Sunnyside 345kV | IA PENDING
GEN-2017-167 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  |  | ER/NR | OKGE | Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-168 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | McClain 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-169 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  |  | ER/NR | OKGE | McClain 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 - Southeast | 19 | DIS-17-2 | Solar | 150 |  |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-172 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-173 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-178 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  |  | ER/NR | OKGE | Woodring 345kV Substation | IA PENDING
GEN-2017-203 | 04 - Southeast | 19 | DIS-17-2 | Solar | 210 |  |  |  | ER | OKGE | Renfrow 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-230 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  |  | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  |  | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 - Southeast | 19 | DIS-17-2 | Solar | 52.2 |  |  |  | ER/NR | OKGE | Brown 138kV Substation | IA PENDING
GEN-2017-233 | 04 - Southeast | 19 | DIS-17-2 | Wind | 215 |  |  |  | ER/NR | OKGE | Minco 345kV | IA PENDING
GEN-2017-146 | 05 - Southwest | 19 | DIS-17-2 | Wind | 151.8 |  |  |  | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 - Southwest | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 - Southwest | 19 | DIS-17-2 | Wind | 265 |  |  |  | ER | SPS | Tolk 230kV Substation | IA PENDING
GEN-2017-187 | 05 - Southwest | 19 | DIS-17-2 | Solar | 150 |  |  |  | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 - Southwest | 19 | DIS-17-2 | Solar | 300 |  |  |  | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J545 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 110 |  |  |  | ER | XEL | Buffalo 115kV Substation
J722 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  |  | ER | OTP | Big Stone South 230kV Substation
J801 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 74 |  |  |  | ER | DPC | Crystal Cave-Rock Elm 161kV line tap
J803 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 32.5 |  |  |  | ER | XEL | Tracy 69 kV line
J874 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 150 |  |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line
J897 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 190 |  |  |  | ER | GRE | Prairie - Ramsey 230 kV line
J898 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 100 |  |  |  | ER | DPC | Rice - Beaver Creek 161kV line tap
J926 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 101.28 |  |  |  | ER | XEL | Pine Lake - Apple River 161 kV Line
IR24 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 57 |  |  |  | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  |  | ER/NR | ALTW | Murray Junction 69 kV substation
J836 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  |  | ER | ALTW | Ledyard 345kV Substation
J877 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Solar | 250 |  |  |  | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation)
GIA-83 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 1031 |  |  |  | ER/NR | AECI | McCredie 345 kV
GIA-85 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 447.3 |  |  |  | ER/NR | AECI | Morgan 345 kV
GIA-86 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 103.68 |  |  |  | ER/NR | AECI | Thomas Hill 69 kV
GIA-88 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 92.09 |  |  |  | ER/NR | AECI | Eudora 69 kV
GIA-90 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 108 |  |  |  | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 104.4 |  |  |  | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 100 |  |  |  | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 252 |  |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 - North | 18 | DIS-17-1 | Wind | 200.1 |  |  |  | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  |  | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  |  | ER | WAPA | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 - North | 18 | DIS-17-1 | Wind | 200 |  |  |  | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-097 | 01 - North | 18 | DIS-17-1 | Solar | 128 |  |  |  | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-004 | 03 - Central | 18 | DIS-17-1 | Wind | 201.6 |  |  |  | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 - Central | 18 | DIS-17-1 | Solar | 189 |  |  |  | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 - Central | 18 | DIS-17-1 | Solar | 65 |  |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-060 | 03 - Central | 18 | DIS-17-1 | Wind | 149.4 |  |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 - Central | 18 | DIS-17-1 | Solar | 103.5 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 - Central | 18 | DIS-17-1 | Wind | 150 |  |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 - Southeast | 18 | DIS-17-1 | Wind | 300 |  |  |  | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-011 | 04 - Southeast | 18 | DIS-17-1 | Solar | 151.8 |  |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 - Southeast | 18 | DIS-17-1 | Solar | 85 |  |  |  | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 - Southeast | 18 | DIS-17-1 | Wind | 140 |  |  |  | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 - Southeast | 18 | DIS-17-1 | Solar | 100 |  |  |  | ER | AEPW | Snyder - Cache 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-040 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200.1 |  |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  |  | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 - Southeast | 18 | DIS-17-1 | Solar | 101.5 |  |  |  | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  |  | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  |  | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  |  | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  |  | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  |  | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-076 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  |  | ER | AEPW | Chamber Springs 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  |  | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 - Southwest | 18 | DIS-17-1 | Wind | 200 |  |  |  | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 - Southwest | 18 | DIS-17-1 | Wind | 102 |  |  |  | ER/NR | SPS | Cole 115kV | IA PENDING
GEN-2017-100 | 05 - Southwest | 18 | DIS-17-1 | Solar | 102.6 |  |  |  | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCNDPW1 | 01 - North | 17.5 | DIS-17-1-PQ | Wind | 5 |  |  |  | ER | WAPA | NELSON 7
J718 | 01 - North | 17.5 | DIS-17-1-PQ | Solar | 49.98 |  |  |  | ER/NR | XEL | Cherry Grove 69kV Substation
J748 | 02 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 200 |  |  |  | ER/NR | MEC | Highland - Raun 345kV Line Tap
GEN-2016-087 | 01 - North | 17 | DIS-16-2 | Wind | 98.9 |  |  |  | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 - North | 17 | DIS-16-2 | Wind | 200 |  |  |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 - North | 17 | DIS-16-2 | Wind | 202 |  |  |  | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  |  |  | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-147 | 02 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  |  |  | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 - Central | 17 | DIS-16-2 | Wind | 134 |  |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 - Central | 17 | DIS-16-2 | Storage | 20 |  |  |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 - Southeast | 17 | DIS-16-2 | Wind | 303.6 |  |  |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 - Southeast | 17 | DIS-16-2 | Wind | 200 |  |  |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-102 | 04 - Southeast | 17 | DIS-16-2 | Wind | 150.9 |  |  |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 - Southeast | 17 | DIS-16-2 | Wind | 288 |  |  |  | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 - Southeast | 17 | DIS-16-2 | Wind | 600 |  |  |  | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 - Southeast | 17 | DIS-16-2 | Wind | 172.5 |  |  |  | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 - Southeast | 17 | DIS-16-2 | Wind | 176 |  |  |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 - Southeast | 17 | DIS-16-2 | Wind | 2.5 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 - Southeast | 17 | DIS-16-2 | Wind | 6.12 |  |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 - Southeast | 17 | DIS-16-2 | Solar | 73.5 |  |  |  | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 - Southwest | 17 | DIS-16-2 | Wind | 90 |  |  |  | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 - Southwest | 17 | DIS-16-2 | Solar | 110 |  |  |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123 | 05 - Southwest | 17 | DIS-16-2 | Wind | 298 |  |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-124 | 05 - Southwest | 17 | DIS-16-2 | Wind | 150 |  |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | 05 - Southwest | 17 | DIS-16-2 | Wind | 74 |  |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 - Southwest | 17 | DIS-16-2 | Gas Turbine | 17 |  |  |  | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
J569 | 01 - North | 16.5 | DIS-16-2-PQ | Wind | 100 |  |  |  | ER/NR | XEL | NSP Rock County Substation
ASGI-2017-006GIA-53 | 03 - Central | 16.5 | DIS-16-2-PQ | Wind | 238 |  |  |  | ER/NR | AECI | 5MARYVL
J476 | 03 - Central | 16.5 | DIS-16-2-PQ | Wind | 246 |  |  |  | ER/NR | AMMO | Atchison County to Booneville 345 kV Line Tap
GEN-2016-004 | 01 - North | 16 | DIS-16-1 | Wind | 202 |  |  |  | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 01 - North | 16 | DIS-16-1 | Wind | 100.05 |  |  |  | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-017 | 01 - North | 16 | DIS-16-1 | Wind | 250.24 |  |  |  | ER | BEPC | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 298.47 |  |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  |  |  | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  |  |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 - Central | 16 | DIS-16-1 | Steam Turbine | 29 |  |  |  | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-013 | 03 - Central | 16 | DIS-16-1 | CT | 10 |  |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 - Central | 16 | DIS-16-1 | CT | 10 |  |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-016 | 03 - Central | 16 | DIS-16-1 | Wind | 78.2 |  |  |  | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Central | 16 | DIS-16-1 | Wind | 299 |  |  |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-073 | 03 - Central | 16 | DIS-16-1 | Wind | 220 |  |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-036 | 04 - Southeast | 16 | DIS-16-1 | Wind | 303.6 |  |  |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 - Southeast | 16 | DIS-16-1 | Wind | 176 |  |  |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 - Southeast | 16 | DIS-16-1 | Wind | 250.4 |  |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | 04 - Southeast | 16 | DIS-16-1 | Wind | 151.8 |  |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 - Southeast | 16 | DIS-16-1 | Solar | 100 |  |  |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 - Southeast | 16 | DIS-16-1 | Wind | 1.5 |  |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  |  | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 - Southeast | 16 | DIS-16-1 | Wind | 9.8 |  |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  |  | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200.1 |  |  |  | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 - Southwest | 16 | DIS-16-1 | Wind | 10 |  |  |  | ER | SPS | Palo Duro 115kV
GEN-2015-041 | 05 - Southwest | 16 | DIS-16-1 | CT | 5 |  |  |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 - Southwest | 16 | DIS-16-1 | Wind | 5.3 |  |  |  | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 - Central | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | 03 - Central | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 - Central | 15 | DIS-15-2 | Wind | 220 |  |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 - Southeast | 15 | DIS-15-2 | Storage | 20 |  |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 - Southeast | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 - Southeast | 15 | DIS-15-2 | Wind | 200 |  |  |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 - Southeast | 15 | DIS-15-2 | Wind | 4.5 |  |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 - Southeast | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 - Southeast | 15 | DIS-15-2 | Wind | 248.4 |  |  |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  |  | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  |  | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 2 |  |  |  | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 10 |  |  |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  |  | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 16 |  |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2008-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 5 |  |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  |  | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.4 |  |  |  | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 3.5 |  |  |  | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2010-001IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 99 |  |  |  | ER/NR | WAPA | Bismarck-Glenham 230kV
GEN-2010-003IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 34 |  |  |  | ER/NR | WAPA | Wessington Springs 230kV
GEN-2014-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Gas | 11.72 |  |  |  | ER/NR | BEPC | Williston 115kV
MPC100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 99 |  |  |  | ER | OTP | Langdon 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
MPC1200 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 49.5 |  |  |  | ER | OTP | Maple River 230 kV
MPC1300 | 01 - North | 14.5 | DIS-15-2-PQ | Coal | 493 |  |  |  | ER/NR | OTP | Square Butte 230 kV
MPC200 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 60 |  |  |  | ER | OTP | Langdon 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
MPC2100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 99.25 |  |  |  | ER | OTP | Center - Mandan 230 kV
MPC300 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  |  |  | ER | OTP | Langdon 115 kV
MPC500 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 327.9 |  |  |  | ER/NR | OTP | Maple River 230 kV
MPC500GRE | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 51 |  |  |  | ER/NR | GRE | Maple River 230 kV
GEN-2015-023 | 02 - Nebraska | 14 | DIS-15-1 | Wind | 300.7 |  |  |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2015-001 | 03 - Central | 14 | DIS-15-1 | Thermal | 6.13 |  |  |  | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 - Central | 14 | DIS-15-1 | Wind | 200.1 |  |  |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 - Central | 14 | DIS-15-1 | Wind | 200 |  |  |  | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 - Central | 14 | DIS-15-1 | Wind | 220 |  |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 - Central | 14 | DIS-15-1 | Wind | 220 |  |  |  | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 - Southeast | 14 | DIS-15-1 | Solar | 120 |  |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-032 | 02 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 - Central | 13 | DIS-14-2 | Wind | 2.42 |  |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 - Southeast | 13 | DIS-14-2 | Wind | 1.06 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 - Southeast | 13 | DIS-14-2 | Wind | 249.9 |  |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 - Southeast | 13 | DIS-14-2 | Wind | 248.4 |  |  |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 4 |  |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 73.5 |  |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 - Central | 12 | DIS-14-1 | Wind | 200.6 |  |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 - Southeast | 12 | DIS-14-1 | Wind | 10.5 |  |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 - Southeast | 12 | DIS-14-1 | Wind | 5.7 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 - Southwest | 11 | DIS-13-2 | Wind | 1.65 |  |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-016 | 05 - Southwest | 10 | DIS-13-1 | CT | 203 |  |  |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Central | 9 | DIS-12-2 | Wind | 180 |  |  |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 - Southeast | 9 | DIS-12-2 | Wind | 98.82 |  |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 - Southwest | 9 | DIS-12-2 | Wind | 18.15 |  |  |  | ER | SPS | FE-Clovis Interchange 115kV
GEN-2012-037 | 05 - Southwest | 9 | DIS-12-2 | CT | 203 |  |  |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 - Nebraska | 8 | PQ | Wind | 75 |  |  |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 - Nebraska | 8 | PQ | Solar | 10 |  |  |  | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 - Nebraska | 8 | PQ | Wind | 20 |  |  |  | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 - Central | 8 | DIS-12-1 | Steam | 21.25 |  |  |  | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-030 | 03 - Central | 8 | PQ | CT | 50 |  |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 03 - Central | 8 | PQ | Wind | 100 |  |  |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 - Central | 8 | PQ | CT | 50 |  |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 - Central | 8 | PQ | Wind | 153 |  |  |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 - Central | 8 | PQ | Wind | 201 |  |  |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 - Southeast | 8 | PQ | Wind | 100.8 |  |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 - Southeast | 8 | DIS-12-1 | Wind | 40.8 |  |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 05 - Southwest | 8 | PQ | Wind | 180 |  |  |  | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 - Southwest | 8 | PQ | Wind | 240 |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 05 - Southwest | 8 | PQ | Gas | 604 |  |  |  | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 - Southwest | 8 | PQ | Wind | 370 |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 - Southeast | 7 | DIS-11-2 | Wind | 6.6 |  |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 - Southeast | 7 | DIS-11-2 | Wind | 300 |  |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 - Southeast | 6 | DIS-11-1 | Wind | 175 |  |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 - Southeast | 6 | DIS-11-1 | Wind | 165.6 |  |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 - Southwest | 6 | DIS-11-1 | Wind | 299 |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 - Southeast | 5 | DIS-10-2 | Wind | 300 |  |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 - Southwest | 5 | DIS-10-2 | Wind | 300 |  |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 03 - Central | 4 | DIS-10-1 | Wind | 72 |  |  |  | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 - Central | 4 | DIS-10-1 | Wind | 99.5 |  |  |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 - Southwest | 4 | DIS-10-1 | Wind | 299.65 |  |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 - Southwest | 4 | DIS-10-1 | Wind | 263.13 |  |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 - Southwest | 4 | DIS-10-1 | Wind | 358.8 |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 - Nebraska | 3 | DIS-09-1 | Wind | 201 |  |  |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Central | 3 | DIS-09-1 | Wind | 200.1 |  |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 03 - Central | 3 | DIS-09-1 | CT | 72 |  |  |  | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 - Southwest | 3 | DIS-09-1 | Wind | 161 |  |  |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 - Southeast | 2 | ICS1 | Wind | 299.2 |  |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 - Southeast | 2 | ICS1 | Wind | 424 |  |  |  | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP, 27WP | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 | [7 empty] | Build New Andrews to Road Runner 345 kV Line
00ALL | ERIS | Thermal | 646362 S1362 5 161 646363 S1363 5 161 1 | 24SP, 27SP, 27WP | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 0.15 | 151.46 |  |  |  | Build New S1362 to S1363 161 kV Second Circuit
00ALL | ERIS | Thermal | 646281 S1281 5 161 646363 S1363 5 161 1 | 24SP, 27SP, 27WP | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.07 | 164.81 |  |  |  | Build New S1362 to S1363 161 kV Second Circuit
00ALL | ERIS | Thermal | 646281 S1281 5 161 646287 S1287 5 161 1 | 24SP, 27SP, 27WP | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 215 | 35.69 | 110.39 |  |  |  | Build New S1362 to S1363 161 kV Second Circuit
00ALL | ERIS | Thermal | 646254 S1254 5 161 646281 S1281 5 161 1 | 24SP, 27SP, 27WP | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 298 | 25.69 | 229.47 |  |  |  | Build New S1362 to S1363 161 kV Second Circuit
00ALL | ERIS | Thermal | 646249 S1249 5 161 646254 S1254 5 161 1 | 24SP, 27SP, 27WP | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 298 | 45.01 | 116.82 |  |  |  | Build New S1362 to S1363 161 kV Second Circuit
00ALL | ERIS | Thermal | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 | 24SP, 27SP, 27WP | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 |  | 797 | 0.83 | 123.87 |  |  |  | Sidewinder to Andrews 345 kV Lidar Clearance Correction
00ALL | ERIS | Thermal | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 | 24SP, 27SP, 27WP | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 |  | 797 | 0.84 | 124.47 |  |  |  | Sidewinder to Hobbs 345 kV Lidar Clearance Correction
00ALL | ERIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 24SP | P42:345:OKGE:SB_CION7384:::: |  | 234 | 35.68 | 103.66 |  |  |  | Anadarko to Gracemont 138 kV Build Circuits 2 & 3
00NR | NRIS | Non-Converge | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00NR | NRIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00NR | NRIS | Thermal | 653312 MORRILL7 115 659821 GERINGT_-TS7 115 1 | 27SP, 24SP | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: |  | 91 | 104.48 | 105.18 |  |  |  | Rebuild the MORRILL7 to GERINGT_-TS7 115kV line 1 (non-SPP)
00NR | NRIS | Thermal | 646209 S1209 5 161 646231 S1231 5 161 1 | 27SP, 24SP | P21:161:OPPD:S1231-S1209 CKT2:LT::HV: |  | 250 | 104.66 | 109.46 |  |  |  | S1209 - S1231 Ckt 2 161 kV Reconductor
00NR | NRIS | Thermal | 543044 MOONLT 5 161 543132 BNSF 5 161 1 | 24SP, 27SP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 |  | 355 | <90% | 103.98 |  |  |  | Rebuild the MOONLT 5 to BNSF 5 161kV line 1
00NR | NRIS | Thermal | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 | 24SP, 27SP | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1 |  | 370 | <90% | 108.73 |  |  |  | Rebuild the SHWNMSN5 to LENEXA 5 161kV line 1
00NR | NRIS | Thermal | 543002 MARTCIT5 161 543053 REDEL 5 161 1 | 24SP, 27SP | 541198 PECULR 7 345 542968 STILWEL7 345 1 |  | 360 | <90% | 106.24 |  |  |  | Rebuild the MARTCIT5 to REDEL 5 161kV line 1
00NR | NRIS | Thermal | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 | 24SP, 27SP, 27WP | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 231 | 104.1 | 132.36 |  |  |  | Rebuild the STHTOWN5 to HICKMAN5 161kV line 1
00NR | NRIS | Thermal | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 1485 | <90% | 107.06 |  |  |  | Blackberry - Wolf Creek 345 kV
00NR | NRIS | Thermal | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | 24SP, 27SP, 27WP | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 |  | 374 | 93.99 | 113.64 |  |  |  | Rebuild the CRAIG 5 to LENEXA 5 161kV line 2
00NR | NRIS | Thermal | 542969 STILWEL5 161 997280 STILWELL11 161 11 | 24SP | 542968 STILWEL7 345 3WXFMR STILWELL22 22 |  | 557 | <90% | 100.67 |  |  |  | Upgrade terminal equipment at Stilwel 345/161 kV transformer
00NR | NRIS | Thermal | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 24SP, 27SP, 27WP | 541198 PECULR 7 345 542968 STILWEL7 345 1 |  | 334 | 90.26 | 113.38 |  |  |  | Rebuild the STILWEL5 to REDEL 5 161kV line 1
00NR | NRIS | Thermal | 542969 STILWEL5 161 542994 HICKMAN5 161 1 | 24SP, 27SP, 27WP | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 280 | 102.53 | 125.92 |  |  |  | Rebuild the STILWEL5 to HICKMAN5 161kV line 1
00NR | NRIS | Thermal | 542968 STILWEL7 345 997280 STILWELL11 161 11 | 24SP | 542968 STILWEL7 345 3WXFMR STILWELL22 22 |  | 557 | <90% | 101.1 |  |  |  | Upgrade terminal equipment at Stilwel 345/161 kV transformer
00NR | NRIS | Thermal | 542966 WGARDNR5 161 997281 WEST GARDN11 161 11 | 24SP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 |  | 535 | <90% | 105.53 |  |  |  | Upgrade terminal equipment at West Gardner 345/161 kV transformer
00NR | NRIS | Thermal | 542966 WGARDNR5 161 997279 WEST GARDN11 161 11 | 27WP, 27SP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 |  | 535 | <90% | 103.96 |  |  |  | Upgrade terminal equipment at West Gardner 345/161 kV transformer
00NR | NRIS | Thermal | 542966 WGARDNR5 161 543132 BNSF 5 161 1 | 27SP, 24SP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 |  | 334 | <90% | 107.1 |  |  |  | Rebuild the WGARDNR5 to BNSF 5 161kV line 1
00NR | NRIS | Thermal | 542965 W.GRDNR7 345 997281 WEST GARDN11 161 11 | 24SP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 |  | 535 | <90% | 106.46 |  |  |  | Upgrade terminal equipment at West Gardner 345/161 kV transformer
00NR | NRIS | Thermal | 542965 W.GRDNR7 345 997279 WEST GARDN11 161 11 | 27WP, 27SP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 |  | 535 | <90% | 104.48 |  |  |  | Upgrade terminal equipment at West Gardner 345/161 kV transformer
00NR | NRIS | Thermal | 533653 WOLFCRK2 69.0 997459 WOLF CREEK T 69.0 1 | 24SP | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 110 | <90% | 118.31 |  |  |  | Blackberry - Wolf Creek 345 kV
00NR | NRIS | Thermal | 532797 WOLFCRK7 345 997459 WOLF CREEK T 69.0 1 | 24SP | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 110 | <90% | 128.42 |  |  |  | Blackberry - Wolf Creek 345 kV
00NR | NRIS | Thermal | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 27SP | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 |  | 997.3 | <90% | 101.53 |  |  |  | Rebuild the TUCO_INT 7 to CRAWFISH_DR 345kV line 2
00NR | NRIS | Thermal | 515120 RUSSET-4 138 515147 GLASSES4 138 1 | 27SP, 27WP | P12:138:OKGE:BKRBKR345:::: |  | 153 | <90% | 100.83 |  |  |  | Rebuild the RUSSET-4 to GLASSES4 138kV line 1
00NR | NRIS | Thermal | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 24SP, 27SP | P42:345:OKGE:SB_GRNT7313:::: |  | 106 | <90% | 107.52 |  |  |  | Rebuild the D.E.S.-4 to OMDUNE-4 138kV line 1
00NR | NRIS | Thermal | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 24SP, 27SP | P42:345:OKGE:SB_GRNT7313:::: |  | 106 | <90% | 112.14 |  |  |  | Rebuild the D.E.S.-4 to DUNCHERTP4 138kV line 1
00NR | NRIS | Thermal | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 24SP, 27SP | P42:345:OKGE:SB_GRNT7313:::: |  | 106 | <90% | 115.94 |  |  |  | Rebuild the DUNCAN-4 to DUNCHERTP4 138kV line 1
00NR | NRIS | Thermal | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 27WP, 24SP | 515150 CANEYCK4 138 515151 LTLCITY4 138 1 |  | 155 | <90% | 110.04 |  |  |  | Russett - South Brown 138 kV Ckt 1 Rebuild
00NR | NRIS | Thermal | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 27SP, 24SP | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 250 | 281 | 96.21 | 108.77 |  |  |  | BELTONS5 to PECULR 5 161kV line 1 Rating Update
00NR | NRIS | Thermal | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 24SP, 27SP, 27WP | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | 374 | 374 | 93.99 | 113.64 |  |  |  | CRAIG 5 to LENEXA 5 161kV line 1 Rating Update
01ALL | ERIS | Stability | Voltage Recovery Issues/GEN-2020-006 Protection Action | 25SP, 25WP | Multiple (refer to Stability Analysis Results) | [7 empty] | Build a 80 MVAR STATCOM at Bowman 230 kV Substation
01ALL | ERIS | Non-Converge | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
01ALL | ERIS | Voltage | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
01ALL | ERIS | Thermal | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 27L, 24SP, 27SP, 27WP | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 |  | 717 | 131.9 | 134.25 |  |  |  | Replace the breaker at GR PRAIRIE 3
01ALL | ERIS | Thermal | 652507 FTTHOMP4 230 996647 FT2 KU1A 230 1 | 27L | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 313 | 107.7 | 123.19 |  |  |  | 2023ITP PORTFOLIO - REPLACE FORT THOMPSON 345_230 KV CKT 1 AND 2 XFMR
01ALL | ERIS | Thermal | 652507 FTTHOMP4 230 996646 FT2 KU1B 230 1 | 27L | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 313 | 105.42 | 120.58 |  |  |  | 2023ITP PORTFOLIO - REPLACE FORT THOMPSON 345_230 KV CKT 1 AND 2 XFMR
01ALL | ERIS | Thermal | 652506 FTTHOMP3 345 996647 FT2 KU1A 230 1 | 27L | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 313 | 107.78 | 123.29 |  |  |  | 2023ITP PORTFOLIO - REPLACE FORT THOMPSON 345_230 KV CKT 1 AND 2 XFMR
01ALL | ERIS | Thermal | 652506 FTTHOMP3 345 996646 FT2 KU1B 230 1 | 27L | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 313 | 105.49 | 120.68 |  |  |  | 2023ITP PORTFOLIO - REPLACE FORT THOMPSON 345_230 KV CKT 1 AND 2 XFMR
01ALL | ERIS | Thermal | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 27L, 24SP, 27SP, 27WP | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 |  | 720 | 131.35 | 133.69 |  |  |  | HOLT.CO3 to GRPRAR1-LNX3 345kV line 1 Rating Update
01ALL | ERIS | Thermal | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | 24SP, 27SP, 27WP | System Intact | 445 |  | 110.22 | 115.17 |  |  |  | Rebuild the HOLT.CO3 to ANTELOPE 3 345kV line 1
02ALL | ERIS | Non-Converge | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
02ALL | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
02ALL | ERIS | Voltage | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
02ALL | ERIS | Thermal | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 | 27SP, 27WP, 24SP | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1 |  | 320 | 90.76 | 116.64 |  |  |  | Rebuild the OGALALA4 to SIDNEY___TS4 230kV line 1
02ALL | ERIS | Thermal | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 27WP, 24SP, 27SP | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 |  | 120 | <90% | 175.73 |  |  |  | Rebuild the HOLDREG7 to G20-013-TAP 115kV line 1
02ALL | ERIS | Thermal | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 | 27L, 24SP, 27SP, 27WP | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | <90% | 149.78 |  |  |  | Rebuild the HEBRN N7 to G20-077-TAP 115kV line 1
02ALL | ERIS | Thermal | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 | 24SP, 27SP, 27L, 27WP | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | <90% | 149.94 |  |  |  | Rebuild the FAIRBRY7 to G20-077-TAP 115kV line 1
02ALL | ERIS | Thermal | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 27L, 27WP, 24SP, 27SP | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | <90% | 137.11 |  |  |  | Rebuild the FAIRBRY7 to HARBINE7 115kV line 1
02ALL | ERIS | Thermal | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 27L, 27WP | P12:115:WERE:KNOB-NPPD-115:::HV: |  | 99 | <90% | 132.66 |  |  |  | Rebuild the BEATRCE7 to HARBINE7 115kV line 1
02ALL | ERIS | Thermal | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 | 27WP | P23:345:ITCGP:SV_BRK382:::EHV: |  | 600 | <90% | 104.54 |  |  |  | Replace Post Rock 345-230 kV Transformer
02ALL | ERIS | Thermal | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 | 27WP | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV: |  | 600 | <90% | 103.65 |  |  |  | Replace Post Rock 345-230 kV Transformer
02ALL | ERIS | Thermal | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 27WP, 27SP, 24SP | P23:345:ITCGP:SV_BRK382:::EHV: |  | 319 | <90% | 120.55 |  |  |  | Upgrade Terminals at Hays to Great Bend
02ALL | ERIS | Thermal | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 27SP, 24SP | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | 956 | 956 | <90% | 101.59 |  |  |  | S3451 3 Breaker Rating Update
02ALL | ERIS | Thermal | 653572 SIDNEY 7 115 659817 COLTON__-TS7 115 1 | 27SP | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1 | 107 | 107 | <90% | 101.27 |  |  |  | SIDNEY 7 to COLTON__-TS7 115kV line 1 Rating Update
03ALL | ERIS | Non-Converge | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
03ALL | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
03ALL | ERIS | Voltage | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
03ALL | ERIS | Thermal | 547479 LAR382 5 161 547480 MON383 5 161 1 | 27WP | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 |  | 223 | <90% | 101.18 |  |  |  | Terminal upgrades at both ends of the line LAR382 5 to MON383
03ALL | ERIS | Thermal | 543067 CENTENL5 161 543069 PAOLA 5 161 1 | 27SP, 27WP, 24SP | P12:161:WERE:MARM-KCPL-161:::HV: |  | 167 | 101.4 | 169.5 |  |  |  | Rebuild the CENTENL5 to PAOLA 5 161kV line 1
03ALL | ERIS | Thermal | 543065 CNTRVIL5 161 543650 DAKOTA_5 161 1 | 24SP, 27SP | P12:161:WERE:MARM-KCPL-161:::HV: |  | 281 | <90% | 107.34 |  |  |  | Rebuild the CNTRVIL5 to DAKOTA_5 161kV line 1
03ALL | ERIS | Thermal | 543065 CNTRVIL5 161 543069 PAOLA 5 161 1 | 24SP, 27SP | P12:161:WERE:MARM-KCPL-161:::HV: |  | 255 | <90% | 109.11 |  |  |  | Terminal upgrades at the line CNTRVIL5 to PAOLA 5 161kV line 1
03ALL | ERIS | Thermal | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 1195 | <90% | 123.97 |  |  |  | Rebuild the LACYGNE7 to G20-007-TAP 345kV line 1
03ALL | ERIS | Thermal | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 24SP, 27SP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 |  | 334 | <90% | 118.63 |  |  |  | Replacing the CT/Relay of West Gardner R2-3 Breaker
03ALL | ERIS | Thermal | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 24SP, 27SP, 27WP | system Intact | 717 |  | <90% | 111.03 |  |  |  | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1
03ALL | ERIS | Thermal | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 | 27SP, 24SP | 543065 CNTRVIL5 161 543650 DAKOTA_5 161 1 |  | 281 | <90% | 107.49 |  |  |  | Rebuild the MARMTNE5 to DAKOTA_5 161kV line 1
03ALL | ERIS | Thermal | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 1016 | <90% | 108.23 |  |  |  | Blackberry - Wolf Creek 345 kV
03ALL | ERIS | Thermal | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 24SP, 27SP, 27WP | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 956 | <90% | 163.74 |  |  |  | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1
03ALL | ERIS | Thermal | 505486 NEO SPA5 161 547472 TIP292 5 161 1 | 24SP, 27SP | 505486 NEO SPA5 161 505488 CARTHAG5 161 1 |  | 222 | <90% | 103.95 |  |  |  | Terminal upgrades in the NEO_SPA substation
03ALL | ERIS | Thermal | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 | 27WP | 547479 LAR382 5 161 547480 MON383 5 161 1 | 167 | 167 | <90% | 103.99 |  |  |  | SPRGFLD5 to LAR382 5 161kV line 1 Rating Update
03ALL | ERIS | Thermal | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 27SP, 27WP, 24SP | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 | 160 | 189 | <90% | 109.29 |  |  |  | MARMTNE5 Breaker Rating Update
04ALL | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
04ALL | ERIS | Non-Converge | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
04ALL | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
04ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 997627 UPDATE LATER 230 1 | 24SP, 27SP | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 |  | 559 | 97.71 | 129.46 |  |  |  | Build 3rd Transformer at Tuco
04ALL | ERIS | Thermal | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 | 24SP, 27SP | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 |  | 559 | 98.91 | 131.52 |  |  |  | Build 3rd Transformer at Tuco
04ALL | ERIS | Thermal | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1 | 24SP, 27SP, 27L | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 169 | 0.24 | 117.44 |  |  |  | Cache Junction to G20-016-TAP 138 kV Line Rebuild
04ALL | ERIS | Thermal | 521106 GRNDFLD4 138 997734 GRNDFLD 69.0 1 | 24SP, 27SP, 27L, 27WP | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 56 | 36.55 | 132.63 |  |  |  | Replace 1st Transformer at Grandfield
04ALL | ERIS | Thermal | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 | 24SP, 27SP, 27L | P12:138:WFEC:ANADRKO_CHRYRD:::: |  | 169 | 24.5 | 118.39 |  |  |  | Snyder to G20-016-TAP 138 kV Line Rebuild
04ALL | ERIS | Thermal | 520926 GRANFLD2 69.0 997734 GRNDFLD 69.0 1 | 24SP, 27SP, 27L, 27WP | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 56 | 36.81 | 135.5 |  |  |  | Replace 1st Transformer at Grandfield
04ALL | ERIS | Thermal | 520814 ANADARK4 138 521129 CHERRYRD 4 138 1 | 27L | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 169 | 21.54 | 102.8 |  |  |  | Anadarko to Cherry Road 138 kV Line Rebuild
04ALL | ERIS | Thermal | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 | 27SP | P42:345:OKGE:SB_GRNT7381:::: |  | 283 | 65.12 | 108.76 |  |  |  | Anadarko to Cleveland Switch 138 kV Line Rebuild
04ALL | ERIS | Thermal | 515802 GRACMNT4 138 997779 GRACMNT3 138 3 | 24SP, 27SP | P42:345:OKGE:SB_GRNT7381:::: |  | 478 | 50.95 | 107.1 |  |  |  | Build 2nd Transformer at Gracemont
04ALL | ERIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 24SP | P42:345:OKGE:SB_GRNT7381:::: |  | 234 | 59.88 | 125.27 |  |  |  | Anadarko to Gracemont 138 kV Build Circuits 2 & 3
04ALL | ERIS | Thermal | 515800 GRACMNT7 345 997779 GRACMNT3 138 3 | 24SP, 27SP | P42:345:OKGE:SB_GRNT7381:::: |  | 478 | 50.52 | 105.77 |  |  |  | Build 2nd Transformer at Gracemont
04ALL | ERIS | Thermal | 515138 CARTER 4 138 515372 ARDWEST4 138 1 | 24SP, 27SP | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 222 | 82.84 | 119.25 |  |  |  | Carter County to Ardmore West 138 kV Line Rebuild
04ALL | ERIS | Thermal | 515138 CARTER 4 138 515171 CHIKSAW4 138 1 | 24SP | P12:138:OKGE:BKRBKR257:::: |  | 191 | 87.09 | 116.88 |  |  |  | Carter County to Chickasaw 138 kV Line Rebuild
04ALL | ERIS | Thermal | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 | 24SP, 27SP | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 222 | 88.38 | 124.7 |  |  |  | Uniroyal to Ardmore West 138 kV Line Rebuild
04ALL | ERIS | Thermal | 515136 SUNNYSD7 345 997852 SUNNYSD3 138 3 | 24SP, 27SP | P13:138-345:OKGE:BKRBKR_3W045:::: |  | 330 | 74.91 | 111.2 |  |  |  | Replace Sunnyside Transformer (CKT ID 3)
04ALL | ERIS | Thermal | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 24SP, 27SP, 27WP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: |  | 1195 | 85.25 | 147 |  |  |  | Sunnyside to G20-074-TAP 345 kV Line Rebuild
04ALL | ERIS | Thermal | 515135 SUNNYSD4 138 997852 SUNNYSD3 138 3 | 24SP, 27SP | P13:138-345:OKGE:BKRBKR_3W045:::: |  | 330 | 75.74 | 112.7 |  |  |  | Replace Sunnyside Transformer (CKT ID 3)
04ALL | ERIS | Thermal | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 24SP, 27SP | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 222 | 98.88 | 135.69 |  |  |  | Sunnyside to Uniroyal 138 kV Line Rebuild
04ALL | ERIS | Thermal | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 | 24SP, 27SP | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 177 | 79.73 | 104.49 |  |  |  | Ratliff to Carter County 138 kV Line Rebuild
04ALL | ERIS | Thermal | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | 24SP, 27SP | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT:::: |  | 222 | 54.74 | 103.38 |  |  |  | Wind Mill Creek Tap to Six Mile Creek Tap 138 kV Line Rebuild
04ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 24SP, 27SP | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT:::: |  | 191 | 59.28 | 115.73 |  |  |  | Wind Mill Creek Tap to Arbuckle 138 kV Line Rebuild
04ALL | ERIS | Thermal | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 | 24SP, 27SP, 27WP | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT:::: |  | 478 | 86.77 | 121.01 |  |  |  | Build 2nd Transformer at Johnson County
04ALL | ERIS | Thermal | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 | 24SP, 27SP, 27WP | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT:::: |  | 478 | 87.27 | 120.99 |  |  |  | Build 2nd Transformer at Johnson County
04ALL | ERIS | Thermal | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | 24SP, 27SP | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT:::: |  | 222 | 55.58 | 104.24 |  |  |  | Johnson County to Six Mile Creek Tap 138 kV Line Rebuild
04ALL | ERIS | Thermal | 514715 WOODRNG7 345 997902 WOODRNG2 138 2 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_WONG7313:::: |  | 359 | 100.78 | 125.92 |  |  |  | Build 2nd Transformer at Woodring
04ALL | ERIS | Thermal | 514714 WOODRNG4 138 997902 WOODRNG2 138 2 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_WONG7313:::: |  | 359 | 101.51 | 126.92 |  |  |  | Build 2nd Transformer at Woodring
04ALL | ERIS | Thermal | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | 24SP, 27SP | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1301 | 58.08 | 113.65 |  |  |  | Terry Road to G17-171-TAP 345 kV Line Rebuild
04ALL | ERIS | Thermal | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 24SP, 27SP | P42:345:OKGE:SB_GRNT7313:::: |  | 171 | 70.64 | 117.93 |  |  |  | Comanche Tap to Duncan Bois D' Arc 138 kV Line Rebuild
04ALL | ERIS | Thermal | 511475 SNYDER-2 69.0 997968 SNYDER 69.0 1 | 24SP, 27SP, 27WP | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1 |  | 75 | 74.08 | 144.19 |  |  |  | Replace 1st Transformer at Snyder
04ALL | ERIS | Thermal | 511475 SNYDER-2 69.0 511495 TOMSTEED2 69.0 1 | 24SP | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1 |  | 35 | 22.6 | 100.07 |  |  |  | Snyder to Tom Steed 69 kV Line Rebuild
04ALL | ERIS | Thermal | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 | 24SP, 27SP | P12:345:OKGE-AEPW:BKRBKR365:::: |  | 1176 | 42.16 | 101.62 |  |  |  | Lawton Eastside to G20-075-TAP 345 kV Line Rebuild
04ALL | ERIS | Thermal | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | 24SP, 27SP, 27WP | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1301 | 76.91 | 132.64 |  |  |  | Lawton Eastside to G17-171-TAP 345 kV Line Rebuild
04ALL | ERIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 24SP, 27SP, 27WP | P42:345:OKGE:SB_GRNT7313:::: |  | 158 | 76.3 | 127.45 |  |  |  | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild
04ALL | ERIS | Thermal | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1 | 27SP | P42:345:OKGE:SB_GRNT7381:::: |  | 152 | 51.07 | 101.15 |  |  |  | Clinton Air Force Base Tap to Hobart Junction 138 kV Line Rating Update
04ALL | ERIS | Thermal | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1 | 24SP | P42:345:OKGE:SB_GRNT7381:::: |  | 152 | 49.74 | 101.47 |  |  |  | Clinton Air Force Base Tap to Elk City 138 kV Line Rating Update
04ALL | ERIS | Thermal | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 | 24SP, 27SP | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1 |  | 35 | 21.93 | 115.38 |  |  |  | Roosevelt Tap to Hobart City 69 kV Line Rebuild
04ALL | ERIS | Thermal | 511441 ALTUSJT2 69.0 511543 TIPTN T2 69.0 1 | 24SP, 27SP | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1 |  | 50 | 61.31 | 116.63 |  |  |  | Altus Junction to Tipton T2 69 kV Line Rating Update
04ALL | ERIS | Thermal | 511435 SNYDER-4 138 997968 SNYDER 69.0 1 | 24SP, 27SP, 27WP | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1 |  | 75 | 74.29 | 143.78 |  |  |  | Replace 1st Transformer at Snyder
04ALL | ERIS | Thermal | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 | 24SP, 27SP | P12:69:AEPW:COMANC-2:L.E.S.-2::: |  | 45 | 75.01 | 115.43 |  |  |  | Walters to Walters Junction 69 kV Line Rebuild
04ALL | ERIS | Thermal | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 27SP | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: |  | 776 | 89.53 | 103.99 |  |  |  | Longwood to Wilkes 345 kV Line Rating Update
04ALL | ERIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 24SP, 27WP | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: |  | 970 | 88.87 | 106.46 |  |  |  | Welsh to Wilkes 345 kV Line Rebuild
05ALL | ERIS | Non-Converge | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
05ALL | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
05ALL | ERIS | Stability | Instability/Voltage Collapse | 25SP, 25WP | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 | [7 empty] | Build New Andrews to Road Runner 345 kV Line
05ALL | ERIS | Thermal | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 24SP, 27SP | System Intact | 121 |  | 73.95 | 106.23 |  |  |  | Comanche Tap to Duncan Bois D' Arc 138 kV Line Rebuild
05ALL | ERIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 24SP, 27SP | System Intact | 121 |  | 73.83 | 106.06 |  |  |  | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2020-006 | 01 - North | TBD | ERIS | Replace the breaker at GR PRAIRIE 3 | Current Study | Replace the existing breaker at GR PRAIRIE 3 with minimum ratings of 980 MVA | 163395.5989 | 28.84% | 566485 | 0.1326
GEN-2020-006 | 01 - North | TBD | ERIS | Build a 80 MVAR STATCOM at Bowman 230 kV Substation | Current Study | Build a 80 MVAR STATCOM at Bowman 230 kV Substation | 15175378.6876 | 88.23% | 17200000 | 0.62141
GEN-2020-006 | 01 - North | 156887 | ERIS | Bowman 230kV substation GEN-2020-006 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-006 (250/Solar), into the Point of Interconnection (POI) at Bowman 230kV substation | 1396145 | 100% | 1396145 | 1
GEN-2020-006 | 01 - North | 156886 | ERIS | Bowman 230kV substation GEN-2020-006 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-006 (250/Solar), into the Point of Interconnection (POI) at Bowman 230kV substation | 2457984 | 100% | 2457984 | 1
GEN-2020-014 | 01 - North | TBD | ERIS | Build a 80 MVAR STATCOM at Bowman 230 kV Substation | Current Study | Build a 80 MVAR STATCOM at Bowman 230 kV Substation | 312098.8391 | 1.815% | 17200000 | 0.071
GEN-2020-014 | 01 - North | 144258 | ERIS | Lonesome Creek 115kV GEN-2020-014 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-014 (60.5/Thermal), into the Point of Interconnection (POI) at Lonesome Creek 115kV | 0 | 100% | 0 | 1
GEN-2020-014 | 01 - North | 144259 | ERIS | Lonesome Creek 115kV GEN-2020-014 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-014 (60.5/Thermal), into the Point of Interconnection (POI) at Lonesome Creek 115kV | 0 | 100% | 0 | 1
GEN-2020-021 | 01 - North | TBD | ERIS | Replace the breaker at GR PRAIRIE 3 | Current Study | Replace the existing breaker at GR PRAIRIE 3 with minimum ratings of 980 MVA | 252557.8416 | 44.58% | 566485 | 0.21804
GEN-2020-021 | 01 - North | NTC-220753 | ERIS | 2023ITP PORTFOLIO - REPLACE FORT THOMPSON 345_230 KV CKT 1 AND 2 XFMR | Contingent | Contingent upgrade from 2023 ITP. Replace both existing Fort Thompson 345/230 kV transformers. | 0 | 100% | 33546913 | 0.17491
GEN-2020-021 | 01 - North | TBD | ERIS | Rebuild the HOLT.CO3 to ANTELOPE 3 345kV line 1 | Contingent | Contingent upgrade from DISIS 1802/1901 phase 2. Increase rating from 445 MVA to 525 MVA. Build approximately 25 miles of 345kV line from Antelope to Holt. Cost updated based on latest information available. | 0 | 100% | 70000000 | 0.05848
GEN-2020-021 | 01 - North | 156923 | ERIS | LeLand Olds-Chapelle Creek 345kV line GEN-2020-021 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-021 (235/Wind), into the Point of Interconnection (POI) at LeLand Olds-Chapelle Creek 345kV line | 3674786 | 100% | 3674786 | 1
GEN-2020-021 | 01 - North | 156922 | ERIS | LeLand Olds-Chapelle Creek 345kV line GEN-2020-021 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-021 (235/Wind), into the Point of Interconnection (POI) at LeLand Olds-Chapelle Creek 345kV line | 23834846 | 100% | 23834846 | 1
GEN-2020-083 | 01 - North | TBD | ERIS | Replace the breaker at GR PRAIRIE 3 | Current Study | Replace the existing breaker at GR PRAIRIE 3 with minimum ratings of 980 MVA | 49485.0595 | 8.735% | 566485 | 0.13476
GEN-2020-083 | 01 - North | TBD | ERIS | Build a 80 MVAR STATCOM at Bowman 230 kV Substation | Current Study | Build a 80 MVAR STATCOM at Bowman 230 kV Substation | 697395.357 | 4.055% | 17200000 | 0.09583
GEN-2020-083 | 01 - North | 156905 | ERIS | Fairview 115kV Substation GEN-2020-083 Interconnection (Non-shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-083 (74.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation | 6400000 | 100% | 6400000 | 1
GEN-2020-083 | 01 - North | 156906 | ERIS | Fairview 115kV Substation GEN-2020-083 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-083 (74.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation | 350000 | 100% | 350000 | 1
GEN-2020-091 | 01 - North | TBD | ERIS | Replace the breaker at GR PRAIRIE 3 | Current Study | Replace the existing breaker at GR PRAIRIE 3 with minimum ratings of 980 MVA | 101046.5 | 17.84% | 566485 | 0.13667
GEN-2020-091 | 01 - North | TBD | ERIS | Build a 80 MVAR STATCOM at Bowman 230 kV Substation | Current Study | Build a 80 MVAR STATCOM at Bowman 230 kV Substation | 1015127.1162 | 5.902% | 17200000 | 0.06928
GEN-2020-091 | 01 - North | 156941 | ERIS | Patent Gate Substation 345 kV GEN-2020-091 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-091 (150/Solar), into the Point of Interconnection (POI) at Patent Gate Substation 345 kV | 1766528 | 100% | 1766528 | 1
GEN-2020-091 | 01 - North | 156942 | ERIS | Patent Gate Substation 345 kV GEN-2020-091 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-091 (150/Solar), into the Point of Interconnection (POI) at Patent Gate Substation 345 kV | 2569702 | 100% | 2569702 | 1
GEN-2020-001 | 02 - Nebraska | 156963 | ERIS | Sidney 345 kV Substation GEN-2020-001 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-001 (200/Solar), into the Point of Interconnection (POI) at Sidney 345 kV Substation | 1923401 | 100% | 1923401 | 1
GEN-2020-001 | 02 - Nebraska | 156962 | ERIS | Sidney 345 kV Substation GEN-2020-001 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-001 (200/Solar), into the Point of Interconnection (POI) at Sidney 345 kV Substation | 4886412 | 100% | 4886412 | 1
GEN-2020-001 | 02 - Nebraska | TBD | ERIS | Upgrade Terminals at Hays to Great Bend | Current Study | Upgrade the existing terminals at S HAYS6 to GRTBEND6 230 kV line(39.2 miles) to a minimum ratings of 455 MVA | 47137.7017 | 10.84% | 435000 | 0.03565
GEN-2020-001 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 503791.1435 | 5.011% | 10052968 | 0.03356
GEN-2020-025 | 02 - Nebraska | NTC 220723 UID 158446 | ERIS | Build New S1362 to S1363 161 kV Second Circuit | Contingent | Build a second 161 kV line from S1362 to S1363 (5.44 miles) to standard rating of 558 MVA | 0 | 31.37% | 5688841.92 | 0.3615
GEN-2020-001 | 02 - Nebraska | TBD | ERIS | Rebuild the OGALALA4 to SIDNEY___TS4 230kV line 1 | Current Study | Rebuild the existing OGALALA4 to SIDNEY___TS4 230 kV line(68.85 miles) to a minimum ratings of 415 MVA | 60829594.65 | 100% | 60829594.65 | 0.23545
GEN-2020-002 | 02 - Nebraska | 143682 | ERIS | 6846 Substation 69 kV GEN-2020-002 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-002 (81/Solar), into the Point of Interconnection (POI) at 6846 Substation 69 kV | 0 | 100% | 0 | 1
GEN-2020-002 | 02 - Nebraska | 143683 | ERIS | 6846 Substation 69 kV GEN-2020-002 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-002 (81/Solar), into the Point of Interconnection (POI) at 6846 Substation 69 kV | 2345838 | 100% | 2345838 | 1
GEN-2020-002 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 104267.2031 | 1.037% | 10052968 | 0.01715
GEN-2020-011 | 02 - Nebraska | TBD | ERIS | Upgrade Terminals at Hays to Great Bend | Current Study | Upgrade the existing terminals at S HAYS6 to GRTBEND6 230 kV line(39.2 miles) to a minimum ratings of 455 MVA | 125665.2783 | 28.89% | 435000 | 0.0594
GEN-2020-011 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 1424786.2041 | 14.17% | 10052968 | 0.05932
GEN-2020-011 | 02 - Nebraska | 156882 | ERIS | Axtell-Sweetwater Substation 345kV GEN-2020-011 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-011 (320/Hybrid), into the Point of Interconnection (POI) at Axtell-Sweetwater Substation 345kV | 700000 | 100% | 700000 | 1
GEN-2020-011 | 02 - Nebraska | 156881 | ERIS | Axtell-Sweetwater Substation 345kV GEN-2020-011 Interconnection (Non-shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-011 (320/Hybrid), into the Point of Interconnection (POI) at Axtell-Sweetwater Substation 345kV | 16700000 | 100% | 16700000 | 1
GEN-2020-013 | 02 - Nebraska | TBD | ERIS | Upgrade Terminals at Hays to Great Bend | Current Study | Upgrade the existing terminals at S HAYS6 to GRTBEND6 230 kV line(39.2 miles) to a minimum ratings of 455 MVA | 69790.9044 | 16.04% | 435000 | 0.0491
GEN-2020-013 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 777990.2817 | 7.739% | 10052968 | 0.04821
GEN-2020-013 | 02 - Nebraska | TBD | ERIS | Rebuild the HOLDREG7 to G20-013-TAP 115kV line 1 | Current Study | Rebuild the existing HOLDREG7 to G20-013-TAP 115 kV line(19 miles) to a minimum ratings of 215 MVA | 13800000 | 100% | 13800000 | 0.9999
GEN-2020-013 | 02 - Nebraska | 156940 | ERIS | Orleans-Holdrege Substation 115kV GEN-2020-013 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-013 (215/Hybrid), into the Point of Interconnection (POI) at Orleans-Holdrege Substation 115kV | 700000 | 100% | 700000 | 1
GEN-2020-013 | 02 - Nebraska | 156939 | ERIS | Orleans-Holdrege Substation 115kV GEN-2020-013 Interconnection (Non-shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-013 (215/Hybrid), into the Point of Interconnection (POI) at Orleans-Holdrege Substation 115kV | 9600000 | 100% | 9600000 | 1
GEN-2020-025 | 02 - Nebraska | 156388 | ERIS | Substation 1363; 161kV Substation GEN-2020-025 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025 (255/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | 2292537 | 100% | 2292537 | 1
GEN-2020-025 | 02 - Nebraska | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 10873424.0187 | 26.48% | 41063166 | 1
GEN-2020-028 | 02 - Nebraska | NTC 220723 UID 158446 | ERIS | Build New S1362 to S1363 161 kV Second Circuit | Contingent | Build a second 161 kV line from S1362 to S1363 (5.44 miles) to standard rating of 558 MVA | 0 | 31.37% | 5688841.92 | 0.3615
GEN-2020-027 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 62110.7228 | 0.6178% | 10052968 | 0.01655
GEN-2020-027 | 02 - Nebraska | 156953 | ERIS | Substation 1363; 161kV Substation GEN-2020-027 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-027 (50/Hybrid), into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 2292537 | 100% | 2292537 | 1
GEN-2020-027 | 02 - Nebraska | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 2132043.9252 | 5.192% | 41063166 | 1
GEN-2020-028 | 02 - Nebraska | 156389 | ERIS | Substation 1363; 161kV Substation GEN-2020-028 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-028 (255/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | 2292537 | 100% | 2292537 | 1
GEN-2020-028 | 02 - Nebraska | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 10873424.0187 | 26.48% | 41063166 | 1
GEN-2020-031 | 02 - Nebraska | NTC 220723 UID 158446 | ERIS | Build New S1362 to S1363 161 kV Second Circuit | Contingent | Build a second 161 kV line from S1362 to S1363 (5.44 miles) to standard rating of 558 MVA | 0 | 37.27% | 5688841.92 | 0.3615
GEN-2020-030 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 62110.7228 | 0.6178% | 10052968 | 0.01655
GEN-2020-030 | 02 - Nebraska | 156954 | ERIS | Substation 1363; 161kV Substation GEN-2020-030 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-030 (50/Hybrid), into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 2292537 | 100% | 2292537 | 1
GEN-2020-030 | 02 - Nebraska | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 2132043.9252 | 5.192% | 41063166 | 1
GEN-2020-031 | 02 - Nebraska | 156968 | ERIS | Substation 1363; 161kV Substation GEN-2020-031 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-031 (303/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | 2292537 | 100% | 2292537 | 1
GEN-2020-031 | 02 - Nebraska | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 12920186.1869 | 31.46% | 41063166 | 1
GEN-2020-084 | 02 - Nebraska | 156030 | ERIS | Ft. Calhoun - Raun 345 kV GEN-2018-043 Interconnection (TOIF) (OPPD) | Contingent | Facilitate the interconnection of GEN-2018-043 | 0 | 100% | 8894071 | 1
GEN-2020-033 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 62110.7228 | 0.6178% | 10052968 | 0.01655
GEN-2020-033 | 02 - Nebraska | 156955 | ERIS | Substation 1363; 161kV Substation GEN-2020-033 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facilities, GEN-2020-027 (50/Hybrid), GEN-2020-030 (50/Hybrid), and GEN-2020-033 (50/Hybrid), into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 2292537 | 100% | 2292537 | 1
GEN-2020-033 | 02 - Nebraska | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 2132043.9252 | 5.192% | 41063166 | 1
GEN-2020-036 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 363427.6653 | 3.615% | 10052968 | 0.01598
GEN-2020-036 | 02 - Nebraska | 156969 | ERIS | Substation 3740; 345kV GEN-2020-036 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-038 (303/Hybrid), into the Point of Interconnection (POI) at Substation 3740; 345kV | 150000 | 100% | 150000 | 1
GEN-2020-036 | 02 - Nebraska | 156970 | ERIS | Substation 3740; 345kV GEN-2020-036, GEN-2020-038 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-036, GEN-2020-038 (303/Hybrid and 303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | 3740372 | 50% | 7480744 | 1
GEN-2020-038 | 02 - Nebraska | 156970 | ERIS | Substation 3740; 345kV GEN-2020-036, GEN-2020-038 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-036, GEN-2020-038 (303/Hybrid and 303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | 3740372 | 50% | 7480744 | 1
GEN-2020-038 | 02 - Nebraska | 156971 | ERIS | Substation 3740; 345kV GEN-2020-038 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-038 (303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | 150000 | 100% | 150000 | 1
GEN-2020-043 | 02 - Nebraska | 156390 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-043 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 2292537 | 100% | 2292537 | 1
GEN-2020-043 | 02 - Nebraska | 156394 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043, GEN-2020-044, GEN-2020-045 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-043, GEN-2020-044, GEN-2020-045 (Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 9139550 | 33.33% | 27418650 | 1
GEN-2020-044 | 02 - Nebraska | 156391 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-044 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-044 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 2292537 | 100% | 2292537 | 1
GEN-2020-044 | 02 - Nebraska | 156394 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043, GEN-2020-044, GEN-2020-045 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-043, GEN-2020-044, GEN-2020-045 (Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 9139550 | 33.33% | 27418650 | 1
GEN-2020-045 | 02 - Nebraska | 156392 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-045 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-045 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 2292537 | 100% | 2292537 | 1
GEN-2020-045 | 02 - Nebraska | 156394 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043, GEN-2020-044, GEN-2020-045 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-043, GEN-2020-044, GEN-2020-045 (Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 9139550 | 33.33% | 27418650 | 1
GEN-2020-069 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 182077.49 | 1.811% | 10052968 | 0.0459
GEN-2020-069 | 02 - Nebraska | 156892 | ERIS | Cody to Valentine 115kV line GEN-2020-069 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-069 (52.85/Wind), into the Point of Interconnection (POI) at Cody to Valentine 115kV line | 700000 | 100% | 700000 | 1
GEN-2020-069 | 02 - Nebraska | 156891 | ERIS | Cody to Valentine 115kV line GEN-2020-069 Interconnection (Non-shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-069 (52.85/Wind), into the Point of Interconnection (POI) at Cody to Valentine 115kV line | 15400000 | 100% | 15400000 | 1
GEN-2020-070 | 02 - Nebraska | TBD | ERIS | Upgrade Terminals at Hays to Great Bend | Current Study | Upgrade the existing terminals at S HAYS6 to GRTBEND6 230 kV line(39.2 miles) to a minimum ratings of 455 MVA | 192406.1156 | 44.23% | 435000 | 0.11413
GEN-2020-070 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 5183648.3349 | 51.56% | 10052968 | 0.27083
GEN-2020-070 | 02 - Nebraska | 156946 | ERIS | Postrock to Axtell 345 KV line GEN-2020-070 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-070 (255/Wind), into the Point of Interconnection (POI) at Postrock to Axtell 345 KV line | 1207987 | 100% | 1207987 | 1
GEN-2020-070 | 02 - Nebraska | 156945 | ERIS | Postrock to Axtell 345 KV line GEN-2020-070 Interconnection (Non-shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-070 (255/Wind), into the Point of Interconnection (POI) at Postrock to Axtell 345 KV line | 19231292 | 100% | 19231292 | 1
GEN-2020-077 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 434092.0291 | 4.318% | 10052968 | 0.03825
GEN-2020-077 | 02 - Nebraska | TBD | ERIS | Rebuild the FAIRBRY7 to HARBINE7 115kV line 1 | Current Study | Rebuild the existing FAIRBRY7 to HARBINE7 115 kV line(9.82 miles) to a minimum ratings of 155 MVA | 6980448.8 | 100% | 6980448.8 | 0.50491
GEN-2020-077 | 02 - Nebraska | TBD | ERIS | Rebuild the FAIRBRY7 to G20-077-TAP 115kV line 1 | Current Study | Rebuild the existing FAIRBRY7 to G20-077-TAP 115 kV line(10.83 miles) to a minimum ratings of 160 MVA | 7698397.2 | 100% | 7698397.2 | 0.50491
GEN-2020-077 | 02 - Nebraska | TBD | ERIS | Rebuild the HEBRN N7 to G20-077-TAP 115kV line 1 | Current Study | Rebuild the existing HEBRN N7 to G20-077-TAP 115 kV line(11.27 miles) to a minimum ratings of 155 MVA | 8011166.8 | 100% | 8011166.8 | 0.49509
GEN-2020-077 | 02 - Nebraska | TBD | ERIS | Rebuild the BEATRCE7 to HARBINE7 115kV line 1 | Current Study | Rebuild the existing BEATRCE7 to HARBINE7 115 kV line(14.08 miles) to a minimum ratings of 142 MVA | 10008627.2 | 100% | 10008627.2 | 0.36772
GEN-2020-077 | 02 - Nebraska | 156936 | ERIS | North Hebron to Fairbury 115 kV GEN-2020-077 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-077 (151.2/Wind), into the Point of Interconnection (POI) at North Hebron to Fairbury 115 kV | 700000 | 100% | 700000 | 1
GEN-2020-077 | 02 - Nebraska | 156935 | ERIS | North Hebron to Fairbury 115 kV GEN-2020-077 Interconnection (Non-shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-077 (151.2/Wind), into the Point of Interconnection (POI) at North Hebron to Fairbury 115 kV | 10600000 | 100% | 10600000 | 1
GEN-2020-078 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 123921.2124 | 1.233% | 10052968 | 0.01651
GEN-2020-078 | 02 - Nebraska | 143684 | ERIS | Substation 1226 to Substation 1237, 161kV Tap GEN-2020-078 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-078 (100/Solar), into the Point of Interconnection (POI) at Substation 1226 to Substation 1237, 161kV Tap | 150000 | 100% | 150000 | 1
GEN-2020-078 | 02 - Nebraska | 143685 | ERIS | Substation 1226 to Substation 1237, 161kV Tap GEN-2020-078 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-078 (100/Solar), into the Point of Interconnection (POI) at Substation 1226 to Substation 1237, 161kV Tap | 16266338 | 100% | 16266338 | 1
GEN-2020-084 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 439503.7307 | 4.372% | 10052968 | 0.01673
GEN-2020-084 | 02 - Nebraska | 156031 | ERIS | Ft. Calhoun - Raun 345 kV Line Tap (DISIS-2018-001) | Contingent | Facilitate the interconnection of GEN-2018-043 | 0 | 100% | 0 | 1
GEN-2020-084 | 02 - Nebraska | TBD | NRIS | S1209 - S1231 Ckt 2 161 kV Reconductor | Contingent | Reconductor 3.3 miles of S1209 - S1231 161 kV Ckt 2 | 0 | 100% | 3647471 | 0.03216
ASGI-2020-001 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0.1038% | 87298154 | 0.00498
GEN-2020-084 | 02 - Nebraska | 156949 | ERIS | Raun - Fort Calhoun 345 kV GEN-2020-084 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-084 (350/Solar), into the Point of Interconnection (POI) at Raun - Fort Calhoun 345 kV (Sharing a GEN Tie line with GEN-2018-043) | 3984923 | 100% | 3984923 | 1
GEN-2020-084 | 02 - Nebraska | 156950 | ERIS | Raun - Fort Calhoun 345 kV GEN-2020-084 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-084 (350/Solar), into the Point of Interconnection (POI) at Raun - Fort Calhoun 345 kV (Sharing a GEN Tie line with GEN-2018-043) | 1375000 | 100% | 1375000 | 1
GEN-2020-094 | 02 - Nebraska | TBD | ERIS | Replace Post Rock 345-230 kV Transformer | Current Study | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | 329130.537 | 3.274% | 10052968 | 0.01754
GEN-2020-094 | 02 - Nebraska | 156931 | ERIS | Neb. City - 103rd & Rokeby 345 kV GEN-2020-094 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-094 (250/Solar), into the Point of Interconnection (POI) at Neb. City - 103rd & Rokeby 345 kV | 19120517 | 100% | 19120517 | 1
GEN-2020-094 | 02 - Nebraska | 156932 | ERIS | Neb. City - 103rd & Rokeby 345 kV GEN-2020-094 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-094 (250/Solar), into the Point of Interconnection (POI) at Neb. City - 103rd & Rokeby 345 kV | 17125000 | 100% | 17125000 | 1
ASGI-2020-003 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0.1319% | 87298154 | 0.00633
ASGI-2020-001 | 03 - Central | TBD | ERIS | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to G20-076-TAP 345 kV line(22 miles) to a minimum ratings of 1570 MVA | 46259.1339 | 0.1837% | 25177768 | 0.03411
GEN-2020-003 | 03 - Central | 122598 | NRIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 3.172% | 87298154 | 0.09184
ASGI-2020-003 | 03 - Central | TBD | ERIS | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to G20-076-TAP 345 kV line(22 miles) to a minimum ratings of 1570 MVA | 43207.7398 | 0.1716% | 25177768 | 0.03186
GEN-2020-003 | 03 - Central | 156902 | ERIS | East Substation 69 kV GEN-2020-003 Interconnection (TOIF) (KPP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-003 (58/Thermal), into the Point of Interconnection (POI) at East Substation 69 kV | 130000 | 100% | 130000 | 1
GEN-2020-003 | 03 - Central | 156901 | ERIS | East Substation 69 kV GEN-2020-003 Interconnection (Non-shared NU) (KPP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-003 (58/Thermal), into the Point of Interconnection (POI) at East Substation 69 kV | 1667200 | 100% | 1667200 | 1
GEN-2020-007 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 25.23% | 87298154 | 0.06518
GEN-2020-007 | 03 - Central | 156904 | ERIS | Evergy La Cygne to Wolf Creek 345kV Substation GEN-2020-007 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-007 (650/Hybrid), into the Point of Interconnection (POI) at Evergy La Cygne to Wolf Creek 345kV Substation | 1705966 | 100% | 1705966 | 1
GEN-2020-007 | 03 - Central | 156903 | ERIS | Evergy La Cygne to Wolf Creek 345kV Substation GEN-2020-007 Interconnection (Non-shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-007 (650/Hybrid), into the Point of Interconnection (POI) at Evergy La Cygne to Wolf Creek 345kV Substation | 25589611 | 100% | 25589611 | 1
GEN-2020-057 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 9.875% | 87298154 | 0.03907
GEN-2020-007 | 03 - Central | TBD | ERIS | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1 | Current Study | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1(11.9 miles) to a minimum ratings of 800 MVA | 24659.088 | 34.46% | 71563 | 0.12824
GEN-2020-007 | 03 - Central | TBD | NRIS | Rebuild the STHTOWN5 to HICKMAN5 161kV line 1 | Current Study | Rebuild the existing STHTOWN5 to HICKMAN5 161 kV line(5.55 miles) to a minimum ratings of 320 MVA | 35962.4369 | 47.95% | 75000 | 0.03853
GEN-2020-007 | 03 - Central | TBD | NRIS | Upgrade terminal equipment at West Gardner 345/161 kV transformer | Current Study | Upgrade terminal equipment to achieve the minimum rating of 600 MVA | 140637.3241 | 42.05% | 334423 | 0.05843
GEN-2020-007 | 03 - Central | TBD | NRIS | Upgrade terminal equipment at Stilwel 345/161 kV transformer | Current Study | Upgrade terminal equipment to achieve normal rating of 550 MVA and emergency 605 MVA | 214779.2787 | 64.22% | 334423 | 0.06366
GEN-2020-007 | 03 - Central | TBD | ERIS | Rebuild the LACYGNE7 to G20-007-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G20-007-TAP 345 kV line(0.6 miles) to a minimum ratings of 1485 MVA | 403302.7666 | 82.48% | 488950.8 | 0.77004
GEN-2020-007 | 03 - Central | TBD | NRIS | Rebuild the CRAIG 5 to LENEXA 5 161kV line 2 | Current Study | Rebuild the existing CRAIG 5 to LENEXA 5 161 kV line(3.02 miles) to a minimum ratings of 460 MVA | 689139.2851 | 22.22% | 3102115 | 0.01826
GEN-2020-007 | 03 - Central | TBD | NRIS | Rebuild the WGARDNR5 to BNSF 5 161kV line 1 | Current Study | Rebuild the existing WGARDNR5 to BNSF 5 161 kV line(2.6 miles) to a minimum ratings of 390 MVA | 696870.6617 | 25.52% | 2730733 | 0.02007
GEN-2020-007 | 03 - Central | TBD | NRIS | Rebuild the SHWNMSN5 to LENEXA 5 161kV line 1 | Current Study | Rebuild the existing SHWNMSN5 to LENEXA 5 161 kV line(3.91 miles) to a minimum ratings of 420 MVA | 995954.0132 | 23.56% | 4227303 | 0.03192
GEN-2020-007 | 03 - Central | TBD | NRIS | Rebuild the MOONLT 5 to BNSF 5 161kV line 1 | Current Study | Rebuild the existing MOONLT 5 to BNSF 5 161 kV line(3.43 miles) to a minimum ratings of 390 MVA | 1106189.3768 | 25.52% | 4334675 | 0.02007
GEN-2020-007 | 03 - Central | TBD | NRIS | Rebuild the MARTCIT5 to REDEL 5 161kV line 1 | Current Study | Rebuild the existing MARTCIT5 to REDEL 5 161 kV line(3.86 miles) to a minimum ratings of 400 MVA | 1652652.8054 | 38.61% | 4280000 | 0.0491
GEN-2020-007 | 03 - Central | TBD | NRIS | Rebuild the STILWEL5 to REDEL 5 161kV line 1 | Current Study | Rebuild the existing STILWEL5 to REDEL 5 161 kV line(4.22 miles) to a minimum ratings of 420 MVA | 1693410.3898 | 38.61% | 4385553 | 0.0491
GEN-2020-007 | 03 - Central | TBD | ERIS | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to G20-076-TAP 345 kV line(22 miles) to a minimum ratings of 1570 MVA | 2029496.7179 | 8.061% | 25177768 | 0.08058
GEN-2020-007 | 03 - Central | TBD | NRIS | Rebuild the STILWEL5 to HICKMAN5 161kV line 1 | Current Study | Rebuild the existing STILWEL5 to HICKMAN5 161 kV line(13.51 miles) to a minimum ratings of 365 MVA | 6336967.9765 | 47.95% | 13215806.24 | 0.03853
GEN-2020-008 | 03 - Central | 156895 | ERIS | Corporation Carpenter 345kV Substation GEN-2020-008 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-008 (250/Hybrid), into the Point of Interconnection (POI) at Corporation Carpenter 345kV Substation | 1636674 | 100% | 1636674 | 1
GEN-2020-008 | 03 - Central | 156896 | ERIS | Corporation Carpenter 345kV Substation GEN-2020-008 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-008 (250/Hybrid), into the Point of Interconnection (POI) at Corporation Carpenter 345kV Substation | 2424709 | 100% | 2424709 | 1
GEN-2020-052 | 03 - Central | TBD | ERIS | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1 | Current Study | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1(11.9 miles) to a minimum ratings of 800 MVA | 3338.4138 | 4.665% | 71563 | 0.04496
GEN-2020-052 | 03 - Central | 156934 | ERIS | Neosho-Delaware 345 kV GEN-2020-052 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-052 (251/Wind), into the Point of Interconnection (POI) at Neosho-Delaware 345 kV | 1705966 | 100% | 1705966 | 1
GEN-2020-052 | 03 - Central | 156933 | ERIS | Neosho-Delaware 345 kV GEN-2020-052 Interconnection (Non-shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-052 (251/Wind), into the Point of Interconnection (POI) at Neosho-Delaware 345 kV | 22839882 | 100% | 22839882 | 1
GEN-2020-056 | 03 - Central | 144325 | ERIS | Russell 115 kV Substation GEN-2020-056 Interconnection (Non-shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-056 (20/Solar), into the Point of Interconnection (POI) at Russell 115 kV Substation | 219181 | 100% | 219181 | 1
GEN-2020-056 | 03 - Central | 144324 | ERIS | Russell 115 kV Substation GEN-2020-056 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-056 (20/Solar), into the Point of Interconnection (POI) at Russell 115 kV Substation | 2268883 | 100% | 2268883 | 1
GEN-2020-057 | 03 - Central | TBD | ERIS | Extend Craig-West Gardner 345 kV, Clearview-Eudora 115 kV Tap,new 345/115 kV substation | Contingent | Contingent upgrade from 2023 ITP. Build a new substation tapping the extention of Craig-West Gardner 345 kV and Clearview-Eudora 115 kV Tap | 0 | 50% | 42141390 | 1
GEN-2020-058 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 9.875% | 87298154 | 0.03907
GEN-2020-057 | 03 - Central | TBD | NRIS | Rebuild the STHTOWN5 to HICKMAN5 161kV line 1 | Current Study | Rebuild the existing STHTOWN5 to HICKMAN5 161 kV line(5.55 miles) to a minimum ratings of 320 MVA | 10460.001 | 13.95% | 75000 | 0.01716
GEN-2020-057 | 03 - Central | TBD | ERIS | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1 | Current Study | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1(11.9 miles) to a minimum ratings of 800 MVA | 10704.3741 | 14.96% | 71563 | 0.08524
GEN-2020-057 | 03 - Central | TBD | ERIS | Replacing the CT/Relay of West Gardner R2-3 Breaker | Current Study | Replace the CT/Relay of West Gardner R2-3 Breaker on the WGARDNR5 to CEDRCRK5 161 kV line(14.6 miles) to a minimum ratings of 435 MVA | 12357.2071 | 13.56% | 91147 | 0.00948
GEN-2020-057 | 03 - Central | TBD | NRIS | Upgrade terminal equipment at Stilwel 345/161 kV transformer | Current Study | Upgrade terminal equipment to achieve normal rating of 550 MVA and emergency 605 MVA | 59821.8607 | 17.89% | 334423 | 0.02715
GEN-2020-057 | 03 - Central | TBD | NRIS | Upgrade terminal equipment at West Gardner 345/161 kV transformer | Current Study | Upgrade terminal equipment to achieve the minimum rating of 600 MVA | 96892.8379 | 28.97% | 334423 | 0.06164
GEN-2020-057 | 03 - Central | TBD | NRIS | Rebuild the WGARDNR5 to BNSF 5 161kV line 1 | Current Study | Rebuild the existing WGARDNR5 to BNSF 5 161 kV line(2.6 miles) to a minimum ratings of 390 MVA | 483455.3236 | 17.7% | 2730733 | 0.02132
GEN-2020-057 | 03 - Central | TBD | ERIS | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to G20-076-TAP 345 kV line(22 miles) to a minimum ratings of 1570 MVA | 694618.762 | 2.759% | 25177768 | 0.04223
GEN-2020-057 | 03 - Central | TBD | NRIS | Rebuild the MOONLT 5 to BNSF 5 161kV line 1 | Current Study | Rebuild the existing MOONLT 5 to BNSF 5 161 kV line(3.43 miles) to a minimum ratings of 390 MVA | 767420.947 | 17.7% | 4334675 | 0.02132
GEN-2020-057 | 03 - Central | TBD | NRIS | Rebuild the MARTCIT5 to REDEL 5 161kV line 1 | Current Study | Rebuild the existing MARTCIT5 to REDEL 5 161 kV line(3.86 miles) to a minimum ratings of 400 MVA | 834651.2884 | 19.5% | 4280000 | 0.03797
GEN-2020-057 | 03 - Central | TBD | NRIS | Rebuild the STILWEL5 to REDEL 5 161kV line 1 | Current Study | Rebuild the existing STILWEL5 to REDEL 5 161 kV line(4.22 miles) to a minimum ratings of 420 MVA | 855235.3883 | 19.5% | 4385553 | 0.03797
GEN-2020-057 | 03 - Central | TBD | NRIS | Rebuild the CRAIG 5 to LENEXA 5 161kV line 2 | Current Study | Rebuild the existing CRAIG 5 to LENEXA 5 161 kV line(3.02 miles) to a minimum ratings of 460 MVA | 1083991.3029 | 34.94% | 3102115 | 0.04398
GEN-2020-057 | 03 - Central | TBD | NRIS | Rebuild the SHWNMSN5 to LENEXA 5 161kV line 1 | Current Study | Rebuild the existing SHWNMSN5 to LENEXA 5 161 kV line(3.91 miles) to a minimum ratings of 420 MVA | 1387879.0543 | 32.83% | 4227303 | 0.06811
GEN-2020-057 | 03 - Central | TBD | NRIS | Rebuild the STILWEL5 to HICKMAN5 161kV line 1 | Current Study | Rebuild the existing STILWEL5 to HICKMAN5 161 kV line(13.51 miles) to a minimum ratings of 365 MVA | 1843164.6177 | 13.95% | 13215806.24 | 0.01716
GEN-2020-057 | 03 - Central | 156898 | ERIS | Craig-West Gardner 345 kV GEN-2020-057 and GEN-2020-058 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Solar) and GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Craig-West Gardner 345 kV | 468824.5 | 50% | 937649 | 1
GEN-2020-057 | 03 - Central | 156897 | ERIS | Craig-West Gardner 345 kV GEN-2020-057 and GEN-2020-058 Interconnection (Non-shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Solar) and GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Craig-West Gardner 345 kV | 1143564.5 | 50% | 2287129 | 1
GEN-2020-058 | 03 - Central | TBD | ERIS | Extend Craig-West Gardner 345 kV, Clearview-Eudora 115 kV Tap,new 345/115 kV substation | Contingent | Contingent upgrade from 2023 ITP. Build a new substation tapping the extention of Craig-West Gardner 345 kV and Clearview-Eudora 115 kV Tap | 0 | 50% | 42141390 | 1
GEN-2020-072 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0.3063% | 87298154 | 0.00343
GEN-2020-058 | 03 - Central | TBD | NRIS | Rebuild the STHTOWN5 to HICKMAN5 161kV line 1 | Current Study | Rebuild the existing STHTOWN5 to HICKMAN5 161 kV line(5.55 miles) to a minimum ratings of 320 MVA | 10460.001 | 13.95% | 75000 | 0.01716
GEN-2020-058 | 03 - Central | TBD | ERIS | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1 | Current Study | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1(11.9 miles) to a minimum ratings of 800 MVA | 10704.3741 | 14.96% | 71563 | 0.08524
GEN-2020-058 | 03 - Central | TBD | ERIS | Replacing the CT/Relay of West Gardner R2-3 Breaker | Current Study | Replace the CT/Relay of West Gardner R2-3 Breaker on the WGARDNR5 to CEDRCRK5 161 kV line(14.6 miles) to a minimum ratings of 435 MVA | 12357.2071 | 13.56% | 91147 | 0.00948
GEN-2020-058 | 03 - Central | TBD | NRIS | Upgrade terminal equipment at Stilwel 345/161 kV transformer | Current Study | Upgrade terminal equipment to achieve normal rating of 550 MVA and emergency 605 MVA | 59821.8607 | 17.89% | 334423 | 0.02715
GEN-2020-058 | 03 - Central | TBD | NRIS | Upgrade terminal equipment at West Gardner 345/161 kV transformer | Current Study | Upgrade terminal equipment to achieve the minimum rating of 600 MVA | 96892.8379 | 28.97% | 334423 | 0.06164
GEN-2020-058 | 03 - Central | TBD | NRIS | Rebuild the WGARDNR5 to BNSF 5 161kV line 1 | Current Study | Rebuild the existing WGARDNR5 to BNSF 5 161 kV line(2.6 miles) to a minimum ratings of 390 MVA | 483455.3236 | 17.7% | 2730733 | 0.02132
GEN-2020-058 | 03 - Central | TBD | ERIS | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to G20-076-TAP 345 kV line(22 miles) to a minimum ratings of 1570 MVA | 694618.762 | 2.759% | 25177768 | 0.04223
GEN-2020-058 | 03 - Central | TBD | NRIS | Rebuild the MOONLT 5 to BNSF 5 161kV line 1 | Current Study | Rebuild the existing MOONLT 5 to BNSF 5 161 kV line(3.43 miles) to a minimum ratings of 390 MVA | 767420.947 | 17.7% | 4334675 | 0.02132
GEN-2020-058 | 03 - Central | TBD | NRIS | Rebuild the MARTCIT5 to REDEL 5 161kV line 1 | Current Study | Rebuild the existing MARTCIT5 to REDEL 5 161 kV line(3.86 miles) to a minimum ratings of 400 MVA | 834651.2884 | 19.5% | 4280000 | 0.03797
GEN-2020-058 | 03 - Central | TBD | NRIS | Rebuild the STILWEL5 to REDEL 5 161kV line 1 | Current Study | Rebuild the existing STILWEL5 to REDEL 5 161 kV line(4.22 miles) to a minimum ratings of 420 MVA | 855235.3883 | 19.5% | 4385553 | 0.03797
GEN-2020-058 | 03 - Central | TBD | NRIS | Rebuild the CRAIG 5 to LENEXA 5 161kV line 2 | Current Study | Rebuild the existing CRAIG 5 to LENEXA 5 161 kV line(3.02 miles) to a minimum ratings of 460 MVA | 1083991.3029 | 34.94% | 3102115 | 0.04398
GEN-2020-058 | 03 - Central | TBD | NRIS | Rebuild the SHWNMSN5 to LENEXA 5 161kV line 1 | Current Study | Rebuild the existing SHWNMSN5 to LENEXA 5 161 kV line(3.91 miles) to a minimum ratings of 420 MVA | 1387879.0543 | 32.83% | 4227303 | 0.06811
GEN-2020-058 | 03 - Central | TBD | NRIS | Rebuild the STILWEL5 to HICKMAN5 161kV line 1 | Current Study | Rebuild the existing STILWEL5 to HICKMAN5 161 kV line(13.51 miles) to a minimum ratings of 365 MVA | 1843164.6177 | 13.95% | 13215806.24 | 0.01716
GEN-2020-058 | 03 - Central | 156898 | ERIS | Craig-West Gardner 345 kV GEN-2020-057 and GEN-2020-058 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Solar) and GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Craig-West Gardner 345 kV | 468824.5 | 50% | 937649 | 1
GEN-2020-058 | 03 - Central | 156897 | ERIS | Craig-West Gardner 345 kV GEN-2020-057 and GEN-2020-058 Interconnection (Non-shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Solar) and GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Craig-West Gardner 345 kV | 1143564.5 | 50% | 2287129 | 1
GEN-2020-061 | 03 - Central | 156944 | ERIS | Pleasant Hill 345/161/69 kV Substation GEN-2020-061 Interconnection (TOIF) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-061 (29/Thermal), into the Point of Interconnection (POI) at Pleasant Hill 345/161/69 kV Substation | 0 | 100% | 0 | 1
GEN-2020-061 | 03 - Central | 156943 | ERIS | Pleasant Hill 345/161/69 kV Substation GEN-2020-061 Interconnection (Non-shared NU) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-061 (29/Thermal), into the Point of Interconnection (POI) at Pleasant Hill 345/161/69 kV Substation | 112911 | 100% | 112911 | 1
GEN-2020-064 | 03 - Central | 156878 | ERIS | 4544 Stateline CC 161kV Substation GEN-2020-064 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-064 (64/Thermal), into the Point of Interconnection (POI) at 4544 Stateline CC 161kV Substation |  | 100% | 0 | 1
GEN-2020-064 | 03 - Central | 156877 | ERIS | 4544 Stateline CC 161kV Substation GEN-2020-064 Interconnection (Non-shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-064 (64/Thermal), into the Point of Interconnection (POI) at 4544 Stateline CC 161kV Substation |  | 100% | 0 | 1
GEN-2020-071 | 03 - Central | TBD | ERIS | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1 | Current Study | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1(11.9 miles) to a minimum ratings of 800 MVA | 3647.673 | 5.097% | 71563 | 0.04893
GEN-2020-071 | 03 - Central | 156973 | ERIS | Swissvale to Morris 230 KV line GEN-2020-071 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-071 (252/Wind), into the Point of Interconnection (POI) at Swissvale to Morris 230 KV line | 1705966 | 100% | 1705966 | 1
GEN-2020-071 | 03 - Central | 156972 | ERIS | Swissvale to Morris 230 KV line GEN-2020-071 Interconnection (Non-shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-071 (252/Wind), into the Point of Interconnection (POI) at Swissvale to Morris 230 KV line | 22839882 | 100% | 22839882 | 1
GEN-2020-073 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 2.489% | 87298154 | 0.02787
GEN-2020-072 | 03 - Central | TBD | ERIS | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to G20-076-TAP 345 kV line(22 miles) to a minimum ratings of 1570 MVA | 210691.4944 | 0.8368% | 25177768 | 0.03625
GEN-2020-072 | 03 - Central | 156987 | ERIS | Windsor to AEC Sedalia 161 kV line GEN-2020-072 Interconnection (TOIF) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-072 (150/Hybrid), into the Point of Interconnection (POI) at Windsor to AEC Sedalia 161 kV line | 890009.14 | 100% | 890009.14 | 1
GEN-2020-072 | 03 - Central | 156986 | ERIS | Windsor to AEC Sedalia 161 kV line GEN-2020-072 Interconnection (Non-shared NU) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-072 (150/Hybrid), into the Point of Interconnection (POI) at Windsor to AEC Sedalia 161 kV line | 12297085 | 100% | 12297085 | 1
GEN-2020-076 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 12.21% | 87298154 | 0.10256
GEN-2020-073 | 03 - Central | TBD | ERIS | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1 | Current Study | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1(11.9 miles) to a minimum ratings of 800 MVA | 3595.6486 | 5.024% | 71563 | 0.08103
GEN-2020-073 | 03 - Central | TBD | NRIS | Rebuild the STHTOWN5 to HICKMAN5 161kV line 1 | Current Study | Rebuild the existing STHTOWN5 to HICKMAN5 161 kV line(5.55 miles) to a minimum ratings of 320 MVA | 10493.8605 | 13.99% | 75000 | 0.04872
GEN-2020-073 | 03 - Central | TBD | ERIS | Replacing the CT/Relay of West Gardner R2-3 Breaker | Current Study | Replace the CT/Relay of West Gardner R2-3 Breaker on the WGARDNR5 to CEDRCRK5 161 kV line(14.6 miles) to a minimum ratings of 435 MVA | 66432.5858 | 72.89% | 91147 | 0.14423
GEN-2020-073 | 03 - Central | TBD | NRIS | Rebuild the CRAIG 5 to LENEXA 5 161kV line 2 | Current Study | Rebuild the existing CRAIG 5 to LENEXA 5 161 kV line(3.02 miles) to a minimum ratings of 460 MVA | 244993.1092 | 7.898% | 3102115 | 0.02813
GEN-2020-073 | 03 - Central | TBD | ERIS | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to G20-076-TAP 345 kV line(22 miles) to a minimum ratings of 1570 MVA | 248063.8064 | 0.9852% | 25177768 | 0.04268
GEN-2020-073 | 03 - Central | TBD | NRIS | Rebuild the SHWNMSN5 to LENEXA 5 161kV line 1 | Current Study | Rebuild the existing SHWNMSN5 to LENEXA 5 161 kV line(3.91 miles) to a minimum ratings of 420 MVA | 334528.7988 | 7.914% | 4227303 | 0.04646
GEN-2020-073 | 03 - Central | TBD | NRIS | Rebuild the MARTCIT5 to REDEL 5 161kV line 1 | Current Study | Rebuild the existing MARTCIT5 to REDEL 5 161 kV line(3.86 miles) to a minimum ratings of 400 MVA | 588927.4747 | 13.76% | 4280000 | 0.07582
GEN-2020-073 | 03 - Central | TBD | NRIS | Rebuild the STILWEL5 to REDEL 5 161kV line 1 | Current Study | Rebuild the existing STILWEL5 to REDEL 5 161 kV line(4.22 miles) to a minimum ratings of 420 MVA | 603451.5546 | 13.76% | 4385553 | 0.07582
GEN-2020-073 | 03 - Central | TBD | NRIS | Rebuild the WGARDNR5 to BNSF 5 161kV line 1 | Current Study | Rebuild the existing WGARDNR5 to BNSF 5 161 kV line(2.6 miles) to a minimum ratings of 390 MVA | 928119.2221 | 33.99% | 2730733 | 0.11583
GEN-2020-073 | 03 - Central | TBD | NRIS | Rebuild the MOONLT 5 to BNSF 5 161kV line 1 | Current Study | Rebuild the existing MOONLT 5 to BNSF 5 161 kV line(3.43 miles) to a minimum ratings of 390 MVA | 1473265.6722 | 33.99% | 4334675 | 0.11583
GEN-2020-073 | 03 - Central | TBD | ERIS | Rebuild the CENTENL5 to PAOLA 5 161kV line 1 | Current Study | Rebuild the existing CENTENL5 to PAOLA 5 161 kV line(2.84 miles) to a minimum ratings of 290 MVA | 1684418.6292 | 60.61% | 2779156.16 | 0.27661
GEN-2020-073 | 03 - Central | TBD | NRIS | Rebuild the STILWEL5 to HICKMAN5 161kV line 1 | Current Study | Rebuild the existing STILWEL5 to HICKMAN5 161 kV line(13.51 miles) to a minimum ratings of 365 MVA | 1849131.0257 | 13.99% | 13215806.24 | 0.04872
GEN-2020-073 | 03 - Central | TBD | ERIS | Rebuild the MARMTNE5 to DAKOTA_5 161kV line 1 | Current Study | Rebuild the existing MARMTNE5 to DAKOTA_5 161 kV line(10.5 miles) to a minimum ratings of 310 MVA | 2397660.0702 | 23.34% | 10271352 | 0.13331
GEN-2020-073 | 03 - Central | 156959 | ERIS | SE Ottawa to Pleasant Valley 161kV GEN-2020-073 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-073 (190/Hybrid), into the Point of Interconnection (POI) at SE Ottawa to Pleasant Valley 161kV | 890009 | 100% | 890009 | 1
GEN-2020-073 | 03 - Central | 156958 | ERIS | SE Ottawa to Pleasant Valley 161kV GEN-2020-073 Interconnection (Non-shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-073 (190/Hybrid), into the Point of Interconnection (POI) at SE Ottawa to Pleasant Valley 161kV | 12351050 | 100% | 12351050 | 1
GEN-2020-076 | 03 - Central | TBD | ERIS | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1 | Current Study | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1(11.9 miles) to a minimum ratings of 800 MVA | 2898.5285 | 4.05% | 71563 | 0.04899
GEN-2020-076 | 03 - Central | TBD | ERIS | Rebuild the LACYGNE7 to G20-007-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G20-007-TAP 345 kV line(0.6 miles) to a minimum ratings of 1485 MVA | 24470.8667 | 5.005% | 488950.8 | 0.15185
GEN-2020-076 | 03 - Central | TBD | ERIS | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to G20-076-TAP 345 kV line(22 miles) to a minimum ratings of 1570 MVA | 5757002.2024 | 22.87% | 25177768 | 0.74288
GEN-2020-086 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent |  | 0 | 30.53% | 87298154 | 0.10256
GEN-2020-076 | 03 - Central | 156883 | ERIS | Benton to Wolf Creek 345 kV Line GEN-2020-076 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-076 (200/Battery/Storage), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | 1705966 | 100% | 1705966 | 1
GEN-2020-076 | 03 - Central | 156885 | ERIS | Benton to Wolf Creek 345kV Line GEN-2020-076, GEN-2020-086 Interconnection (DISIS-2020-001) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-076, GEN-2020-086 (200/Battery/Storage and 500/Solar), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | 6525680.5714 | 28.57% | 22839882 | 1
GEN-2020-079 | 03 - Central | TBD | ERIS | Terminal upgrades in the NEO_SPA substation | Current Study | Upgrade terminals on the NEO SPA5 to TIP292 5 161 kV line(10.6 miles) to achieve a minimum rating of 232 MVA. | 1096294.231 | 84.33% | 1300000 | 0.1109
GEN-2020-079 | 03 - Central | 156952 | ERIS | Riverton-Neosho 161kV line GEN-2020-079 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-079 (225/Hybrid), into the Point of Interconnection (POI) at Riverton-Neosho 161kV line | 632109 | 100% | 632109 | 1
GEN-2020-079 | 03 - Central | 156951 | ERIS | Riverton-Neosho 161kV line GEN-2020-079 Interconnection (Non-shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-079 (225/Hybrid), into the Point of Interconnection (POI) at Riverton-Neosho 161kV line | 12010063 | 100% | 12010063 | 1
GEN-2020-086 | 03 - Central | TBD | ERIS | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1 | Current Study | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1(11.9 miles) to a minimum ratings of 800 MVA | 7246.3213 | 10.13% | 71563 | 0.04899
GEN-2020-086 | 03 - Central | TBD | ERIS | Rebuild the LACYGNE7 to G20-007-TAP 345kV line 1 | Current Study | Rebuild the existing LACYGNE7 to G20-007-TAP 345 kV line(0.6 miles) to a minimum ratings of 1485 MVA | 61177.1667 | 12.51% | 488950.8 | 0.15185
GEN-2020-086 | 03 - Central | TBD | ERIS | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to G20-076-TAP 345 kV line(22 miles) to a minimum ratings of 1570 MVA | 14392505.506 | 57.16% | 25177768 | 0.74288
GEN-2020-089 | 03 - Central | 122598 | NRIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 6.078% | 87298154 | 0.09816
GEN-2020-086 | 03 - Central | 156884 | ERIS | Benton to Wolf Creek 345 kV Line GEN-2020-086 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-086 (500/Solar), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | 112911 | 100% | 112911 | 1
GEN-2020-086 | 03 - Central | 156885 | ERIS | Benton to Wolf Creek 345kV Line GEN-2020-076, GEN-2020-086 Interconnection (DISIS-2020-001) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-076, GEN-2020-086 (200/Battery/Storage and 500/Solar), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | 16314201.4286 | 71.43% | 22839882 | 1
GEN-2020-088 | 03 - Central | TBD | ERIS | Terminal upgrades in the NEO_SPA substation | Current Study | Upgrade terminals on the NEO SPA5 to TIP292 5 161 kV line(10.6 miles) to achieve a minimum rating of 232 MVA. | 203705.769 | 15.67% | 1300000 | 0.03091
GEN-2020-088 | 03 - Central | TBD | ERIS | Terminal upgrades at both ends of the line LAR382 5 to MON383 | Current Study | Upgrade terminals on the LAR382 to MON383 161 kV line(15.56 miles) to achieve a minimum rating of 230 MVA. | 250000 | 100% | 250000 | 0.31311
GEN-2020-088 | 03 - Central | 156916 | ERIS | La Russell 161 kV Substation GEN-2020-088 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-088 (150/Solar), into the Point of Interconnection (POI) at La Russell 161 kV Substation | 221466 | 100% | 221466 | 1
GEN-2020-088 | 03 - Central | 156915 | ERIS | La Russell 161 kV Substation GEN-2020-088 Interconnection (Non-shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-088 (150/Solar), into the Point of Interconnection (POI) at La Russell 161 kV Substation | 4207850 | 100% | 4207850 | 1
GEN-2020-089 | 03 - Central | TBD | ERIS | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1 | Current Study | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1(11.9 miles) to a minimum ratings of 800 MVA | 1819.8192 | 2.543% | 71563 | 0.05915
GEN-2020-089 | 03 - Central | TBD | NRIS | Rebuild the STHTOWN5 to HICKMAN5 161kV line 1 | Current Study | Rebuild the existing STHTOWN5 to HICKMAN5 161 kV line(5.55 miles) to a minimum ratings of 320 MVA | 7623.7006 | 10.16% | 75000 | 0.05105
GEN-2020-089 | 03 - Central | TBD | ERIS | Terminal upgrades at the line CNTRVIL5 to PAOLA 5 161kV line 1 | Current Study | Upgrade terminals on the CNTRVIL5 to PAOLA 5 161 kV line(23.8 miles) to achieve a minimum rating of 285 MVA | 50000 | 100% | 50000 | 0.36837
GEN-2020-089 | 03 - Central | TBD | NRIS | Rebuild the SHWNMSN5 to LENEXA 5 161kV line 1 | Current Study | Rebuild the existing SHWNMSN5 to LENEXA 5 161 kV line(3.91 miles) to a minimum ratings of 420 MVA | 121062.0793 | 2.864% | 4227303 | 0.02425
GEN-2020-089 | 03 - Central | TBD | NRIS | Rebuild the WGARDNR5 to BNSF 5 161kV line 1 | Current Study | Rebuild the existing WGARDNR5 to BNSF 5 161 kV line(2.6 miles) to a minimum ratings of 390 MVA | 138832.469 | 5.084% | 2730733 | 0.02499
GEN-2020-089 | 03 - Central | TBD | ERIS | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to G20-076-TAP 345 kV line(22 miles) to a minimum ratings of 1570 MVA | 154662.8623 | 0.6143% | 25177768 | 0.03838
GEN-2020-089 | 03 - Central | TBD | NRIS | Rebuild the MOONLT 5 to BNSF 5 161kV line 1 | Current Study | Rebuild the existing MOONLT 5 to BNSF 5 161 kV line(3.43 miles) to a minimum ratings of 390 MVA | 220378.057 | 5.084% | 4334675 | 0.02499
GEN-2020-089 | 03 - Central | TBD | NRIS | Rebuild the MARTCIT5 to REDEL 5 161kV line 1 | Current Study | Rebuild the existing MARTCIT5 to REDEL 5 161 kV line(3.86 miles) to a minimum ratings of 400 MVA | 369117.1431 | 8.624% | 4280000 | 0.06854
GEN-2020-089 | 03 - Central | TBD | NRIS | Rebuild the STILWEL5 to REDEL 5 161kV line 1 | Current Study | Rebuild the existing STILWEL5 to REDEL 5 161 kV line(4.22 miles) to a minimum ratings of 420 MVA | 378220.279 | 8.624% | 4385553 | 0.06854
GEN-2020-089 | 03 - Central | TBD | ERIS | Rebuild the CENTENL5 to PAOLA 5 161kV line 1 | Current Study | Rebuild the existing CENTENL5 to PAOLA 5 161 kV line(2.84 miles) to a minimum ratings of 290 MVA | 1094737.5308 | 39.39% | 2779156.16 | 0.25929
GEN-2020-089 | 03 - Central | TBD | NRIS | Rebuild the STILWEL5 to HICKMAN5 161kV line 1 | Current Study | Rebuild the existing STILWEL5 to HICKMAN5 161 kV line(13.51 miles) to a minimum ratings of 365 MVA | 1343378.0024 | 10.16% | 13215806.24 | 0.05105
GEN-2020-089 | 03 - Central | TBD | ERIS | Rebuild the MARMTNE5 to DAKOTA_5 161kV line 1 | Current Study | Rebuild the existing MARMTNE5 to DAKOTA_5 161 kV line(10.5 miles) to a minimum ratings of 310 MVA | 7873691.9298 | 76.66% | 10271352 | 0.63141
GEN-2020-089 | 03 - Central | TBD | ERIS | Rebuild the CNTRVIL5 to DAKOTA_5 161kV line 1 | Current Study | Rebuild the existing CNTRVIL5 to DAKOTA_5 161 kV line(17.38 miles) to a minimum ratings of 310 MVA | 17001533.12 | 100% | 17001533.12 | 0.36837
GEN-2020-089 | 03 - Central | 156899 | ERIS | Dakota 161 kV Substation GEN-2020-089 Interconnection (Non-shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-089 (104/Solar), into the Point of Interconnection (POI) at Dakota 161 kV Substation | 730484 | 100% | 730484 | 1
GEN-2020-089 | 03 - Central | 156900 | ERIS | Dakota 161 kV Substation GEN-2020-089 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-089 (104/Solar), into the Point of Interconnection (POI) at Dakota 161 kV Substation | 890009 | 100% | 890009 | 1
GEN-2020-015 | 04 - Southeast | 112443 | NRIS | Russett - South Brown 138 kV Ckt 1 Rebuild | Contingent | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 0 | 14.22% | 10267391 | 0.02853
GEN-2020-090 | 03 - Central | TBD | ERIS | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1 | Current Study | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1(11.9 miles) to a minimum ratings of 800 MVA | 2948.7593 | 4.121% | 71563 | 0.04879
GEN-2020-090 | 03 - Central | TBD | ERIS | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1 | Current Study | Rebuild the existing BENTON 7 to G20-076-TAP 345 kV line(22 miles) to a minimum ratings of 1570 MVA | 906641.0129 | 3.601% | 25177768 | 0.11453
GEN-2020-090 | 03 - Central | 156989 | ERIS | Wolf Creek- Blackberry 345 kV Substation GEN-2020-090 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-090 (204.3/Solar), into the Point of Interconnection (POI) at Wolf Creek- Blackberry 345 kV Substation | 1705966 | 100% | 1705966 | 1
GEN-2020-090 | 03 - Central | 156988 | ERIS | Wolf Creek- Blackberry 345 kV Substation GEN-2020-090 Interconnection (Non-shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-090 (204.3/Solar), into the Point of Interconnection (POI) at Wolf Creek- Blackberry 345 kV Substation | 21420838 | 100% | 21420838 | 1
GEN-2020-010 | 04 - Southeast | 156960 | ERIS | Seiling-Taloga Substations 138kV GEN-2020-010 Interconnection (Non-shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-010 (140/Hybrid), into the Point of Interconnection (POI) at Seiling-Taloga Substations 138kV | 5000000 | 100% | 5000000 | 1
GEN-2020-010 | 04 - Southeast | 156961 | ERIS | Seiling-Taloga Substations 138kV GEN-2020-010 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-010 (140/Hybrid), into the Point of Interconnection (POI) at Seiling-Taloga Substations 138kV | 500000 | 100% | 500000 | 1
GEN-2020-012 | 04 - Southeast | 156967 | ERIS | Snyder-Altus Jct. 138kV GEN-2020-012 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-012 (113/Hybrid), into the Point of Interconnection (POI) at Snyder-Altus Jct. 138kV | 1800000 | 100% | 1800000 | 1
GEN-2020-012 | 04 - Southeast | 156966 | ERIS | Snyder-Altus Jct. 138kV GEN-2020-012 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-012 (113/Hybrid), into the Point of Interconnection (POI) at Snyder-Altus Jct. 138kV | 9100000 | 100% | 9100000 | 1
GEN-2020-012 | 04 - Southeast | TBD | NRIS | Rebuild the DUNCAN-4 to DUNCHERTP4 138kV line 1 | Current Study | Rebuild the existing DUNCAN-4 to DUNCHERTP4 138 kV line(1.6 miles) to a minimum ratings of 135 MVA | 116260.7764 | 7.536% | 1542654.4 | 0.02292
GEN-2020-012 | 04 - Southeast | TBD | NRIS | Rebuild the D.E.S.-4 to OMDUNE-4 138kV line 1 | Current Study | Rebuild the existing D.E.S.-4 to OMDUNE-4 138 kV line(1.26 miles) to a minimum ratings of 125 MVA | 126778.6315 | 10.44% | 1214840 | 0.02292
GEN-2020-012 | 04 - Southeast | TBD | NRIS | Rebuild the D.E.S.-4 to DUNCHERTP4 138kV line 1 | Current Study | Rebuild the existing D.E.S.-4 to DUNCHERTP4 138 kV line(3.53 miles) to a minimum ratings of 130 MVA | 256500.3378 | 7.536% | 3403481.27 | 0.02292
GEN-2020-012 | 04 - Southeast | TBD | ERIS | Roosevelt Tap to Hobart City 69 kV Line Rebuild | Current Study | Rebuild 1.4 miles of the Hobart City to Roosevelt Tap 69 kV line, near Hobart City to a minimum of 50 MVA (The other 8.6 miles closest to Roosevelt Tap has a summer emergency rating of 123 MVA) | 498133.0422 | 39.15% | 1272528.6 | 0.05631
GEN-2020-012 | 04 - Southeast | TBD | ERIS | Replace 1st Transformer at Snyder | Current Study | Replace transformer at Snyder to an emergency rating of 250 MVA | 1019899.5932 | 32.6% | 3128743 | 0.06727
GEN-2020-012 | 04 - Southeast | TBD | ERIS | Anadarko to Cleveland Switch 138 kV Line Rebuild | Current Study | Rebuild 11.1 miles of 138 kV from Aanadarko to Cleveland Switch (SN/SE/WN/WE: 299/353/381/421 MVA) | 1537276.8624 | 14.23% | 10800000 | 0.05525
GEN-2020-012 | 04 - Southeast | TBD | ERIS | Snyder to Tom Steed 69 kV Line Rebuild | Current Study | Rebuild 8.7 miles of Snyder to Tom Steed Tap 69 kV line to a minimum of 40 MVA (The other 6.3 miles has summer emergency ratings of 68 MVA or higher ) | 3095541.0482 | 39.15% | 7907856.3 | 0.05631
GEN-2020-016 | 04 - Southeast | NTC 220754 | ERIS | Anadarko to Gracemont 138 kV Build Circuits 2 & 3 | Contingent | Build two new 15 mile circuits from Anadarko to Gracemont 138 kV with SN/SE ratings of 478 MVA | 0 | 29.39% | 10984522.6317 | 0.03867
GEN-2020-015 | 04 - Southeast | 156914 | ERIS | Johnston County 345 kV Substation GEN-2020-015 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-015 (104/Solar), into the Point of Interconnection (POI) at Johnston County 345 kV Substation | 4312689 | 100% | 4312689 | 1
GEN-2020-015 | 04 - Southeast | 156913 | ERIS | Johnston County 345 kV Substation GEN-2020-015 Interconnection (Non-shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-015 (104/Solar), into the Point of Interconnection (POI) at Johnston County 345 kV Substation | 5043342 | 100% | 5043342 | 1
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Uniroyal to Ardmore West 138 kV Line Rebuild | Current Study | Rebuild Ardmore West to Uniroyal 0.57 mile 138 kV line to a minimum of 280 MVA | 20168.0641 | 3.67% | 549570.63 | 0.01489
GEN-2020-015 | 04 - Southeast | TBD | NRIS | Rebuild the TUCO_INT 7 to CRAWFISH_DR 345kV line 2 | Current Study | Rebuild the existing TUCO_INT 7 to CRAWFISH_DR 345 kV line(1.53 miles) to a minimum ratings of 1250 MVA | 56908.896 | 3.25% | 1750999.32 | 0.02157
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Wind Mill Creek Tap to Six Mile Creek Tap 138 kV Line Rebuild | Current Study | Rebuild Wind Mill Creek Tap to Six Mile Creek Tap 0.55 mile 138 kV line to a minimum of 230 MVA | 143466.412 | 27.05% | 530287.45 | 0.09224
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Carter County to Ardmore West 138 kV Line Rebuild | Current Study | Rebuild Ardmore West to Carter County 4.06 mile 138 kV line to a minimum of 270 MVA | 143653.2285 | 3.67% | 3914485.54 | 0.01489
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Sunnyside to Uniroyal 138 kV Line Rebuild | Current Study | Rebuild Sunnyside to Uniroyal 5.58 miles 138 kV line to a minimum of 310 MVA | 197434.7327 | 3.67% | 5380007.22 | 0.01489
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Build 3rd Transformer at Tuco | Current Study | Build 3rd 345/138 kV Transformer to an emergency rating of 675 MVA | 380412.5438 | 4.582% | 8302968 | 0.01423
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Line Rebuild | Current Study | Rebuild 12.08 miles from Welsh to Wilkes 345 kV line to a minimum of 1040 MVA (The remaining 18.55 miles doesn't get overloaded) | 646852.2016 | 4.679% | 13824883.52 | 0.04081
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Johnson County to Six Mile Creek Tap 138 kV Line Rebuild | Current Study | Rebuild Six Mile Creek Tap to Johnson County 6.08 mile 138 kV line to a minimum of 240 MVA | 1585955.9721 | 27.05% | 5862086.72 | 0.09224
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Build 2nd Transformer at Johnson County | Current Study | Build 2nd 345/138 kV Transformer to a minimum of 580 MVA | 2202342.9515 | 26.52% | 8302968 | 0.09808
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Wind Mill Creek Tap to Arbuckle 138 kV Line Rebuild | Current Study | Rebuild Arbuckle to Wind Mill Creek Tap 13.16 mile 138 kV line to a minimum of 230 MVA | 2612674.779 | 20.59% | 12688332.44 | 0.09224
GEN-2020-015 | 04 - Southeast | TBD | NRIS | Rebuild the RUSSET-4 to GLASSES4 138kV line 1 | Current Study | Rebuild the existing RUSSET-4 to GLASSES4 138 kV line(8.33 miles) to a minimum ratings of 180 MVA | 9600000 | 100% | 9600000 | 0.01262
GEN-2020-074 | 04 - Southeast | 112443 | NRIS | Russett - South Brown 138 kV Ckt 1 Rebuild | Contingent | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 0 | 24.51% | 10267391 | 0.02558
GEN-2020-016 | 04 - Southeast | 156964 | ERIS | Snyder SW-Cache 138 kV line GEN-2020-016 Interconnection (Non-shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-016 (202/Wind), into the Point of Interconnection (POI) at Snyder SW-Cache 138 kV line | 5000000 | 100% | 5000000 | 1
GEN-2020-016 | 04 - Southeast | 156965 | ERIS | Snyder SW-Cache 138 kV line GEN-2020-016 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-016 (202/Wind), into the Point of Interconnection (POI) at Snyder SW-Cache 138 kV line | 500000 | 100% | 500000 | 1
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Replace 1st Transformer at Grandfield | Current Study | Replace transformer at Grandfield to an emergency rating of 112 MVA | 500000 | 100% | 500000 | 0.10892
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Build 3rd Transformer at Tuco | Current Study | Build 3rd 345/138 kV Transformer to an emergency rating of 675 MVA | 730570.3736 | 8.799% | 8302968 | 0.01407
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Roosevelt Tap to Hobart City 69 kV Line Rebuild | Current Study | Rebuild 1.4 miles of the Hobart City to Roosevelt Tap 69 kV line, near Hobart City to a minimum of 50 MVA (The other 8.6 miles closest to Roosevelt Tap has a summer emergency rating of 123 MVA) | 774395.5578 | 60.85% | 1272528.6 | 0.04897
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Replace 1st Transformer at Snyder | Current Study | Replace transformer at Snyder to an emergency rating of 250 MVA | 2108843.4068 | 67.4% | 3128743 | 0.07781
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Cache Junction to G20-016-TAP 138 kV Line Rebuild | Current Study | Rebuild a total of 18.55 miles of 138 kV line from Cache Junction to Snyder (SN/SE/WN/WE: 241/283/287/287 MVA) | 2758000 | 100% | 2758000 | 0.47723
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Anadarko to Cleveland Switch 138 kV Line Rebuild | Current Study | Rebuild 11.1 miles of 138 kV from Aanadarko to Cleveland Switch (SN/SE/WN/WE: 299/353/381/421 MVA) | 3485177.1 | 32.27% | 10800000 | 0.07007
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Build 2nd Transformer at Gracemont | Current Study | Build 2nd 345/138 kV Transformer to a minimum of 520 MVA | 3753540.2147 | 45.21% | 8302968 | 0.11831
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Walters to Walters Junction 69 kV Line Rebuild | Current Study | Rebuild 5.13 miles of 69 kV from Walters to Walters Junction to a minimum of 60 MVA | 4662908.37 | 100% | 4662908.37 | 0.04276
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Snyder to Tom Steed 69 kV Line Rebuild | Current Study | Rebuild 8.7 miles of Snyder to Tom Steed Tap 69 kV line to a minimum of 40 MVA (The other 6.3 miles has summer emergency ratings of 68 MVA or higher ) | 4812315.2518 | 60.85% | 7907856.3 | 0.04897
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Snyder to G20-016-TAP 138 kV Line Rebuild | Current Study | Rebuild a total of 18.55 miles of 138 kV line from Cache Junction to Snyder (SN/SE/WN/WE: 241/283/287/287 MVA) | 10227000 | 100% | 10227000 | 0.52277
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Anadarko to Cherry Road 138 kV Line Rebuild | Current Study | Rebuild 25.15 miles of 138 kV from Aanadarko to Cherry Road (SN/SE/WN/WE: 241/283/306/338 MVA) | 17605000 | 100% | 17605000 | 0.36241
GEN-2020-020 | 04 - Southeast | 156974 | ERIS | Tap the 345 kV Northwest Texarkana - Valliant line GEN-2020-020 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-020 (201.6/Hybrid), into the Point of Interconnection (POI) at Tap the 345 kV Northwest Texarkana - Valliant line | 3250000 | 100% | 3250000 | 1
GEN-2020-020 | 04 - Southeast | 156993 | ERIS | Tap the 345 kV Northwest Texarkana - Valliant line GEN-2020-020 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-020 (201.6/Hybrid), into the Point of Interconnection (POI) at Tap the 345 kV Northwest Texarkana - Valliant line | 16950000 | 100% | 16950000 | 1
GEN-2020-020 | 04 - Southeast | TBD | ERIS | Build 2nd Transformer at Johnson County | Current Study | Build 2nd 345/138 kV Transformer to a minimum of 580 MVA | 488376.2513 | 5.882% | 8302968 | 0.01122
GEN-2020-020 | 04 - Southeast | TBD | ERIS | Wind Mill Creek Tap to Arbuckle 138 kV Line Rebuild | Current Study | Rebuild Arbuckle to Wind Mill Creek Tap 13.16 mile 138 kV line to a minimum of 230 MVA | 1347952.9812 | 10.62% | 12688332.44 | 0.02455
GEN-2020-020 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Line Rebuild | Current Study | Rebuild 12.08 miles from Welsh to Wilkes 345 kV line to a minimum of 1040 MVA (The remaining 18.55 miles doesn't get overloaded) | 2655584.7584 | 19.21% | 13824883.52 | 0.08643
GEN-2020-023 | 04 - Southeast | 156991 | ERIS | Woodring 345 KV Station GEN-2020-023 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-023 (202/Battery/Storage), into the Point of Interconnection (POI) at Woodring 345 KV Station | 4116657 | 100% | 4116657 | 1
GEN-2020-023 | 04 - Southeast | 156990 | ERIS | Woodring 345 KV Station GEN-2020-023 Interconnection (Non-shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-023 (202/Battery/Storage), into the Point of Interconnection (POI) at Woodring 345 KV Station | 4814099 | 100% | 4814099 | 1
GEN-2020-023 | 04 - Southeast | TBD | ERIS | Build 2nd Transformer at Woodring | Current Study | Build 2nd 345/138 kV Transformer to a minimum of 460 MVA | 8302968 | 100% | 8302968 | 0.08037
GEN-2020-054 | 04 - Southeast | 156929 | ERIS | Lydia 345 kV Station GEN-2020-054 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-054 (298/Solar), into the Point of Interconnection (POI) at Lydia 345 kV Station | 2850000 | 100% | 2850000 | 1
GEN-2020-054 | 04 - Southeast | 156930 | ERIS | Lydia 345kV Station GEN-2020-054 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-054, into the Point of Interconnection (POI) at Lydia 345 kV Station | 3000000 | 100% | 3000000 | 1
GEN-2020-054 | 04 - Southeast | TBD | ERIS | Build 2nd Transformer at Johnson County | Current Study | Build 2nd 345/138 kV Transformer to a minimum of 580 MVA | 593223.4871 | 7.145% | 8302968 | 0.00922
GEN-2020-054 | 04 - Southeast | TBD | ERIS | Wind Mill Creek Tap to Arbuckle 138 kV Line Rebuild | Current Study | Rebuild Arbuckle to Wind Mill Creek Tap 13.16 mile 138 kV line to a minimum of 230 MVA | 1683285.3181 | 13.27% | 12688332.44 | 0.02074
GEN-2020-054 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Line Rebuild | Current Study | Rebuild 12.08 miles from Welsh to Wilkes 345 kV line to a minimum of 1040 MVA (The remaining 18.55 miles doesn't get overloaded) | 5887899.8331 | 42.59% | 13824883.52 | 0.12964
GEN-2020-074 | 04 - Southeast | NTC 220754 | ERIS | Anadarko to Gracemont 138 kV Build Circuits 2 & 3 | Contingent | Build two new 15 mile circuits from Anadarko to Gracemont 138 kV with SN/SE ratings of 478 MVA | 0 | 2.355% | 10984522.6317 | 0.00313
GEN-2020-075 | 04 - Southeast | NTC 220754 | ERIS | Anadarko to Gracemont 138 kV Build Circuits 2 & 3 | Contingent | Build two new 15 mile circuits from Anadarko to Gracemont 138 kV with SN/SE ratings of 478 MVA | 0 | 9.195% | 10984522.6317 | 0.01222
GEN-2020-074 | 04 - Southeast | 156920 | ERIS | Lawton to Sunnyside 345 kV Substation GEN-2020-074 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-074 (200/Battery/Storage), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Substation (Sharing a GEN Tie line with GEN-2020-085) | 3250000 | 100% | 3250000 | 1
GEN-2020-074 | 04 - Southeast | 156921 | ERIS | Lawton to Sunnyside 345kV Line GEN-2020-074, GEN-2020-085 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-074, GEN-2020-085 (200/Battery/Storage, 500/Solar), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Substation (Sharing a GEN Tie line with GEN-2020-085) | 5728571.4286 | 28.57% | 20050000 | 1
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Wind Mill Creek Tap to Six Mile Creek Tap 138 kV Line Rebuild | Current Study | Rebuild Wind Mill Creek Tap to Six Mile Creek Tap 0.55 mile 138 kV line to a minimum of 230 MVA | 110520.2966 | 20.84% | 530287.45 | 0.03695
GEN-2020-074 | 04 - Southeast | TBD | NRIS | Rebuild the DUNCAN-4 to DUNCHERTP4 138kV line 1 | Current Study | Rebuild the existing DUNCAN-4 to DUNCHERTP4 138 kV line(1.6 miles) to a minimum ratings of 135 MVA | 122457.2572 | 7.938% | 1542654.4 | 0.01364
GEN-2020-074 | 04 - Southeast | TBD | NRIS | Rebuild the TUCO_INT 7 to CRAWFISH_DR 345kV line 2 | Current Study | Rebuild the existing TUCO_INT 7 to CRAWFISH_DR 345 kV line(1.53 miles) to a minimum ratings of 1250 MVA | 137548.6048 | 7.855% | 1750999.32 | 0.02711
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Uniroyal to Ardmore West 138 kV Line Rebuild | Current Study | Rebuild Ardmore West to Uniroyal 0.57 mile 138 kV line to a minimum of 280 MVA | 151257.876 | 27.52% | 549570.63 | 0.05807
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Build 2nd Transformer at Gracemont | Current Study | Build 2nd 345/138 kV Transformer to a minimum of 520 MVA | 210461.6872 | 2.535% | 8302968 | 0.0067
GEN-2020-074 | 04 - Southeast | TBD | NRIS | Rebuild the D.E.S.-4 to DUNCHERTP4 138kV line 1 | Current Study | Rebuild the existing D.E.S.-4 to DUNCHERTP4 138 kV line(3.53 miles) to a minimum ratings of 130 MVA | 270171.3237 | 7.938% | 3403481.27 | 0.01364
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild | Current Study | Rebuild 3.9 miles of 138 kV from Duncan to Duncan Bois D' Arc. Upgrade RCTL at Duncan | 271675.6152 | 7.225% | 3760220.1 | 0.0142
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Carter County to Chickasaw 138 kV Line Rebuild | Current Study | Rebuild Carter County to Chickasaw 2.73 mile 138 kV line to a minimum of 230 MVA | 752044.02 | 28.57% | 2632154.07 | 0.02274
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Build 3rd Transformer at Tuco | Current Study | Build 3rd 345/138 kV Transformer to an emergency rating of 675 MVA | 911497.1623 | 10.98% | 8302968 | 0.01773
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Carter County to Ardmore West 138 kV Line Rebuild | Current Study | Rebuild Ardmore West to Carter County 4.06 mile 138 kV line to a minimum of 270 MVA | 1077380.6604 | 27.52% | 3914485.54 | 0.05807
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Line Rebuild | Current Study | Rebuild 12.08 miles from Welsh to Wilkes 345 kV line to a minimum of 1040 MVA (The remaining 18.55 miles doesn't get overloaded) | 1197005.1627 | 8.658% | 13824883.52 | 0.03927
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Johnson County to Six Mile Creek Tap 138 kV Line Rebuild | Current Study | Rebuild Six Mile Creek Tap to Johnson County 6.08 mile 138 kV line to a minimum of 240 MVA | 1221751.6422 | 20.84% | 5862086.72 | 0.03695
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Comanche Tap to Duncan Bois D' Arc 138 kV Line Rebuild | Current Study | Rebuild 17.69 miles of 138 kV from Comanche Tap to Duncan Bois D' Arc | 1232292.7266 | 7.225% | 17055972.71 | 0.0142
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Build 2nd Transformer at Johnson County | Current Study | Build 2nd 345/138 kV Transformer to a minimum of 580 MVA | 1348137.0574 | 16.24% | 8302968 | 0.03122
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Sunnyside to Uniroyal 138 kV Line Rebuild | Current Study | Rebuild Sunnyside to Uniroyal 5.58 miles 138 kV line to a minimum of 310 MVA | 1480734.9964 | 27.52% | 5380007.22 | 0.05807
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Ratliff to Carter County 138 kV Line Rebuild | Current Study | Rebuild Ratliff to Carter County 7.22 mile 138 kV line to a minimum of 190 MVA | 1988922.28 | 28.57% | 6961227.98 | 0.03239
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Wind Mill Creek Tap to Arbuckle 138 kV Line Rebuild | Current Study | Rebuild Arbuckle to Wind Mill Creek Tap 13.16 mile 138 kV line to a minimum of 230 MVA | 2012691.2462 | 15.86% | 12688332.44 | 0.03695
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Replace Sunnyside Transformer (CKT ID 3) | Current Study | Replace the transformer with circuit ID 3 at Sunnyside to an emergency rating of 380 MVA | 2372276.5714 | 28.57% | 8302968 | 0.06564
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Current Study | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap (on the line to Terry Road) to a minimum of 1760 MVA | 4283490.4 | 28.57% | 14992216.4 | 0.58241
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Terry Road to G17-171-TAP 345 kV Line Rebuild | Current Study | Rebuild 13.91 miles of 345 kV from Terry Road to G17-171-TAP to a minimum of 1480 MVA | 4548347.44 | 28.57% | 15919216.04 | 0.41759
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Lawton Eastside to G17-171-TAP 345 kV Line Rebuild | Current Study | Rebuild 14.4 miles of 345 kV Lawton Eastside to G17-171-TAP 1 to a minimum of 1730 MVA | 4708569.6 | 28.57% | 16479993.6 | 0.41759
GEN-2020-085 | 04 - Southeast | 112443 | NRIS | Russett - South Brown 138 kV Ckt 1 Rebuild | Contingent | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 0 | 61.27% | 10267391 | 0.02558
GEN-2020-075 | 04 - Southeast | 156888 | ERIS | Cimmarron to Lawton 345 kV Line GEN-2020-075 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-075 (200/Battery/Storage), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | 3250000 | 100% | 3250000 | 1
GEN-2020-075 | 04 - Southeast | 156890 | ERIS | Cimmarron to Lawton 345kV Line GEN-2020-075, GEN-2020-087 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-075, GEN-2020-087 (200/Battery/Storage and 500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | 5728571.4286 | 28.57% | 20050000 | 1
GEN-2020-075 | 04 - Southeast | TBD | NRIS | Rebuild the DUNCAN-4 to DUNCHERTP4 138kV line 1 | Current Study | Rebuild the existing DUNCAN-4 to DUNCHERTP4 138 kV line(1.6 miles) to a minimum ratings of 135 MVA | 189431.6809 | 12.28% | 1542654.4 | 0.0211
GEN-2020-075 | 04 - Southeast | TBD | NRIS | Rebuild the TUCO_INT 7 to CRAWFISH_DR 345kV line 2 | Current Study | Rebuild the existing TUCO_INT 7 to CRAWFISH_DR 345 kV line(1.53 miles) to a minimum ratings of 1250 MVA | 206246.8013 | 11.78% | 1750999.32 | 0.04065
GEN-2020-075 | 04 - Southeast | TBD | NRIS | Rebuild the D.E.S.-4 to OMDUNE-4 138kV line 1 | Current Study | Rebuild the existing D.E.S.-4 to OMDUNE-4 138 kV line(1.26 miles) to a minimum ratings of 125 MVA | 206569.1459 | 17% | 1214840 | 0.0211
GEN-2020-075 | 04 - Southeast | TBD | NRIS | Rebuild the D.E.S.-4 to DUNCHERTP4 138kV line 1 | Current Study | Rebuild the existing D.E.S.-4 to DUNCHERTP4 138 kV line(3.53 miles) to a minimum ratings of 130 MVA | 417933.646 | 12.28% | 3403481.27 | 0.0211
GEN-2020-075 | 04 - Southeast | TBD | ERIS | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild | Current Study | Rebuild 3.9 miles of 138 kV from Duncan to Duncan Bois D' Arc. Upgrade RCTL at Duncan | 528810.8454 | 14.06% | 3760220.1 | 0.02764
GEN-2020-075 | 04 - Southeast | TBD | ERIS | Build 2nd Transformer at Gracemont | Current Study | Build 2nd 345/138 kV Transformer to a minimum of 520 MVA | 1089374.8229 | 13.12% | 8302968 | 0.03468
GEN-2020-075 | 04 - Southeast | TBD | ERIS | Build 3rd Transformer at Tuco | Current Study | Build 3rd 345/138 kV Transformer to an emergency rating of 675 MVA | 1143355.7185 | 13.77% | 8302968 | 0.02224
GEN-2020-075 | 04 - Southeast | TBD | ERIS | Anadarko to Cleveland Switch 138 kV Line Rebuild | Current Study | Rebuild 11.1 miles of 138 kV from Aanadarko to Cleveland Switch (SN/SE/WN/WE: 299/353/381/421 MVA) | 1650727.4393 | 15.28% | 10800000 | 0.03352
GEN-2020-075 | 04 - Southeast | TBD | ERIS | Lawton Eastside to G20-075-TAP 345 kV Line Rebuild | Current Study | Rebuild 6.9 miles of 345 kV from Lawton Eastside to G20-075-TAP to a minimum of 1200 MVA (Update line length in model to 6.9 miles) | 2256189.6 | 28.57% | 7896663.6 | 0.49016
GEN-2020-075 | 04 - Southeast | TBD | ERIS | Comanche Tap to Duncan Bois D' Arc 138 kV Line Rebuild | Current Study | Rebuild 17.69 miles of 138 kV from Comanche Tap to Duncan Bois D' Arc | 2398631.7579 | 14.06% | 17055972.71 | 0.02764
GEN-2020-081 | 04 - Southeast | TBD | ERIS | Build 2nd Transformer at Johnson County | Current Study | Build 2nd 345/138 kV Transformer to a minimum of 580 MVA | 300545.6092 | 3.62% | 8302968 | 0.00696
GEN-2020-081 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Line Rebuild | Current Study | Rebuild 12.08 miles from Welsh to Wilkes 345 kV line to a minimum of 1040 MVA (The remaining 18.55 miles doesn't get overloaded) | 445028.6574 | 3.219% | 13824883.52 | 0.0146
GEN-2020-081 | 04 - Southeast | 156976 | ERIS | Tenaska Switching Substation 345kV GEN-2020-081 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-081 (200/Battery/Storage), into the Point of Interconnection (POI) at Tenaska Switching Substation 345kV | 3150000 | 100% | 3150000 | 1
GEN-2020-081 | 04 - Southeast | 156975 | ERIS | Tenaska Switching Substation 345kV GEN-2020-081 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-081 (200/Battery/Storage), into the Point of Interconnection (POI) at Tenaska Switching Substation 345kV | 3400000 | 100% | 3400000 | 1
GEN-2020-085 | 04 - Southeast | NTC 220754 | ERIS | Anadarko to Gracemont 138 kV Build Circuits 2 & 3 | Contingent | Build two new 15 mile circuits from Anadarko to Gracemont 138 kV with SN/SE ratings of 478 MVA | 0 | 5.888% | 10984522.6317 | 0.00313
GEN-2020-087 | 04 - Southeast | NTC 220754 | ERIS | Anadarko to Gracemont 138 kV Build Circuits 2 & 3 | Contingent | Build two new 15 mile circuits from Anadarko to Gracemont 138 kV with SN/SE ratings of 478 MVA | 0 | 22.99% | 10984522.6317 | 0.01222
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Wind Mill Creek Tap to Six Mile Creek Tap 138 kV Line Rebuild | Current Study | Rebuild Wind Mill Creek Tap to Six Mile Creek Tap 0.55 mile 138 kV line to a minimum of 230 MVA | 276300.7415 | 52.1% | 530287.45 | 0.03695
GEN-2020-085 | 04 - Southeast | TBD | NRIS | Rebuild the DUNCAN-4 to DUNCHERTP4 138kV line 1 | Current Study | Rebuild the existing DUNCAN-4 to DUNCHERTP4 138 kV line(1.6 miles) to a minimum ratings of 135 MVA | 306143.143 | 19.85% | 1542654.4 | 0.01364
GEN-2020-085 | 04 - Southeast | TBD | NRIS | Rebuild the TUCO_INT 7 to CRAWFISH_DR 345kV line 2 | Current Study | Rebuild the existing TUCO_INT 7 to CRAWFISH_DR 345 kV line(1.53 miles) to a minimum ratings of 1250 MVA | 343871.512 | 19.64% | 1750999.32 | 0.02711
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Uniroyal to Ardmore West 138 kV Line Rebuild | Current Study | Rebuild Ardmore West to Uniroyal 0.57 mile 138 kV line to a minimum of 280 MVA | 378144.6899 | 68.81% | 549570.63 | 0.05807
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Build 2nd Transformer at Gracemont | Current Study | Build 2nd 345/138 kV Transformer to a minimum of 520 MVA | 526154.2181 | 6.337% | 8302968 | 0.0067
GEN-2020-085 | 04 - Southeast | TBD | NRIS | Rebuild the D.E.S.-4 to DUNCHERTP4 138kV line 1 | Current Study | Rebuild the existing D.E.S.-4 to DUNCHERTP4 138 kV line(3.53 miles) to a minimum ratings of 130 MVA | 675428.3093 | 19.85% | 3403481.27 | 0.01364
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild | Current Study | Rebuild 3.9 miles of 138 kV from Duncan to Duncan Bois D' Arc. Upgrade RCTL at Duncan | 679189.0381 | 18.06% | 3760220.1 | 0.0142
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Carter County to Chickasaw 138 kV Line Rebuild | Current Study | Rebuild Carter County to Chickasaw 2.73 mile 138 kV line to a minimum of 230 MVA | 1880110.05 | 71.43% | 2632154.07 | 0.02274
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Build 3rd Transformer at Tuco | Current Study | Build 3rd 345/138 kV Transformer to an emergency rating of 675 MVA | 2278742.9057 | 27.44% | 8302968 | 0.01773
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Carter County to Ardmore West 138 kV Line Rebuild | Current Study | Rebuild Ardmore West to Carter County 4.06 mile 138 kV line to a minimum of 270 MVA | 2693451.6511 | 68.81% | 3914485.54 | 0.05807
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Line Rebuild | Current Study | Rebuild 12.08 miles from Welsh to Wilkes 345 kV line to a minimum of 1040 MVA (The remaining 18.55 miles doesn't get overloaded) | 2992512.9068 | 21.65% | 13824883.52 | 0.03927
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Johnson County to Six Mile Creek Tap 138 kV Line Rebuild | Current Study | Rebuild Six Mile Creek Tap to Johnson County 6.08 mile 138 kV line to a minimum of 240 MVA | 3054379.1056 | 52.1% | 5862086.72 | 0.03695
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Comanche Tap to Duncan Bois D' Arc 138 kV Line Rebuild | Current Study | Rebuild 17.69 miles of 138 kV from Comanche Tap to Duncan Bois D' Arc | 3080731.8164 | 18.06% | 17055972.71 | 0.0142
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Build 2nd Transformer at Johnson County | Current Study | Build 2nd 345/138 kV Transformer to a minimum of 580 MVA | 3370342.6435 | 40.59% | 8302968 | 0.03122
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Sunnyside to Uniroyal 138 kV Line Rebuild | Current Study | Rebuild Sunnyside to Uniroyal 5.58 miles 138 kV line to a minimum of 310 MVA | 3701837.4909 | 68.81% | 5380007.22 | 0.05807
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Ratliff to Carter County 138 kV Line Rebuild | Current Study | Rebuild Ratliff to Carter County 7.22 mile 138 kV line to a minimum of 190 MVA | 4972305.7 | 71.43% | 6961227.98 | 0.03239
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Wind Mill Creek Tap to Arbuckle 138 kV Line Rebuild | Current Study | Rebuild Arbuckle to Wind Mill Creek Tap 13.16 mile 138 kV line to a minimum of 230 MVA | 5031728.1155 | 39.66% | 12688332.44 | 0.03695
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Replace Sunnyside Transformer (CKT ID 3) | Current Study | Replace the transformer with circuit ID 3 at Sunnyside to an emergency rating of 380 MVA | 5930691.4286 | 71.43% | 8302968 | 0.06564
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Current Study | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap (on the line to Terry Road) to a minimum of 1760 MVA | 10708726 | 71.43% | 14992216.4 | 0.58241
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Terry Road to G17-171-TAP 345 kV Line Rebuild | Current Study | Rebuild 13.91 miles of 345 kV from Terry Road to G17-171-TAP to a minimum of 1480 MVA | 11370868.6 | 71.43% | 15919216.04 | 0.41759
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Lawton Eastside to G17-171-TAP 345 kV Line Rebuild | Current Study | Rebuild 14.4 miles of 345 kV Lawton Eastside to G17-171-TAP 1 to a minimum of 1730 MVA | 11771424 | 71.43% | 16479993.6 | 0.41759
GEN-2020-085 | 04 - Southeast | 156919 | ERIS | Lawton to Sunnyside 345 kV Line GEN-2020-085 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-085 (500/Solar), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Line (Sharing a GEN Tie line with GEN-2020-074) | 3250000 | 100% | 3250000 | 1
GEN-2020-085 | 04 - Southeast | 156921 | ERIS | Lawton to Sunnyside 345kV Line GEN-2020-074, GEN-2020-085 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-074, GEN-2020-085 (200/Battery/Storage, 500/Solar), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Substation (Sharing a GEN Tie line with GEN-2020-074) | 14321428.5714 | 71.43% | 20050000 | 1
GEN-2020-065 | 05 - Southwest | NTC 220754 | ERIS | Anadarko to Gracemont 138 kV Build Circuits 2 & 3 | Contingent | Build two new 15 mile circuits from Anadarko to Gracemont 138 kV with SN/SE ratings of 478 MVA | 0 | 30.19% | 10984522.6317 | 0.008
GEN-2020-087 | 04 - Southeast | TBD | NRIS | Rebuild the DUNCAN-4 to DUNCHERTP4 138kV line 1 | Current Study | Rebuild the existing DUNCAN-4 to DUNCHERTP4 138 kV line(1.6 miles) to a minimum ratings of 135 MVA | 473579.2022 | 30.7% | 1542654.4 | 0.0211
GEN-2020-087 | 04 - Southeast | TBD | NRIS | Rebuild the TUCO_INT 7 to CRAWFISH_DR 345kV line 2 | Current Study | Rebuild the existing TUCO_INT 7 to CRAWFISH_DR 345 kV line(1.53 miles) to a minimum ratings of 1250 MVA | 515617.0034 | 29.45% | 1750999.32 | 0.04065
GEN-2020-087 | 04 - Southeast | TBD | NRIS | Rebuild the D.E.S.-4 to OMDUNE-4 138kV line 1 | Current Study | Rebuild the existing D.E.S.-4 to OMDUNE-4 138 kV line(1.26 miles) to a minimum ratings of 125 MVA | 516422.8647 | 42.51% | 1214840 | 0.0211
GEN-2020-087 | 04 - Southeast | TBD | NRIS | Rebuild the D.E.S.-4 to DUNCHERTP4 138kV line 1 | Current Study | Rebuild the existing D.E.S.-4 to DUNCHERTP4 138 kV line(3.53 miles) to a minimum ratings of 130 MVA | 1044834.1149 | 30.7% | 3403481.27 | 0.0211
GEN-2020-087 | 04 - Southeast | TBD | ERIS | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild | Current Study | Rebuild 3.9 miles of 138 kV from Duncan to Duncan Bois D' Arc. Upgrade RCTL at Duncan | 1322027.1136 | 35.16% | 3760220.1 | 0.02764
GEN-2020-087 | 04 - Southeast | TBD | ERIS | Build 2nd Transformer at Gracemont | Current Study | Build 2nd 345/138 kV Transformer to a minimum of 520 MVA | 2723437.0571 | 32.8% | 8302968 | 0.03468
GEN-2020-087 | 04 - Southeast | TBD | ERIS | Build 3rd Transformer at Tuco | Current Study | Build 3rd 345/138 kV Transformer to an emergency rating of 675 MVA | 2858389.2962 | 34.43% | 8302968 | 0.02224
GEN-2020-087 | 04 - Southeast | TBD | ERIS | Anadarko to Cleveland Switch 138 kV Line Rebuild | Current Study | Rebuild 11.1 miles of 138 kV from Aanadarko to Cleveland Switch (SN/SE/WN/WE: 299/353/381/421 MVA) | 4126818.5983 | 38.21% | 10800000 | 0.03352
GEN-2020-087 | 04 - Southeast | TBD | ERIS | Lawton Eastside to G20-075-TAP 345 kV Line Rebuild | Current Study | Rebuild 6.9 miles of 345 kV from Lawton Eastside to G20-075-TAP to a minimum of 1200 MVA (Update line length in model to 6.9 miles) | 5640474 | 71.43% | 7896663.6 | 0.49016
GEN-2020-087 | 04 - Southeast | TBD | ERIS | Comanche Tap to Duncan Bois D' Arc 138 kV Line Rebuild | Current Study | Rebuild 17.69 miles of 138 kV from Comanche Tap to Duncan Bois D' Arc | 5996579.3948 | 35.16% | 17055972.71 | 0.02764
GEN-2020-087 | 04 - Southeast | 156889 | ERIS | Cimmarron to Lawton 345 kV Line GEN-2020-087 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-087 (500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | 3250000 | 100% | 3250000 | 1
GEN-2020-087 | 04 - Southeast | 156890 | ERIS | Cimmarron to Lawton 345kV Line GEN-2020-075, GEN-2020-087 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-075, GEN-2020-087 (200/Battery/Storage and 500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | 14321428.5714 | 71.43% | 20050000 | 1
GEN-2020-092 | 04 - Southeast | 156948 | ERIS | Pryor Junction - Midwest Carbide 138kV line GEN-2020-092 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-092 (100/Solar), into the Point of Interconnection (POI) at Pryor Junction - Midwest Carbide 138kV line | 1800000 | 100% | 1800000 | 1
GEN-2020-092 | 04 - Southeast | 156947 | ERIS | Pryor Junction - Midwest Carbide 138kV line GEN-2020-092 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-092 (100/Solar), into the Point of Interconnection (POI) at Pryor Junction - Midwest Carbide 138kV line | 8850000 | 100% | 8850000 | 1
GEN-2020-009 | 05 - Southwest | 156918 | ERIS | Lawton East Side to Oklaunion 345kV GEN-2020-009 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-009 (300/Hybrid), into the Point of Interconnection (POI) at Lawton East Side to Oklaunion 345kV | 3250000 | 100% | 3250000 | 1
GEN-2020-009 | 05 - Southwest | 156917 | ERIS | Lawton East Side to Oklaunion 345kV GEN-2020-009 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-009 (300/Hybrid), into the Point of Interconnection (POI) at Lawton East Side to Oklaunion 345kV | 16950000 | 100% | 16950000 | 1
GEN-2020-009 | 05 - Southwest | TBD | NRIS | Rebuild the DUNCAN-4 to DUNCHERTP4 138kV line 1 | Current Study | Rebuild the existing DUNCAN-4 to DUNCHERTP4 138 kV line(1.6 miles) to a minimum ratings of 135 MVA | 334782.3403 | 21.7% | 1542654.4 | 0.02486
GEN-2020-009 | 05 - Southwest | TBD | NRIS | Rebuild the D.E.S.-4 to OMDUNE-4 138kV line 1 | Current Study | Rebuild the existing D.E.S.-4 to OMDUNE-4 138 kV line(1.26 miles) to a minimum ratings of 125 MVA | 365069.3578 | 30.05% | 1214840 | 0.02486
GEN-2020-009 | 05 - Southwest | TBD | NRIS | Rebuild the TUCO_INT 7 to CRAWFISH_DR 345kV line 2 | Current Study | Rebuild the existing TUCO_INT 7 to CRAWFISH_DR 345 kV line(1.53 miles) to a minimum ratings of 1250 MVA | 490806.5025 | 28.03% | 1750999.32 | 0.06449
GEN-2020-009 | 05 - Southwest | TBD | NRIS | Rebuild the D.E.S.-4 to DUNCHERTP4 138kV line 1 | Current Study | Rebuild the existing D.E.S.-4 to DUNCHERTP4 138 kV line(3.53 miles) to a minimum ratings of 130 MVA | 738613.5383 | 21.7% | 3403481.27 | 0.02486
GEN-2020-009 | 05 - Southwest | TBD | ERIS | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild | Current Study | Rebuild 3.9 miles of 138 kV from Duncan to Duncan Bois D' Arc. Upgrade RCTL at Duncan | 958517.4876 | 25.49% | 3760220.1 | 0.0334
GEN-2020-009 | 05 - Southwest | TBD | ERIS | Comanche Tap to Duncan Bois D' Arc 138 kV Line Rebuild | Current Study | Rebuild 17.69 miles of 138 kV from Comanche Tap to Duncan Bois D' Arc | 4347737.0142 | 25.49% | 17055972.71 | 0.0334
GEN-2020-017 | 05 - Southwest | 156875 | ERIS | 230kV Lamb County Interchange GEN-2020-017 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-017 (74.88/Solar), into the Point of Interconnection (POI) at 230kV Lamb County Interchange | 10594150 | 100% | 10594150 | 1
GEN-2020-017 | 05 - Southwest | 156876 | ERIS | 230kV Lamb County Interchange GEN-2020-017 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-017 (74.88/Solar), into the Point of Interconnection (POI) at 230kV Lamb County Interchange | 1017923 | 100% | 1017923 | 1
GEN-2020-059 | 05 - Southwest | 156982 | ERIS | Tuco-Yoakum-Hobbs 345 kV GEN-2020-059 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-059 (250/Hybrid), into the Point of Interconnection (POI) at Tuco-Yoakum-Hobbs 345 kV | 15573312 | 100% | 15573312 | 1
GEN-2020-059 | 05 - Southwest | 156983 | ERIS | Tuco-Yoakum-Hobbs 345 kV GEN-2020-059 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-059 (250/Hybrid), into the Point of Interconnection (POI) at Tuco-Yoakum-Hobbs 345 kV | 1381735 | 100% | 1381735 | 1
GEN-2020-060 | 05 - Southwest | 156926 | ERIS | Lubbock East Substation 230 kV GEN-2020-060 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-060 (200/Battery/Storage), into the Point of Interconnection (POI) at Lubbock East Substation 230 kV | 9772056 | 100% | 9772056 | 1
GEN-2020-060 | 05 - Southwest | 156927 | ERIS | Lubbock East Substation 230 kV GEN-2020-060 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-060 (200/Battery/Storage), into the Point of Interconnection (POI) at Lubbock East Substation 230 kV | 1947926 | 100% | 1947926 | 1
GEN-2020-062 | 05 - Southwest | 156937 | ERIS | OASIS 230kV Substation GEN-2020-062 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-062 (256/Solar), into the Point of Interconnection (POI) at OASIS 230kV Substation | 9895590 | 100% | 9895590 | 1
GEN-2020-062 | 05 - Southwest | 156938 | ERIS | OASIS 230kV Substation GEN-2020-062 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-062 (256/Solar), into the Point of Interconnection (POI) at OASIS 230kV Substation | 1852814 | 100% | 1852814 | 1
GEN-2020-001 | 02 - Nebraska | TBD | NRIS | Rebuild the MORRILL7 to GERINGT_-TS7 115kV line 1 (non-SPP) | Current Study | Rebuild the existing MORRILL7 to GERINGT_-TS7 115 kV line(24.19 miles) to a minimum ratings of 110 MVA (non-SPP) (Facility Owner to address) | 0 | 100% | 17195219.6 | 0.02354
GEN-2020-065 | 05 - Southwest | 156909 | ERIS | Hobbs-Andrews 345 kV Line GEN-2020-065 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-065 (1003/Thermal), into the Point of Interconnection (POI) at Hobbs-Andrews 345 kV Line | 30437222 | 100% | 30437222 | 1
GEN-2020-065 | 05 - Southwest | 156910 | ERIS | Hobbs-Andrews 345 kV Line GEN-2020-065 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-065 (1003/Thermal), into the Point of Interconnection (POI) at Hobbs-Andrews 345 kV Line | 1532799 | 100% | 1532799 | 1
GEN-2020-065 | 05 - Southwest | TBD | ERIS | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Current Study | Correct existing Lidar clearance issues on Sidewinder to Andrews 345 kV line to increase the line rating to 1400MVA SN/SE. | 400000 | 100% | 400000 | 0.7427
GEN-2020-065 | 05 - Southwest | TBD | ERIS | Sidewinder to Hobbs 345 kV Lidar Clearance Correction | Current Study | Correct existing Lidar clearance issues on Sidewinder to Hobbs 345 kV line to increase the line rating to 1400MVA SN/SE. | 400000 | 100% | 400000 | 0.2763
GEN-2020-065 | 05 - Southwest | TBD | ERIS | Build New Andrews to Road Runner 345 kV Line | Current Study | Build a new 40 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | 70410000 | 100% | 70410000 | 0.2081
GEN-2020-067 | 05 - Southwest | 156979 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-067 (352.5/Wind), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | 690867 | 100% | 690867 | 1
GEN-2020-067 | 05 - Southwest | 156980 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067, GEN-2020-068 Interconnection (DISIS-2020-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-067, GEN-2020-068 (352.5/Wind and 400/Solar), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | 10162212.897 | 46.84% | 21693802 | 1
GEN-2020-068 | 05 - Southwest | 156980 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067, GEN-2020-068 Interconnection (DISIS-2020-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-067, GEN-2020-068 (352.5/Wind and 400/Solar), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | 11531589.103 | 53.16% | 21693802 | 1
GEN-2020-068 | 05 - Southwest | 156981 | ERIS | Tuco to Yoakum 345kV line GEN-2020-068 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-068 (400/Solar), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | 690867 | 100% | 690867 | 1
1274487606.39

## Upgrade Summary
Upgrade Type | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | Steady State | 01 - North | 2023 ITP | ERIS | 2023ITP PORTFOLIO - REPLACE FORT THOMPSON 345_230 KV CKT 1 AND 2 XFMR | NTC-220753 | Contingent upgrade from 2023 ITP. Replace both existing Fort Thompson 345/230 kV transformers. | WAPA | 36 | 33546913
Contingent | Steady State | 01 - North | DISIS-2018-002 & DISIS-2019-001 | ERIS | Rebuild the HOLT.CO3 to ANTELOPE 3 345kV line 1 | TBD | Contingent upgrade from DISIS 1802/1901 phase 2. Increase rating from 445 MVA to 525 MVA. Build approximately 25 miles of 345kV line from Antelope to Holt. Cost updated based on latest information available | NPPD | 36 | 70000000
Current Study | Stability | 01 - North | DISIS-2020-001 | ERIS | Build a 80 MVAR STATCOM at Bowman 230 kV Substation | TBD | 80 MVAR STATCOM required at Bowman 230 kV substation to resolve the voltage recovery issues observed in the stability study due to the reactive response of GEN-2020-006 | BEPC | 36 | 17200000
Current Study | Steady State | 01 - North | DISIS-2020-001 | ERIS | Replace the breaker at GR PRAIRIE 3 | TBD | Replace the existing breaker at GR PRAIRIE 3 with minimum ratings of 980 MVA | WAPA UGP | 36 | 566485
Current Study | Steady State | 01 - North | DISIS-2020-001 | ERIS | HOLT.CO3 to GRPRAR1-LNX3 345kV line 1 Rating Update | TBD | Correct the HOLT.CO3 to GRPRAR1-LNX3 345 kV line to minimum rating of 980 MVA per TO feedback | WAPA UGP | 0 | 0
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Lonesome Creek 115kV GEN-2020-014 Interconnection (TOIF) (BEPC) | 144258 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-014 (60.5/Thermal), into the Point of Interconnection (POI) at Lonesome Creek 115kV | BEPC | 0 | 0
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Lonesome Creek 115kV GEN-2020-014 Interconnection (Non-shared NU) (BEPC) | 144259 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-014 (60.5/Thermal), into the Point of Interconnection (POI) at Lonesome Creek 115kV | BEPC | 0 | 0
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Bowman 230kV substation GEN-2020-006 Interconnection (Non-shared NU) (BEPC) | 156886 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-006 (250/Solar), into the Point of Interconnection (POI) at Bowman 230kV substation | BEPC | 48 | 2457984
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Bowman 230kV substation GEN-2020-006 Interconnection (TOIF) (BEPC) | 156887 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-006 (250/Solar), into the Point of Interconnection (POI) at Bowman 230kV substation | BEPC | 48 | 1396145
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | LeLand Olds-Chapelle Creek 345kV line GEN-2020-021 Interconnection (Non-shared NU) (BEPC) | 156922 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-021 (235/Wind), into the Point of Interconnection (POI) at LeLand Olds-Chapelle Creek 345kV line | BEPC | 60 | 23834846
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | LeLand Olds-Chapelle Creek 345kV line GEN-2020-021 Interconnection (TOIF) (BEPC) | 156923 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-021 (235/Wind), into the Point of Interconnection (POI) at LeLand Olds-Chapelle Creek 345kV line | BEPC | 60 | 3674786
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Patent Gate Substation 345 kV GEN-2020-091 Interconnection (Non-shared NU) (BEPC) | 156941 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-091 (150/Solar), into the Point of Interconnection (POI) at Patent Gate Substation 345 kV | BEPC | 60 | 1766528
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Patent Gate Substation 345 kV GEN-2020-091 Interconnection (TOIF) (BEPC) | 156942 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-091 (150/Solar), into the Point of Interconnection (POI) at Patent Gate Substation 345 kV | BEPC | 60 | 2569702
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Fairview 115kV Substation GEN-2020-083 Interconnection (Non-shared NU) (WAPA) | 156905 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-083 (74.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation | WAPA | 58 | 6400000
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Fairview 115kV Substation GEN-2020-083 Interconnection (TOIF) (WAPA) | 156906 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-083 (74.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation | WAPA | 58 | 350000
Contingent | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Build New S1362 to S1363 161 kV Second Circuit | NTC 220723 UID 158446 | Build a second 161 kV line from S1362 to S1363 (5.44 miles) to standard rating of 558 MVA | OPPD | 36 | 5688841.92
Contingent | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Ft. Calhoun - Raun 345 kV GEN-2018-043 Interconnection (TOIF) (OPPD) | 156030 | Facilitate the interconnection of GEN-2018-043 | OPPD | 30 | 8894071
Contingent | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Ft. Calhoun - Raun 345 kV Line Tap (DISIS-2018-001) | 156031 | Facilitate the interconnection of GEN-2018-043 | OPPD | 0 | 0
Contingent | Steady State | 02 - Nebraska | DPA-2018-February-841 | NRIS | S1209 - S1231 Ckt 2 161 kV Reconductor | TBD | Reconductor 3.3 miles of S1209 - S1231 161 kV Ckt 2 | OPPD | 36 | 3647471
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Upgrade Terminals at Hays to Great Bend | TBD | Upgrade the existing terminals at S HAYS6 to GRTBEND6 230 kV line(39.2 miles) to a minimum ratings of 455 MVA | MIDW | 36 | 435000
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Replace Post Rock 345-230 kV Transformer | TBD | Replace the existing Post Rock 345-230 kV to a minimum rating of 620 MVA | MIDW | 36 | 10052968
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Rebuild the BEATRCE7 to HARBINE7 115kV line 1 | TBD | Rebuild the existing BEATRCE7 to HARBINE7 115 kV line(14.08 miles) to a minimum ratings of 142 MVA | NPPD | 36 | 10008627.2
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Rebuild the FAIRBRY7 to G20-077-TAP 115kV line 1 | TBD | Rebuild the existing FAIRBRY7 to G20-077-TAP 115 kV line(10.83 miles) to a minimum ratings of 160 MVA | NPPD | 36 | 7698397.2
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Rebuild the FAIRBRY7 to HARBINE7 115kV line 1 | TBD | Rebuild the existing FAIRBRY7 to HARBINE7 115 kV line(9.82 miles) to a minimum ratings of 155 MVA | NPPD | 36 | 6980448.8
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Rebuild the HEBRN N7 to G20-077-TAP 115kV line 1 | TBD | Rebuild the existing HEBRN N7 to G20-077-TAP 115 kV line(11.27 miles) to a minimum ratings of 155 MVA | NPPD | 36 | 8011166.8
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Rebuild the HOLDREG7 to G20-013-TAP 115kV line 1 | TBD | Rebuild the existing HOLDREG7 to G20-013-TAP 115 kV line(19 miles) to a minimum ratings of 215 MVA | NPPD | 36 | 13800000
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Rebuild the OGALALA4 to SIDNEY___TS4 230kV line 1 | TBD | Rebuild the existing OGALALA4 to SIDNEY___TS4 230 kV line(68.85 miles) to a minimum ratings of 415 MVA | NPPD | 36 | 60829594.65
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | S3451 3 Breaker Rating Update | TBD | Correct the breaker rating to 1160MVA per TO feedback | WAPA | 0 | 0
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | SIDNEY 7 to COLTON__-TS7 115kV line 1 Rating Update | TBD | Correct the line rating to 117.5MVA per TO feedback | WAPA | 0 | 0
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | NRIS | Rebuild the MORRILL7 to GERINGT_-TS7 115kV line 1 (non-SPP) | TBD | Rebuild the existing MORRILL7 to GERINGT_-TS7 115 kV line(24.19 miles) to a minimum ratings of 110 MVA (non-SPP) (Facility Owner to address) | WAPA RMR | 36 | 17195219.6
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Sidney 345 kV Substation GEN-2020-001 Interconnection (Non-shared NU) (BEPC) | 156962 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-001 (200/Solar), into the Point of Interconnection (POI) at Sidney 345 kV Substation | BEPC | 60 | 4886412
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Sidney 345 kV Substation GEN-2020-001 Interconnection (TOIF) (BEPC) | 156963 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-001 (200/Solar), into the Point of Interconnection (POI) at Sidney 345 kV Substation | BEPC | 60 | 1923401
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Postrock to Axtell 345 KV line GEN-2020-070 Interconnection (Non-shared NU) (ITCGP) | 156945 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-070 (255/Wind), into the Point of Interconnection (POI) at Postrock to Axtell 345 KV line | ITCGP | 30 | 19231292
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Postrock to Axtell 345 KV line GEN-2020-070 Interconnection (TOIF) (ITCGP) | 156946 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-070 (255/Wind), into the Point of Interconnection (POI) at Postrock to Axtell 345 KV line | ITCGP | 30 | 1207987
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Cody to Valentine 115kV line GEN-2020-069 Interconnection (Non-shared NU) (NPPD) | 156891 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-069 (52.85/Wind), into the Point of Interconnection (POI) at Cody to Valentine 115kV line | NPPD | 36 | 15400000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | North Hebron to Fairbury 115 kV GEN-2020-077 Interconnection (Non-shared NU) (NPPD) | 156935 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-077 (151.2/Wind), into the Point of Interconnection (POI) at North Hebron to Fairbury 115 kV | NPPD | 36 | 10600000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Orleans-Holdrege Substation 115kV GEN-2020-013 Interconnection (Non-shared NU) (NPPD) | 156939 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-013 (215/Hybrid), into the Point of Interconnection (POI) at Orleans-Holdrege Substation 115kV | NPPD | 36 | 9600000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Axtell-Sweetwater Substation 345kV GEN-2020-011 Interconnection (Non-shared NU) (NPPD) | 156881 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-011 (320/Hybrid), into the Point of Interconnection (POI) at Axtell-Sweetwater Substation 345kV | NPPD | 36 | 16700000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Axtell-Sweetwater Substation 345kV GEN-2020-011 Interconnection (TOIF) (NPPD) | 156882 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-011 (320/Hybrid), into the Point of Interconnection (POI) at Axtell-Sweetwater Substation 345kV | NPPD | 36 | 700000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Cody to Valentine 115kV line GEN-2020-069 Interconnection (TOIF) (NPPD) | 156892 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-069 (52.85/Wind), into the Point of Interconnection (POI) at Cody to Valentine 115kV line | NPPD | 36 | 700000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | North Hebron to Fairbury 115 kV GEN-2020-077 Interconnection (TOIF) (NPPD) | 156936 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-077 (151.2/Wind), into the Point of Interconnection (POI) at North Hebron to Fairbury 115 kV | NPPD | 36 | 700000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Orleans-Holdrege Substation 115kV GEN-2020-013 Interconnection (TOIF) (NPPD) | 156940 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-013 (215/Hybrid), into the Point of Interconnection (POI) at Orleans-Holdrege Substation 115kV | NPPD | 36 | 700000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | 6846 Substation 69 kV GEN-2020-002 Interconnection (TOIF) (OPPD) | 143682 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-002 (81/Solar), into the Point of Interconnection (POI) at 6846 Substation 69 kV | OPPD | 0 | 0
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | 6846 Substation 69 kV GEN-2020-002 Interconnection (Non-shared NU) (OPPD) | 143683 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-002 (81/Solar), into the Point of Interconnection (POI) at 6846 Substation 69 kV | OPPD | 18 | 2345838
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1226 to Substation 1237, 161kV Tap GEN-2020-078 Interconnection (TOIF) (OPPD) | 143684 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-078 (100/Solar), into the Point of Interconnection (POI) at Substation 1226 to Substation 1237, 161kV Tap | OPPD | 36 | 150000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1226 to Substation 1237, 161kV Tap GEN-2020-078 Interconnection (Non-shared NU) (OPPD) | 143685 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-078 (100/Solar), into the Point of Interconnection (POI) at Substation 1226 to Substation 1237, 161kV Tap | OPPD | 48 | 16266338
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-025 Interconnection (TOIF) (OPPD) | 156388 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025 (255/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | OPPD | 10 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-028 Interconnection (TOIF) (OPPD) | 156389 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-028 (255/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | OPPD | 10 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043 Interconnection (TOIF) (OPPD) | 156390 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-043 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | OPPD | 10 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-044 Interconnection (TOIF) (OPPD) | 156391 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-044 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | OPPD | 10 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-045 Interconnection (TOIF) (OPPD) | 156392 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-045 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | OPPD | 10 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | 156393 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | OPPD | 10 | 41063166
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043, GEN-2020-044, GEN-2020-045 Interconnection (DISIS-2020-001) (OPPD) | 156394 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-043, GEN-2020-044, GEN-2020-045 (Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | OPPD | 10 | 27418650
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Neb. City - 103rd & Rokeby 345 kV GEN-2020-094 Interconnection (Non-shared NU) (OPPD) | 156931 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-094 (250/Solar), into the Point of Interconnection (POI) at Neb. City - 103rd & Rokeby 345 kV | OPPD | 48 | 19120517
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Neb. City - 103rd & Rokeby 345 kV GEN-2020-094 Interconnection (TOIF) (OPPD) | 156932 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-094 (250/Solar), into the Point of Interconnection (POI) at Neb. City - 103rd & Rokeby 345 kV | OPPD | 36 | 17125000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Raun - Fort Calhoun 345 kV GEN-2020-084 Interconnection (Non-shared NU) (OPPD) | 156949 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-084 (350/Solar), into the Point of Interconnection (POI) at Raun - Fort Calhoun 345 kV | OPPD | 42 | 3984923
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Raun - Fort Calhoun 345 kV GEN-2020-084 Interconnection (TOIF) (OPPD) | 156950 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-084 (350/Solar), into the Point of Interconnection (POI) at Raun - Fort Calhoun 345 kV | OPPD | 36 | 1375000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-027 Interconnection (TOIF) (OPPD) | 156953 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-027 (50/Hybrid), into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | OPPD | 36 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-030 Interconnection (TOIF) (OPPD) | 156954 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-030 (50/Hybrid), into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | OPPD | 36 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-033 Interconnection (TOIF) (OPPD) | 156955 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facilities, GEN-2020-033 (50/Hybrid), into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | OPPD | 36 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-031 Interconnection (TOIF) (OPPD) | 156968 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-031 (303/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | OPPD | 36 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 3740; 345kV GEN-2020-036 Interconnection (TOIF) (OPPD) | 156969 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-038 (303/Hybrid), into the Point of Interconnection (POI) at Substation 3740; 345kV | OPPD | 36 | 150000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 3740; 345kV GEN-2020-036, GEN-2020-038 Interconnection (DISIS-2020-001) (OPPD) | 156970 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-036, GEN-2020-038 (303/Hybrid and 303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | OPPD | 36 | 7480744
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 3740; 345kV GEN-2020-038 Interconnection (TOIF) (OPPD) | 156971 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-038 (303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | OPPD | 36 | 150000
Contingent | Steady State | 03 - Central | 2019 ITP | NRIS | Blackberry - Wolf Creek 345 kV | 122598 | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | NEET | 36 | 87298154
Contingent | Steady State | 03 - Central | 2019 ITP | ERIS | Blackberry - Wolf Creek 345 kV | 122598 | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | NEET | 36 | 87298154
Contingent | Steady State | 03 - Central | 2023 ITP | ERIS | Extend Craig-West Gardner 345 kV, Clearview-Eudora 115 kV Tap,new 345/115 kV substation | TBD | Contingent upgrade from 2023 ITP. Build a new substation tapping the extention of Craig-West Gardner 345 kV and Clearview-Eudora 115 kV Tap | KCPL/WERE | 42 | 42141390
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Terminal upgrades at both ends of the line LAR382 5 to MON383 | TBD | Upgrade terminals on the LAR382 to MON383 161 kV line(15.56 miles) to achieve a minimum rating of 230 MVA. | EMDE | 36 | 250000
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Rebuild the MARMTNE5 to DAKOTA_5 161kV line 1 | TBD | Rebuild the existing MARMTNE5 to DAKOTA_5 161 kV line(10.5 miles) to a minimum ratings of 310 MVA | KCPL | 36 | 10271352
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Terminal upgrades at the line CNTRVIL5 to PAOLA 5 161kV line 1 | TBD | Upgrade terminals on the CNTRVIL5 to PAOLA 5 161 kV line(23.8 miles) to achieve a minimum rating of 285 MVA | KCPL | 36 | 50000
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Replacing the CT/Relay of West Gardner R2-3 Breaker | TBD | Replace the CT/Relay of West Gardner R2-3 Breaker on the WGARDNR5 to CEDRCRK5 161 kV line(14.6 miles) to a minimum ratings of 435 MVA | KCPL | 36 | 91147
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1 | TBD | Replace the wave trap on PECULR 7 to PHILL 7 345kV line 1(11.9 miles) to a minimum ratings of 800 MVA | KCPL | 36 | 71563
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Terminal upgrades in the NEO_SPA substation | TBD | Upgrade terminals on the NEO SPA5 to TIP292 5 161 kV line(10.6 miles) to achieve a minimum rating of 232 MVA. | EDE | 36 | 1300000
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Rebuild the CENTENL5 to PAOLA 5 161kV line 1 | TBD | Rebuild the existing CENTENL5 to PAOLA 5 161 kV line(2.84 miles) to a minimum ratings of 290 MVA | KCPL | 36 | 2779156.16
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Rebuild the CNTRVIL5 to DAKOTA_5 161kV line 1 | TBD | Rebuild the existing CNTRVIL5 to DAKOTA_5 161 kV line(17.38 miles) to a minimum ratings of 310 MVA | KCPL | 36 | 17001533.12
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Rebuild the MARTCIT5 to REDEL 5 161kV line 1 | TBD | Rebuild the existing MARTCIT5 to REDEL 5 161 kV line(3.86 miles) to a minimum ratings of 400 MVA | KCPL | 36 | 4280000
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Rebuild the SHWNMSN5 to LENEXA 5 161kV line 1 | TBD | Rebuild the existing SHWNMSN5 to LENEXA 5 161 kV line(3.91 miles) to a minimum ratings of 420 MVA | KCPL | 36 | 4227303
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Rebuild the STILWEL5 to REDEL 5 161kV line 1 | TBD | Rebuild the existing STILWEL5 to REDEL 5 161 kV line(4.22 miles) to a minimum ratings of 420 MVA | KCPL | 36 | 4385553
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Rebuild the WGARDNR5 to BNSF 5 161kV line 1 | TBD | Rebuild the existing WGARDNR5 to BNSF 5 161 kV line(2.6 miles) to a minimum ratings of 390 MVA | KCPL | 36 | 2730733
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Upgrade terminal equipment at Stilwel 345/161 kV transformer | TBD | Upgrade terminal equipment to achieve normal rating of 550 MVA and emergency 605 MVA | KCPL | 36 | 334423
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Rebuild the STHTOWN5 to HICKMAN5 161kV line 1 | TBD | Rebuild the existing STHTOWN5 to HICKMAN5 161 kV line(5.55 miles) to a minimum ratings of 320 MVA | KCPL | 36 | 75000
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Upgrade terminal equipment at West Gardner 345/161 kV transformer | TBD | Upgrade terminal equipment to achieve the minimum rating of 600 MVA | KCPL | 36 | 334423
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Rebuild the MOONLT 5 to BNSF 5 161kV line 1 | TBD | Rebuild the existing MOONLT 5 to BNSF 5 161 kV line(3.43 miles) to a minimum ratings of 390 MVA | KCPL | 36 | 4334675
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Rebuild the CRAIG 5 to LENEXA 5 161kV line 2 | TBD | Rebuild the existing CRAIG 5 to LENEXA 5 161 kV line(3.02 miles) to a minimum ratings of 460 MVA | KCPL | 36 | 3102115
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Rebuild the STILWEL5 to HICKMAN5 161kV line 1 | TBD | Rebuild the existing STILWEL5 to HICKMAN5 161 kV line(13.51 miles) to a minimum ratings of 365 MVA | KCPL | 36 | 13215806.24
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | BELTONS5 to PECULR 5 161kV line 1 Rating Update | TBD | Correct line ratings to 467 & 522 MVA for Summer Normal and Emergency and Winter rating to 548 & 557 MVA for Normal and Emergency per TO feedback | KCPL | 0 | 0
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | CRAIG 5 to LENEXA 5 161kV line 1 Rating Update | TBD | Correct the line rating to 535 MVA for all seasons both normal and emergency per TO feedback | KCPL | 0 | 0
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | SPRGFLD5 to LAR382 5 161kV line 1 Rating Update | TBD | Correct the line rating to 223 MVA per TO feedback | SWPA | 0 | 0
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Rebuild the BENTON 7 to G20-076-TAP 345kV line 1 | TBD | Rebuild the existing BENTON 7 to G20-076-TAP 345 kV line(22 miles) to a minimum ratings of 1570 MVA | WERE | 36 | 25177768
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Rebuild the LACYGNE7 to G20-007-TAP 345kV line 1 | TBD | Rebuild the existing LACYGNE7 to G20-007-TAP 345 kV line(0.6 miles) to a minimum ratings of 1485 MVA | WERE | 36 | 488950.8
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | MARMTNE5 Breaker Rating Update | TBD | Correct line ratings to 370 MVA and 418 MVA for Normal and Emergency per TO feedback | WERE | 0 | 0
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | 4544 Stateline CC 161kV Substation GEN-2020-064 Interconnection (Non-shared NU) (EDE) | 156877 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-064 (64/Thermal), into the Point of Interconnection (POI) at 4544 Stateline CC 161kV Substation | EDE | 0 | 0
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | 4544 Stateline CC 161kV Substation GEN-2020-064 Interconnection (TOIF) (EDE) | 156878 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-064 (64/Thermal), into the Point of Interconnection (POI) at 4544 Stateline CC 161kV Substation | EDE | 0 | 0
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | La Russell 161 kV Substation GEN-2020-088 Interconnection (Non-shared NU) (EDE) | 156915 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-088 (150/Solar), into the Point of Interconnection (POI) at La Russell 161 kV Substation | EDE | 36 | 4207850
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | La Russell 161 kV Substation GEN-2020-088 Interconnection (TOIF) (EDE) | 156916 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-088 (150/Solar), into the Point of Interconnection (POI) at La Russell 161 kV Substation | EDE | 36 | 221466
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Riverton-Neosho 161kV line GEN-2020-079 Interconnection (Non-shared NU) (EDE) | 156951 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-079 (225/Hybrid), into the Point of Interconnection (POI) at Riverton-Neosho 161kV line | EDE | 36 | 12010063
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Riverton-Neosho 161kV line GEN-2020-079 Interconnection (TOIF) (EDE) | 156952 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-079 (225/Hybrid), into the Point of Interconnection (POI) at Riverton-Neosho 161kV line | EDE | 36 | 632109
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Pleasant Hill 345/161/69 kV Substation GEN-2020-061 Interconnection (Non-shared NU) (GMO) | 156943 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-061 (29/Thermal), into the Point of Interconnection (POI) at Pleasant Hill 345/161/69 kV Substation | GMO | 12-18 | 112911
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Pleasant Hill 345/161/69 kV Substation GEN-2020-061 Interconnection (TOIF) (GMO) | 156944 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-061 (29/Thermal), into the Point of Interconnection (POI) at Pleasant Hill 345/161/69 kV Substation | GMO | 0 | 0
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Windsor to AEC Sedalia 161 kV line GEN-2020-072 Interconnection (Non-shared NU) (GMO) | 156986 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-072 (150/Hybrid), into the Point of Interconnection (POI) at Windsor to AEC Sedalia 161 kV line | GMO | 36-48 | 12297085
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Windsor to AEC Sedalia 161 kV line GEN-2020-072 Interconnection (TOIF) (GMO) | 156987 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-072 (150/Hybrid), into the Point of Interconnection (POI) at Windsor to AEC Sedalia 161 kV line | GMO | 36-48 | 890009.14
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Craig-West Gardner 345 kV GEN-2020-057 and GEN-2020-058 Interconnection (Non-shared NU) (KCPL) | 156897 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Solar) and GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Craig-West Gardner 345 kV | KCPL | 36-48 | 2287129
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Craig-West Gardner 345 kV GEN-2020-057 and GEN-2020-058 Interconnection (TOIF) (KCPL) | 156898 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Solar) and GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Craig-West Gardner 345 kV | KCPL | 36-48 | 937649
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Evergy La Cygne to Wolf Creek 345kV Substation GEN-2020-007 Interconnection (Non-shared NU) (KCPL) | 156903 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-007 (650/Hybrid), into the Point of Interconnection (POI) at Evergy La Cygne to Wolf Creek 345kV Substation | KCPL | 36-48 | 25589611
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Evergy La Cygne to Wolf Creek 345kV Substation GEN-2020-007 Interconnection (TOIF) (KCPL) | 156904 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-007 (650/Hybrid), into the Point of Interconnection (POI) at Evergy La Cygne to Wolf Creek 345kV Substation | KCPL | 36-48 | 1705966
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | SE Ottawa to Pleasant Valley 161kV GEN-2020-073 Interconnection (Non-shared NU) (KCPL) | 156958 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-073 (190/Hybrid), into the Point of Interconnection (POI) at SE Ottawa to Pleasant Valley 161kV | KCPL | 36-48 | 12351050
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | SE Ottawa to Pleasant Valley 161kV GEN-2020-073 Interconnection (TOIF) (KCPL) | 156959 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-073 (190/Hybrid), into the Point of Interconnection (POI) at SE Ottawa to Pleasant Valley 161kV | KCPL | 36-48 | 890009
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | East Substation 69 kV GEN-2020-003 Interconnection (Non-shared NU) (KPP) | 156901 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-003 (58/Thermal), into the Point of Interconnection (POI) at East Substation 69 kV | KPP | 24 | 1667200
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | East Substation 69 kV GEN-2020-003 Interconnection (TOIF) (KPP) | 156902 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-003 (58/Thermal), into the Point of Interconnection (POI) at East Substation 69 kV | KPP | 24 | 130000
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Corporation Carpenter 345kV Substation GEN-2020-008 Interconnection (Non-shared NU) (SPS) | 156895 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-008 (250/Hybrid), into the Point of Interconnection (POI) at Corporation Carpenter 345kV Substation | SPS | 42 | 1636674
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Corporation Carpenter 345kV Substation GEN-2020-008 Interconnection (TOIF) (SPS) | 156896 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-008 (250/Hybrid), into the Point of Interconnection (POI) at Corporation Carpenter 345kV Substation | SPS | 42 | 2424709
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Russell 115 kV Substation GEN-2020-056 Interconnection (TOIF) (SUNC) | 144324 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-056 (20/Solar), into the Point of Interconnection (POI) at Russell 115 kV Substation | SUNC | 12 | 2268883
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Russell 115 kV Substation GEN-2020-056 Interconnection (Non-shared NU) (SUNC) | 144325 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-056 (20/Solar), into the Point of Interconnection (POI) at Russell 115 kV Substation | SUNC | 12 | 219181
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Benton to Wolf Creek 345 kV Line GEN-2020-076 Interconnection (TOIF) (WERE) | 156883 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-076 (200/Battery/Storage), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | WERE | 36-48 | 1705966
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Benton to Wolf Creek 345 kV Line GEN-2020-086 Interconnection (TOIF) (WERE) | 156884 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-086 (500/Solar), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | WERE | 36-48 | 112911
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Benton to Wolf Creek 345kV Line GEN-2020-076, GEN-2020-086 Interconnection (DISIS-2020-001) (WERE) | 156885 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-076, GEN-2020-086 (200/Battery/Storage and 500/Solar), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | WERE | 36-48 | 22839882
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Dakota 161 kV Substation GEN-2020-089 Interconnection (Non-shared NU) (WERE) | 156899 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-089 (104/Solar), into the Point of Interconnection (POI) at Dakota 161 kV Substation | WERE | 36-48 | 730484
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Dakota 161 kV Substation GEN-2020-089 Interconnection (TOIF) (WERE) | 156900 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-089 (104/Solar), into the Point of Interconnection (POI) at Dakota 161 kV Substation | WERE | 36-48 | 890009
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Neosho-Delaware 345 kV GEN-2020-052 Interconnection (Non-shared NU) (WERE) | 156933 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-052 (251/Wind), into the Point of Interconnection (POI) at Neosho-Delaware 345 kV | WERE | 36-48 | 22839882
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Neosho-Delaware 345 kV GEN-2020-052 Interconnection (TOIF) (WERE) | 156934 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-052 (251/Wind), into the Point of Interconnection (POI) at Neosho-Delaware 345 kV | WERE | 36-48 | 1705966
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Swissvale to Morris 230 KV line GEN-2020-071 Interconnection (Non-shared NU) (WERE) | 156972 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-071 (252/Wind), into the Point of Interconnection (POI) at Swissvale to Morris 230 KV line | WERE | 36-48 | 22839882
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Swissvale to Morris 230 KV line GEN-2020-071 Interconnection (TOIF) (WERE) | 156973 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-071 (252/Wind), into the Point of Interconnection (POI) at Swissvale to Morris 230 KV line | WERE | 36-48 | 1705966
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Wolf Creek- Blackberry 345 kV Substation GEN-2020-090 Interconnection (Non-shared NU) (WERE) | 156988 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-090 (204.3/Solar), into the Point of Interconnection (POI) at Wolf Creek- Blackberry 345 kV Substation | WERE | 36-48 | 21420838
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Wolf Creek- Blackberry 345 kV Substation GEN-2020-090 Interconnection (TOIF) (WERE) | 156989 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-090 (204.3/Solar), into the Point of Interconnection (POI) at Wolf Creek- Blackberry 345 kV Substation | WERE | 36-48 | 1705966
Contingent | Steady State | 04 - Southeast | 2020 ITP | NRIS | Russett - South Brown 138 kV Ckt 1 Rebuild | TBD | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | WFEC | 36 | 10267391
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Replace 1st Transformer at Snyder | TBD | Replace transformer at Snyder to an emergency rating of 250 MVA | AEPW | 36 | 3128743
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lawton Eastside to G20-075-TAP 345 kV Line Rebuild | TBD | Rebuild 6.9 miles of 345 kV from Lawton Eastside to G20-075-TAP to a minimum of 1200 MVA (Update line length in model to 6.9 miles) | AEPW | 36 | 7896663.6
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Roosevelt Tap to Hobart City 69 kV Line Rebuild | TBD | Rebuild 1.4 miles of the Hobart City to Roosevelt Tap 69 kV line, near Hobart City to a minimum of 50 MVA (The other 8.6 miles closest to Roosevelt Tap has a summer emergency rating of 123 MVA) | AEPW | 36 | 1272528.6
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lawton Eastside to G17-171-TAP 345 kV Line Rebuild | TBD | Rebuild 14.4 miles of 345 kV Lawton Eastside to G17-171-TAP 1 to a minimum of 1730 MVA | AEPW | 36 | 16479993.6
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Welsh to Wilkes 345 kV Line Rebuild | TBD | Rebuild 12.08 miles from Welsh to Wilkes 345 kV line to a minimum of 1040 MVA (The remaining 18.55 miles doesn't get overloaded) | AEPW | 36 | 13824883.52
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Longwood to Wilkes 345 kV Line Rating Update | TBD | Update emergency rating in the model to 1195 MVA for the Longwood to Wilkes 345 kV Line per TO feedback | AEPW | 0 | 0
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Terry Road to G17-171-TAP 345 kV Line Rebuild | TBD | Rebuild 13.91 miles of 345 kV from Terry Road to G17-171-TAP to a minimum of 1480 MVA | AEPW | 36 | 15919216.04
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Snyder to Tom Steed 69 kV Line Rebuild | TBD | Rebuild 8.7 miles of Snyder to Tom Steed Tap 69 kV line to a minimum of 40 MVA (The other 6.3 miles has summer emergency ratings of 68 MVA or higher ) | AEPW | 36 | 7907856.3
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Altus Junction to Tipton T2 69 kV Line Rating Update | TBD | Update emergency rating in the model to 206 MVA for the Altus Junction to Tipton T2 6 kV Line per TO feedback | AEPW | 0 | 0
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Clinton Air Force Base Tap to Hobart Junction 138 kV Line Rating Update | TBD | Update emergency rating in the model to 330 MVA for the Clinton Air Force Base Tap to Hobart Junction 138 kV Line per TO feedback | AEPW | 0 | 0
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Clinton Air Force Base Tap to Elk City 138 kV Line Rating Update | TBD | Update emergency rating in the model to 330 MVA for the Clinton Air Force Base Tap to Elk City 138 kV Line per TO feedback | AEPW | 0 | 0
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Walters to Walters Junction 69 kV Line Rebuild | TBD | Rebuild 5.13 miles of 69 kV from Walters to Walters Junction to a minimum of 60 MVA | AEPW/WFEC | 36 | 4662908.37
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | NRIS | Rebuild the RUSSET-4 to GLASSES4 138kV line 1 | TBD | Rebuild the existing RUSSET-4 to GLASSES4 138 kV line(8.33 miles) to a minimum ratings of 180 MVA | OGE | 36 | 9600000
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Build 2nd Transformer at Gracemont | TBD | BUILD 2nd 345/138 kV Transformer to a minimum of 520 MVA | OKGE | 36 | 8302968
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Build 2nd Transformer at Johnson County | TBD | BUILD 2nd 345/138 kV Transformer to a minimum of 580 MVA | OKGE | 36 | 8302968
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Build 2nd Transformer at Woodring | TBD | Build 2nd 345/138 kV Transformer to a minimum of 460 MVA | OKGE | 36 | 8302968
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Replace Sunnyside Transformer (CKT ID 3) | TBD | Replace the transformer with circuit ID 3 at Sunnyside to an emergency rating of 380 MVA | OKGE | 36 | 8302968
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Carter County to Chickasaw 138 kV Line Rebuild | TBD | Rebuild Carter County to Chickasaw 2.73 mile 138 kV line to a minimum of 230 MVA | OKGE | 36 | 2632154.07
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Sunnyside to Uniroyal 138 kV Line Rebuild | TBD | Rebuild Sunnyside to Uniroyal 5.58 miles 138 kV line to a minimum of 310 MVA | OKGE | 36 | 5380007.22
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Johnson County to Six Mile Creek Tap 138 kV Line Rebuild | TBD | Rebuild Six Mile Creek Tap to Johnson County 6.08 mile 138 kV line to a minimum of 240 MVA | OKGE | 36 | 5862086.72
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Wind Mill Creek Tap to Six Mile Creek Tap 138 kV Line Rebuild | TBD | Rebuild Wind Mill Creek Tap to Six Mile Creek Tap 0.55 mile 138 kV line to a minimum of 230 MVA | OKGE | 36 | 530287.45
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Ratliff to Carter County 138 kV Line Rebuild | TBD | Rebuild Ratliff to Carter County 7.22 mile 138 kV line to a minimum of 190 MVA | OKGE | 36 | 6961227.98
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Carter County to Ardmore West 138 kV Line Rebuild | TBD | Rebuild Ardmore West to Carter County 4.06 mile 138 kV line to a minimum of 270 MVA | OKGE | 36 | 3914485.54
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Uniroyal to Ardmore West 138 kV Line Rebuild | TBD | Rebuild Ardmore West to Uniroyal 0.57 mile 138 kV line to a minimum of 280 MVA | OKGE | 36 | 549570.63
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Wind Mill Creek Tap to Arbuckle 138 kV Line Rebuild | TBD | Rebuild Arbuckle to Wind Mill Creek Tap 13.16 mile 138 kV line to a minimum of 230 MVA | OKGE | 36 | 12688332.44
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Sunnyside to G20-074-TAP 345 kV Line Rebuild | TBD | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap (on the line to Terry Road) to a minimum of 1760 MVA | OKGE/AEPW | 36 | 14992216.4
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Build 3rd Transformer at Tuco | TBD | BUILD 3rd 345/138 kV Transformer to an emergency rating of 675 MVA | SPS | 36 | 8302968
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Anadarko to Cherry Road 138 kV Line Rebuild | TBD | Rebuild 25.15 miles of 138 kV from Aanadarko to Cherry Road (SN/SE/WN/WE: 241/283/306/338 MVA) | WFEC | 36 | 17605000
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Snyder to G20-016-TAP 138 kV Line Rebuild | TBD | Rebuild a total of 18.55 miles of 138 kV line from Cache Junction to Snyder (SN/SE/WN/WE: 241/283/287/287 MVA) | WFEC | 36 | 10227000
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Replace 1st Transformer at Grandfield | TBD | Replace transformer at Grandfield to an emergency rating of 112 MVA | WFEC | 36 | 500000
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Cache Junction to G20-016-TAP 138 kV Line Rebuild | TBD | Rebuild a total of 18.55 miles of 138 kV line from Cache Junction to Snyder (SN/SE/WN/WE: 241/283/287/287 MVA) | WFEC | 36 | 2758000
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Anadarko to Cleveland Switch 138 kV Line Rebuild | TBD | Rebuild 11.1 miles of 138 kV from Aanadarko to Cleveland Switch (SN/SE/WN/WE: 299/353/381/421 MVA) | WFEC | 36 | 10800000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Cimmarron to Lawton 345 kV Line GEN-2020-075 Interconnection (TOIF) (AEP) | 156888 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-075 (200/Battery/Storage), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | AEP | 42 | 3250000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Cimmarron to Lawton 345 kV Line GEN-2020-087 Interconnection (TOIF) (AEP) | 156889 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-087 (500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | AEP | 42 | 3250000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Cimmarron to Lawton 345kV Line GEN-2020-075, GEN-2020-087 Interconnection (DISIS-2020-001) (AEP) | 156890 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-075, GEN-2020-087 (200/Battery/Storage and 500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | AEP | 42 | 20050000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lawton to Sunnyside 345 kV Line GEN-2020-085 Interconnection (TOIF) (AEP) | 156919 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-085 (500/Solar), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Line | AEP | 42 | 3250000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lawton to Sunnyside 345 kV Substation GEN-2020-074 Interconnection (TOIF) (AEP) | 156920 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-074 (200/Battery/Storage), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Substation | AEP | 42 | 3250000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lawton to Sunnyside 345kV Line GEN-2020-074, GEN-2020-085 Interconnection (DISIS-2020-001) (AEP) | 156921 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-074, GEN-2020-085 (200/Battery/Storage, 500/Solar), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Substation | AEP | 42 | 20050000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lydia 345 kV Station GEN-2020-054 Interconnection (TOIF) (AEP) | 156929 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-054 (298/Solar), into the Point of Interconnection (POI) at Lydia 345 kV Station | AEP | 36 | 2850000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lydia 345kV Station GEN-2020-054 Interconnection (DISIS-2020-001) (AEP) | 156930 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-054, into the Point of Interconnection (POI) at Lydia 345 kV Station | AEP | 36 | 3000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Pryor Junction - Midwest Carbide 138kV line GEN-2020-092 Interconnection (Non-shared NU) (AEP) | 156947 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-092 (100/Solar), into the Point of Interconnection (POI) at Pryor Junction - Midwest Carbide 138kV line | AEP | 36 | 8850000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Pryor Junction - Midwest Carbide 138kV line GEN-2020-092 Interconnection (TOIF) (AEP) | 156948 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-092 (100/Solar), into the Point of Interconnection (POI) at Pryor Junction - Midwest Carbide 138kV line | AEP | 36 | 1800000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Snyder-Altus Jct. 138kV GEN-2020-012 Interconnection (Non-shared NU) (AEP) | 156966 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-012 (113/Hybrid), into the Point of Interconnection (POI) at Snyder-Altus Jct. 138kV | AEP | 36 | 9100000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Snyder-Altus Jct. 138kV GEN-2020-012 Interconnection (TOIF) (AEP) | 156967 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-012 (113/Hybrid), into the Point of Interconnection (POI) at Snyder-Altus Jct. 138kV | AEP | 36 | 1800000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Tap the 345 kV Northwest Texarkana - Valliant line GEN-2020-020 Interconnection (TOIF) (AEP) | 156974 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-020 (201.6/Hybrid), into the Point of Interconnection (POI) at Tap the 345 kV Northwest Texarkana - Valliant line | AEP | 42 | 3250000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Tenaska Switching Substation 345kV GEN-2020-081 Interconnection (Non-shared NU) (AEP) | 156975 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-081 (200/Battery/Storage), into the Point of Interconnection (POI) at Tenaska Switching Substation 345kV | AEP | 36 | 3400000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Tenaska Switching Substation 345kV GEN-2020-081 Interconnection (TOIF) (AEP) | 156976 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-081 (200/Battery/Storage), into the Point of Interconnection (POI) at Tenaska Switching Substation 345kV | AEP | 36 | 3150000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Tap the 345 kV Northwest Texarkana - Valliant line GEN-2020-020 Interconnection (Non-shared NU) (AEP) | 156993 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-020 (201.6/Hybrid), into the Point of Interconnection (POI) at Tap the 345 kV Northwest Texarkana - Valliant line | AEP | 42 | 16950000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Johnston County 345 kV Substation GEN-2020-015 Interconnection (Non-shared NU) (OGE) | 156913 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-015 (104/Solar), into the Point of Interconnection (POI) at Johnston County 345 kV Substation | OGE | 36 | 5043342
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Johnston County 345 kV Substation GEN-2020-015 Interconnection (TOIF) (OGE) | 156914 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-015 (104/Solar), into the Point of Interconnection (POI) at Johnston County 345 kV Substation | OGE | 36 | 4312689
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Woodring 345 KV Station GEN-2020-023 Interconnection (Non-shared NU) (OGE) | 156990 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-023 (202/Battery/Storage), into the Point of Interconnection (POI) at Woodring 345 KV Station | OGE | 36 | 4814099
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Woodring 345 KV Station GEN-2020-023 Interconnection (TOIF) (OGE) | 156991 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-023 (202/Battery/Storage), into the Point of Interconnection (POI) at Woodring 345 KV Station | OGE | 36 | 4116657
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Seiling-Taloga Substations 138kV GEN-2020-010 Interconnection (Non-shared NU) (WFEC) | 156960 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-010 (140/Hybrid), into the Point of Interconnection (POI) at Seiling-Taloga Substations 138kV | WFEC | 36 | 5000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Seiling-Taloga Substations 138kV GEN-2020-010 Interconnection (TOIF) (WFEC) | 156961 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-010 (140/Hybrid), into the Point of Interconnection (POI) at Seiling-Taloga Substations 138kV | WFEC | 36 | 500000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Snyder SW-Cache 138 kV line GEN-2020-016 Interconnection (Non-shared NU) (WFEC) | 156964 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-016 (202/Wind), into the Point of Interconnection (POI) at Snyder SW-Cache 138 kV line | WFEC | 36 | 5000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Snyder SW-Cache 138 kV line GEN-2020-016 Interconnection (TOIF) (WFEC) | 156965 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-016 (202/Wind), into the Point of Interconnection (POI) at Snyder SW-Cache 138 kV line | WFEC | 36 | 500000
Contingent | Steady State | 04 - Southeast/05 - Southwest | 2023 ITP | ERIS | Anadarko to Gracemont 138 kV Build Circuits 2 & 3 | NTC 220754 | Build two new 15 mile circuits from Anadarko to Gracemont 138 kV with SN/SE ratings of 478 MVA | OKGE/WFEC | 36 | 10984522.6317
Current Study | Steady State | 04 - Southeast/05 - Southwest | DISIS-2020-001 | NRIS | Rebuild the D.E.S.-4 to OMDUNE-4 138kV line 1 | TBD | Rebuild the existing D.E.S.-4 to OMDUNE-4 138 kV line(1.26 miles) to a minimum ratings of 125 MVA | AEPW | 36 | 1214840
Current Study | Steady State | 04 - Southeast/05 - Southwest | DISIS-2020-001 | NRIS | Rebuild the DUNCAN-4 to DUNCHERTP4 138kV line 1 | TBD | Rebuild the existing DUNCAN-4 to DUNCHERTP4 138 kV line(1.6 miles) to a minimum ratings of 135 MVA | AEPW | 36 | 1542654.4
Current Study | Steady State | 04 - Southeast/05 - Southwest | DISIS-2020-001 | NRIS | Rebuild the D.E.S.-4 to DUNCHERTP4 138kV line 1 | TBD | Rebuild the existing D.E.S.-4 to DUNCHERTP4 138 kV line(3.53 miles) to a minimum ratings of 130 MVA | AEPW | 36 | 3403481.27
Current Study | Steady State | 04 - Southeast/05 - Southwest | DISIS-2020-001 | ERIS | Duncan to Duncan Bois D' Arc 138 kV Line Rebuild | TBD | Rebuild 3.9 miles of 138 kV from Duncan to Duncan Bois D' Arc. Upgrade RCTL at Duncan | AEPW/OMPA | 36 | 3760220.1
Current Study | Steady State | 04 - Southeast/05 - Southwest | DISIS-2020-001 | ERIS | Comanche Tap to Duncan Bois D' Arc 138 kV Line Rebuild | TBD | Rebuild 17.69 miles of 138 kV from Comanche Tap to Duncan Bois D' Arc | AEPW/OMPA | 36 | 17055972.71
Current Study | Steady State | 04 - Southeast/05 - Southwest | DISIS-2020-001 | NRIS | Rebuild the TUCO_INT 7 to CRAWFISH_DR 345kV line 2 | TBD | Rebuild the existing TUCO_INT 7 to CRAWFISH_DR 345 kV line(1.53 miles) to a minimum ratings of 1250 MVA | SPS | 36 | 1750999.32
Current Study | Steady State/Stability | 05 - Southwest | DISIS-2020-001 | ERIS | Build New Andrews to Road Runner 345 kV Line | TBD | Build a new 40 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | SPS | 36 | 70410000
Current Study | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Sidewinder to Andrews 345 kV Lidar Clearance Correction | TBD | Correct existing Lidar clearance issues on Sidewinder to Andrews 345 kV line to increase the line rating to 1400MVA SN/SE. | SPS | 36 | 400000
Current Study | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Sidewinder to Hobbs 345 kV Lidar Clearance Correction | TBD | Correct existing Lidar clearance issues on Sidewinder to Hobbs 345 kV line to increase the line rating to 1400MVA SN/SE. | SPS | 36 | 400000
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Lawton East Side to Oklaunion 345kV GEN-2020-009 Interconnection (Non-shared NU) (AEP) | 156917 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-009 (300/Hybrid), into the Point of Interconnection (POI) at Lawton East Side to Oklaunion 345kV | AEP | 42 | 16950000
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Lawton East Side to Oklaunion 345kV GEN-2020-009 Interconnection (TOIF) (AEP) | 156918 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-009 (300/Hybrid), into the Point of Interconnection (POI) at Lawton East Side to Oklaunion 345kV | AEP | 42 | 3250000
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | 230kV Lamb County Interchange GEN-2020-017 Interconnection (Non-shared NU) (SPS) | 156875 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-017 (74.88/Solar), into the Point of Interconnection (POI) at 230kV Lamb County Interchange | SPS | 42 | 10594150
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | 230kV Lamb County Interchange GEN-2020-017 Interconnection (TOIF) (SPS) | 156876 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-017 (74.88/Solar), into the Point of Interconnection (POI) at 230kV Lamb County Interchange | SPS | 42 | 1017923
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Hobbs-Andrews 345 kV Line GEN-2020-065 Interconnection (Non-shared NU) (SPS) | 156909 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-065 (1003/Thermal), into the Point of Interconnection (POI) at Hobbs-Andrews 345 kV Line | SPS | 42 | 30437222
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Hobbs-Andrews 345 kV Line GEN-2020-065 Interconnection (TOIF) (SPS) | 156910 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-065 (1003/Thermal), into the Point of Interconnection (POI) at Hobbs-Andrews 345 kV Line | SPS | 42 | 1532799
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Lubbock East Substation 230 kV GEN-2020-060 Interconnection (Non-shared NU) (SPS) | 156926 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-060 (200/Battery/Storage), into the Point of Interconnection (POI) at Lubbock East Substation 230 kV | SPS | 42 | 9772056
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Lubbock East Substation 230 kV GEN-2020-060 Interconnection (TOIF) (SPS) | 156927 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-060 (200/Battery/Storage), into the Point of Interconnection (POI) at Lubbock East Substation 230 kV | SPS | 42 | 1947926
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | OASIS 230kV Substation GEN-2020-062 Interconnection (Non-shared NU) (SPS) | 156937 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-062 (256/Solar), into the Point of Interconnection (POI) at OASIS 230kV Substation | SPS | 42 | 9895590
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | OASIS 230kV Substation GEN-2020-062 Interconnection (TOIF) (SPS) | 156938 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-062 (256/Solar), into the Point of Interconnection (POI) at OASIS 230kV Substation | SPS | 42 | 1852814
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067 Interconnection (TOIF) (SPS) | 156979 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-067 (352.5/Wind), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | SPS | 42 | 690867
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067, GEN-2020-068 Interconnection (DISIS-2020-001) (SPS) | 156980 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-067, GEN-2020-068 (352.5/Wind and 400/Solar), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | SPS | 42 | 21693802
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco to Yoakum 345kV line GEN-2020-068 Interconnection (TOIF) (SPS) | 156981 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-068 (400/Solar), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | SPS | 42 | 690867
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco-Yoakum-Hobbs 345 kV GEN-2020-059 Interconnection (Non-shared NU) (SPS) | 156982 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-059 (250/Hybrid), into the Point of Interconnection (POI) at Tuco-Yoakum-Hobbs 345 kV | SPS | 42 | 15573312
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco-Yoakum-Hobbs 345 kV GEN-2020-059 Interconnection (TOIF) (SPS) | 156983 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-059 (250/Hybrid), into the Point of Interconnection (POI) at Tuco-Yoakum-Hobbs 345 kV | SPS | 42 | 1381735
1651449734.5417

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 00ALL | 0 | 24SP | GEN-2020-065 | " | Non-Converge |  |  |  |  | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Non-Converge | 00ALL | 0 | 27SP | GEN-2020-065 | " | Non-Converge |  |  |  |  | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Non-Converge | 00ALL | 0 | 27WP | GEN-2020-065 | " | Non-Converge |  |  |  |  | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Non-Converge | 01NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 03NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 04ALL | 0 | 24SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 04ALL | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 04ALL | 0 | 27SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 04ALL | 0 | 27WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 04NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 05ALL | 0 | 24SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 05ALL | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 05ALL | 0 | 27SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 05ALL | 0 | 27WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 05NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 650269 70&BLUFF 7 115 996691 T691 115 1 |  | 120 | 0.12248 | 105.4 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 650269 70&BLUFF 7 115 996691 T691 115 1 |  | 120 | 0.12248 | 105.4 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 650269 70&BLUFF 7 115 996691 T691 115 1 |  | 120 | 0.12248 | 105.4 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 650269 70&BLUFF 7 115 996691 T691 115 1 |  | 120 | 0.12248 | 103.95 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 650269 70&BLUFF 7 115 996691 T691 115 1 |  | 120 | 0.12248 | 103.95 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 650269 70&BLUFF 7 115 996691 T691 115 1 |  | 120 | 0.12248 | 103.95 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.81 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.8 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.8 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82652 | 127.63 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82652 | 127.63 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54236 | 104.67 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54236 | 104.67 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54236 | 102.9 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54236 | 102.9 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53884 | 102.53 | P12:161:OPPD:S1249-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53884 | 100.83 | P21:161:OPPD:S1249-S1256:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53884 | 100.83 | P12:161:OPPD:S1249-S1256:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53884 | 100.66 | P12:161:OPPD:S1253-S1256:LS::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.28 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.27 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.26 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82668 | 115.52 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82668 | 115.52 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.46 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.46 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.45 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82664 | 116.97 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82664 | 116.97 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.81 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.8 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.8 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82652 | 127.63 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82652 | 127.63 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54236 | 104.67 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54236 | 104.67 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54236 | 102.9 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54236 | 102.9 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53884 | 102.53 | P12:161:OPPD:S1249-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53884 | 100.83 | P21:161:OPPD:S1249-S1256:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53884 | 100.83 | P12:161:OPPD:S1249-S1256:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53884 | 100.66 | P12:161:OPPD:S1253-S1256:LS::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.28 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.27 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.26 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82668 | 115.52 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82668 | 115.52 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.46 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.46 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.45 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82664 | 116.97 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82664 | 116.97 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.81 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.8 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.8 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82652 | 127.63 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82652 | 127.63 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54236 | 104.67 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54236 | 104.67 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54236 | 102.9 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54236 | 102.9 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53884 | 102.53 | P12:161:OPPD:S1249-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53884 | 100.83 | P21:161:OPPD:S1249-S1256:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53884 | 100.83 | P12:161:OPPD:S1249-S1256:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53884 | 100.66 | P12:161:OPPD:S1253-S1256:LS::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.28 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.27 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.26 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82668 | 115.52 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82668 | 115.52 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.46 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.46 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.45 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82664 | 116.97 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82664 | 116.97 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.81 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.59 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.52 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.81 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.59 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.52 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.81 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.59 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.52 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646281 S1281 5 161 646287 S1287 5 161 1 |  | 215 | 0.16976 | 110.39 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646281 S1281 5 161 646287 S1287 5 161 1 |  | 215 | 0.17081 | 102.1 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646281 S1281 5 161 646287 S1287 5 161 1 |  | 215 | 0.16967 | 103.4 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646281 S1281 5 161 646287 S1287 5 161 1 |  | 215 | 0.16976 | 110.39 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646281 S1281 5 161 646287 S1287 5 161 1 |  | 215 | 0.17081 | 102.1 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646281 S1281 5 161 646287 S1287 5 161 1 |  | 215 | 0.16967 | 103.4 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646281 S1281 5 161 646287 S1287 5 161 1 |  | 215 | 0.16976 | 110.39 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646281 S1281 5 161 646287 S1287 5 161 1 |  | 215 | 0.17081 | 102.1 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646281 S1281 5 161 646287 S1287 5 161 1 |  | 215 | 0.16967 | 103.4 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83024 | 229.47 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45764 | 111.84 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45764 | 111.84 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45764 | 107.33 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45764 | 107.33 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.82919 | 210.68 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45518 | 111.83 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45518 | 111.83 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45518 | 105.85 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45518 | 105.85 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83033 | 209.61 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45756 | 101.29 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45756 | 101.29 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83024 | 229.47 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45764 | 111.84 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45764 | 111.84 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45764 | 107.33 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45764 | 107.33 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.82919 | 210.68 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45518 | 111.83 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45518 | 111.83 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45518 | 105.85 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45518 | 105.85 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83033 | 209.61 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45756 | 101.29 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45756 | 101.29 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83024 | 229.47 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45764 | 111.84 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45764 | 111.84 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45764 | 107.33 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45764 | 107.33 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.82919 | 210.68 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45518 | 111.83 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45518 | 111.83 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45518 | 105.85 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45518 | 105.85 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83033 | 209.61 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45756 | 101.29 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45756 | 101.29 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25426 | 106.15 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | FROM->TO | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25751 | 111.88 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | FROM->TO | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25417 | 116.82 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25426 | 106.15 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | FROM->TO | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25751 | 111.88 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | FROM->TO | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25417 | 116.82 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25426 | 106.15 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | FROM->TO | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25751 | 111.88 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | FROM->TO | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25417 | 116.82 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-065 | FROM->TO | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 |  | 797 | 1 | 123.87 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 |  | 797 | 1 | 112.7 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-065 | FROM->TO | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 |  | 797 | 1 | 112.67 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-065 | FROM->TO | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 |  | 797 | 1 | 124.47 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 |  | 797 | 1 | 112.81 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-065 | FROM->TO | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 |  | 797 | 1 | 113.24 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.062 | 103.66 | P42:345:OKGE:SB_CION7384::::
Thermal | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06215 | 102.99 | 514801 MINCO 7 345 514901 CIMARON7 345 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06238 | 102.04 | P42:345:OKGE:SB_MICO7301::::
Thermal | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06268 | 100.91 | P42:345:OKGE:SB_MICO7312::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04959 | 102.15 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04959 | 102.15 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0306 | 102.15 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04702 | 102.15 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04947 | 101.02 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04947 | 101.02 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03065 | 101.02 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0469 | 101.02 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04959 | 105.95 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04959 | 105.95 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0306 | 105.95 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04702 | 105.95 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04947 | 104.73 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04947 | 104.73 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03065 | 104.73 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0469 | 104.73 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.03629 | 108.52 | 515120 RUSSET-4 138 515147 GLASSES4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03847 | 104.28 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03847 | 104.28 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0324 | 104.28 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0324 | 104.28 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03223 | 104.28 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03693 | 104.28 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03847 | 108.1 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03847 | 108.1 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0324 | 108.1 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0324 | 108.1 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03223 | 108.1 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03693 | 108.1 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-074 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0368 | 102.2 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-085 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0368 | 102.2 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03065 | 102.2 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03065 | 102.2 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.031 | 102.2 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03528 | 102.2 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.03629 | 106.19 | 515147 GLASSES4 138 515149 MADINDT4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03565 | 104.45 | 515150 CANEYCK4 138 515151 LTLCITY4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03565 | 104.45 | 515150 CANEYCK4 138 515151 LTLCITY4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.04375 | 104.45 | 515150 CANEYCK4 138 515151 LTLCITY4 138 1
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.04426 | 110.04 | 515150 CANEYCK4 138 515151 LTLCITY4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03565 | 103.16 | 515151 LTLCITY4 138 515152 BROWNTP4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03565 | 103.16 | 515151 LTLCITY4 138 515152 BROWNTP4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.04375 | 103.16 | 515151 LTLCITY4 138 515152 BROWNTP4 138 1
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.04426 | 109.18 | 515151 LTLCITY4 138 515152 BROWNTP4 138 1
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.03747 | 100.79 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-074 | TO->FROM | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.05018 | 101.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-085 | TO->FROM | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.05018 | 101.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | TO->FROM | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.07583 | 101.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | TO->FROM | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.07583 | 101.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO->FROM | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.11929 | 101.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-015 | TO->FROM | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 |  | 997.3 | 0.04006 | 101.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-003 | TO->FROM | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1485 | 0.07284 | 107.06 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-072 | TO->FROM | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1485 | 0.03273 | 107.06 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1485 | 0.06673 | 107.06 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1485 | 0.93234 | 107.06 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-076 | TO->FROM | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1485 | 0.56192 | 107.06 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-086 | TO->FROM | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1485 | 0.56192 | 107.06 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03312 | 124.97 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06389 | 124.97 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03312 | 124.97 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06358 | 124.97 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05894 | 124.97 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05944 | 123.49 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05967 | 123.49 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.054 | 123.49 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.05096 | 118.33 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04808 | 118.33 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04609 | 118.33 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04774 | 117.13 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04531 | 117.13 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04249 | 117.13 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03312 | 119.93 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06389 | 119.93 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03312 | 119.93 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06358 | 119.93 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05894 | 119.93 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05944 | 118.66 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05967 | 118.66 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.054 | 118.66 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.06073 | 104.53 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.09048 | 104.53 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.06073 | 104.53 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.0761 | 104.53 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.08174 | 104.53 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.05793 | 103.68 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.08796 | 103.68 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.05793 | 103.68 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.07474 | 103.68 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 334 | 0.07829 | 103.68 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 360 | 0.06817 | 106.24 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 360 | 0.09991 | 106.24 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 360 | 0.06817 | 106.24 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 360 | 0.08698 | 106.24 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 360 | 0.0908 | 106.24 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 360 | 0.06519 | 105.43 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 360 | 0.09725 | 105.43 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 360 | 0.06519 | 105.43 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 360 | 0.08554 | 105.43 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 543002 MARTCIT5 161 543053 REDEL 5 161 1 |  | 360 | 0.08708 | 105.43 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04997 | 100.15 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04723 | 100.15 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04714 | 100.15 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03316 | 127.36 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06211 | 127.36 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03316 | 127.36 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06201 | 127.36 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05946 | 127.36 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05777 | 125.52 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05825 | 125.52 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0546 | 125.52 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05598 | 103.7 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05647 | 103.7 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05281 | 103.7 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.06073 | 113.38 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.09048 | 113.38 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.06073 | 113.38 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.0761 | 113.38 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.08174 | 113.38 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.05793 | 112.39 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.08796 | 112.39 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.05793 | 112.39 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.07474 | 112.39 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.07829 | 112.39 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.0608 | 103.22 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.09083 | 103.22 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.0608 | 103.22 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.0776 | 103.22 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.08115 | 103.22 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 385 | 0.06817 | 107.02 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 385 | 0.09991 | 107.02 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 385 | 0.06817 | 107.02 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 385 | 0.08698 | 107.02 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 385 | 0.0908 | 107.02 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 385 | 0.06519 | 106.14 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 385 | 0.09725 | 106.14 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 385 | 0.06519 | 106.14 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 385 | 0.08554 | 106.14 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 385 | 0.08708 | 106.14 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04997 | 121.25 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04723 | 121.25 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04714 | 121.25 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04682 | 119.72 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04459 | 119.72 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04356 | 119.72 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03316 | 121.91 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06211 | 121.91 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03316 | 121.91 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06201 | 121.91 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05946 | 121.91 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05777 | 120.34 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05825 | 120.34 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0546 | 120.34 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05765 | 117.06 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0579 | 117.06 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05015 | 117.06 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0529 | 115.95 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05358 | 115.95 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04501 | 115.95 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04569 | 111.01 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04334 | 111.01 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03882 | 111.01 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04228 | 110.13 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0403 | 110.13 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03511 | 110.13 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05765 | 113.39 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0579 | 113.39 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05015 | 113.39 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0529 | 112.43 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05358 | 112.43 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04501 | 112.43 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05728 | 130.05 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06236 | 130.05 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04951 | 130.05 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05196 | 128.63 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0573 | 128.63 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04393 | 128.63 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04501 | 120.62 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04628 | 120.62 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03808 | 120.62 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0412 | 119.49 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04271 | 119.49 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03407 | 119.49 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05728 | 124.1 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06236 | 124.1 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04951 | 124.1 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05196 | 122.89 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0573 | 122.89 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04393 | 122.89 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03079 | 123.91 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0715 | 123.91 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03079 | 123.91 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.07165 | 123.91 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05508 | 123.91 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06719 | 123.38 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06773 | 123.38 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05043 | 123.38 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.05448 | 114.18 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.05192 | 114.18 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04151 | 114.18 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0514 | 113.72 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04917 | 113.72 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03818 | 113.72 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03079 | 118.96 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0715 | 118.96 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03079 | 118.96 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.07165 | 118.96 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05508 | 118.96 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06719 | 118.49 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06773 | 118.49 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05043 | 118.49 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05292 | 108.98 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05544 | 108.98 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04415 | 108.98 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04899 | 108.23 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05178 | 108.23 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03998 | 108.23 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.04022 | 102.97 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.07293 | 102.97 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.04022 | 102.97 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.06605 | 102.97 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.05567 | 102.97 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.03836 | 103.54 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.07118 | 103.54 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.03836 | 103.54 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.06476 | 103.54 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 334 | 0.05355 | 103.54 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04227 | 106.02 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04189 | 106.02 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03466 | 106.02 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03947 | 105.44 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03932 | 105.44 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03166 | 105.44 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05292 | 106.7 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05544 | 106.7 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04415 | 106.7 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04899 | 106.04 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05178 | 106.04 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03998 | 106.04 | 541340 BELTONS5 161 541342 PECULR 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 334 | 0.05455 | 103.27 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 334 | 0.11399 | 103.27 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 334 | 0.05455 | 103.27 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 334 | 0.03095 | 103.27 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 334 | 0.05414 | 102.75 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 334 | 0.11372 | 102.75 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 334 | 0.05414 | 102.75 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 334 | 0.03036 | 102.75 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 355 | 0.0583 | 103.98 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 355 | 0.12178 | 103.98 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 355 | 0.0583 | 103.98 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 355 | 0.03034 | 103.98 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 355 | 0.03299 | 103.98 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 355 | 0.05779 | 103.47 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 355 | 0.12143 | 103.47 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 355 | 0.05779 | 103.47 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 355 | 0.03039 | 103.47 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 355 | 0.03229 | 103.47 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03787 | 100.97 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04508 | 100.97 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03787 | 100.97 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04404 | 100.97 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0402 | 100.97 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03496 | 100.02 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04229 | 100.02 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03496 | 100.02 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04157 | 100.02 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03713 | 100.02 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0487 | 131.19 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05686 | 131.19 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0487 | 131.19 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05865 | 131.19 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05199 | 131.19 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04461 | 129.93 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05293 | 129.93 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04461 | 129.93 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05511 | 129.93 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04771 | 129.93 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-058 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0417 | 102.6 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05002 | 102.6 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-057 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0417 | 102.6 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0522 | 102.6 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0448 | 102.6 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.0487 | 100.08 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.05686 | 100.08 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.0487 | 100.08 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.05865 | 100.08 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.05199 | 100.08 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03787 | 122.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04508 | 122.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03787 | 122.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04404 | 122.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0402 | 122.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03496 | 121.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04229 | 121.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03496 | 121.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04157 | 121.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03713 | 121.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0487 | 125.1 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05686 | 125.1 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0487 | 125.1 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05865 | 125.1 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05199 | 125.1 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04461 | 124.02 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05293 | 124.02 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04461 | 124.02 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05511 | 124.02 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04771 | 124.02 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542966 WGARDNR5 161 997281 WEST GARDN11 161 11 |  | 535 | 0.15934 | 105.53 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542966 WGARDNR5 161 997281 WEST GARDN11 161 11 |  | 535 | 0.15934 | 105.53 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542966 WGARDNR5 161 997281 WEST GARDN11 161 11 |  | 535 | 0.09238 | 105.53 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542966 WGARDNR5 161 997279 WEST GARDN11 161 11 |  | 535 | 0.15908 | 100.92 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542966 WGARDNR5 161 997279 WEST GARDN11 161 11 |  | 535 | 0.15908 | 100.92 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542966 WGARDNR5 161 997279 WEST GARDN11 161 11 |  | 535 | 0.09146 | 100.92 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-058 | FROM->TO | 542966 WGARDNR5 161 997279 WEST GARDN11 161 11 |  | 535 | 0.14771 | 103.96 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-057 | FROM->TO | 542966 WGARDNR5 161 997279 WEST GARDN11 161 11 |  | 535 | 0.14771 | 103.96 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-007 | FROM->TO | 542966 WGARDNR5 161 997279 WEST GARDN11 161 11 |  | 535 | 0.08009 | 103.96 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 334 | 0.05455 | 106.93 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 334 | 0.11399 | 106.93 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 334 | 0.05455 | 106.93 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 334 | 0.03095 | 106.93 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 334 | 0.05414 | 107.1 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 334 | 0.11372 | 107.1 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 334 | 0.05414 | 107.1 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 334 | 0.03036 | 107.1 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.0583 | 104.48 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.12178 | 104.48 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.0583 | 104.48 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.03034 | 104.48 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.03299 | 104.48 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.05779 | 104.61 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.12143 | 104.61 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.05779 | 104.61 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.03039 | 104.61 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.03229 | 104.61 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542965 W.GRDNR7 345 997281 WEST GARDN11 161 11 |  | 535 | 0.09238 | 106.46 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542965 W.GRDNR7 345 997281 WEST GARDN11 161 11 |  | 535 | 0.15934 | 106.46 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542965 W.GRDNR7 345 997281 WEST GARDN11 161 11 |  | 535 | 0.15934 | 106.46 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542965 W.GRDNR7 345 997279 WEST GARDN11 161 11 |  | 535 | 0.09146 | 101.86 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-007 | FROM->TO | 542965 W.GRDNR7 345 997279 WEST GARDN11 161 11 |  | 535 | 0.08009 | 104.48 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542965 W.GRDNR7 345 997279 WEST GARDN11 161 11 |  | 535 | 0.15908 | 101.86 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-057 | FROM->TO | 542965 W.GRDNR7 345 997279 WEST GARDN11 161 11 |  | 535 | 0.14771 | 104.48 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542965 W.GRDNR7 345 997279 WEST GARDN11 161 11 |  | 535 | 0.15908 | 101.86 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-058 | FROM->TO | 542965 W.GRDNR7 345 997279 WEST GARDN11 161 11 |  | 535 | 0.14771 | 104.48 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0445 | 111.58 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04656 | 111.58 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03454 | 111.58 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04863 | 111.79 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05096 | 111.79 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03842 | 111.79 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03555 | 106.44 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03474 | 106.44 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03886 | 106.6 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03828 | 106.6 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03002 | 106.6 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0445 | 108.82 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04656 | 108.82 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03454 | 108.82 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04863 | 108.97 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05096 | 108.97 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03842 | 108.97 | 542951 HAW G5 1 22.0 543665 HAWTHN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 334 | 0.15273 | 100.02 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 334 | 0.03287 | 100.02 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 355 | 0.16198 | 100.1 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 543044 MOONLT 5 161 543132 BNSF 5 161 1 |  | 355 | 0.03614 | 100.1 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06126 | 108.93 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05676 | 108.93 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04416 | 108.93 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05726 | 108.15 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05305 | 108.15 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03991 | 108.15 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04854 | 104.64 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04249 | 104.64 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03427 | 104.64 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04568 | 104.02 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03989 | 104.02 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03122 | 104.02 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06126 | 106.65 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05676 | 106.65 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04416 | 106.65 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05726 | 105.97 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05305 | 105.97 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03991 | 105.97 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 334 | 0.15202 | 104.25 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 334 | 0.03251 | 104.25 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 334 | 0.15273 | 103.68 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 334 | 0.03287 | 103.68 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.16198 | 100.7 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.03614 | 100.7 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.16115 | 101.22 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542966 WGARDNR5 161 543132 BNSF 5 161 1 |  | 365 | 0.03565 | 101.22 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 997280 STILWELL11 161 11 |  | 557 | 0.04191 | 100.67 | 542968 STILWEL7 345 3WXFMR STILWELL22 22
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 997280 STILWELL11 161 11 |  | 557 | 0.04191 | 100.67 | 542968 STILWEL7 345 3WXFMR STILWELL22 22
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 997280 STILWELL11 161 11 |  | 557 | 0.09645 | 100.67 | 542968 STILWEL7 345 3WXFMR STILWELL22 22
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542968 STILWEL7 345 997280 STILWELL11 161 11 |  | 557 | 0.04191 | 101.1 | 542968 STILWEL7 345 3WXFMR STILWELL22 22
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542968 STILWEL7 345 997280 STILWELL11 161 11 |  | 557 | 0.04191 | 101.1 | 542968 STILWEL7 345 3WXFMR STILWELL22 22
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542968 STILWEL7 345 997280 STILWELL11 161 11 |  | 557 | 0.09645 | 101.1 | 542968 STILWEL7 345 3WXFMR STILWELL22 22
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0505 | 118.9 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06007 | 118.9 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0456 | 118.9 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04656 | 118.41 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05638 | 118.41 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04143 | 118.41 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04092 | 113.75 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04545 | 113.75 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03577 | 113.75 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0381 | 113.37 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04285 | 113.37 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03277 | 113.37 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0505 | 114.81 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06007 | 114.81 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0456 | 114.81 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04656 | 114.37 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05638 | 114.37 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04143 | 114.37 | 542969 STILWEL5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03079 | 132.36 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0715 | 132.36 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03079 | 132.36 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.07165 | 132.36 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05508 | 132.36 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06719 | 131.78 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06773 | 131.78 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05043 | 131.78 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06483 | 105.78 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06536 | 105.78 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04806 | 105.78 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.03079 | 100.74 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.0715 | 100.74 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.03079 | 100.74 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.07165 | 100.74 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.05508 | 100.74 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.06719 | 100.32 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.06773 | 100.32 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 350 | 0.05043 | 100.32 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.05448 | 120.77 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.05192 | 120.77 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04151 | 120.77 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0514 | 120.27 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04917 | 120.27 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03818 | 120.27 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03079 | 125.92 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0715 | 125.92 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03079 | 125.92 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.07165 | 125.92 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05508 | 125.92 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06719 | 125.4 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06773 | 125.4 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05043 | 125.4 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06483 | 100.72 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06536 | 100.72 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04806 | 100.72 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07327 | 102.72 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04969 | 102.72 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07327 | 102.72 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0358 | 102.72 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.08459 | 105.93 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.05618 | 105.93 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.08459 | 105.93 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.04032 | 105.93 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.08001 | 102.5 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.05175 | 102.5 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.08001 | 102.5 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.03542 | 102.5 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.07534 | 113.64 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.05077 | 113.64 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.07534 | 113.64 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.0349 | 113.64 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.07135 | 110.73 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.0469 | 110.73 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.07135 | 110.73 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.03062 | 110.73 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-058 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.06667 | 101 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-073 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.04223 | 101 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-057 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.06667 | 101 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 430 | 0.08116 | 103.06 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 430 | 0.0534 | 103.06 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 430 | 0.08116 | 103.06 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 430 | 0.03665 | 103.06 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 430 | 0.07662 | 100.28 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 430 | 0.04901 | 100.28 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 430 | 0.07662 | 100.28 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 430 | 0.0318 | 100.28 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07327 | 100.37 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04969 | 100.37 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07327 | 100.37 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0358 | 100.37 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.08459 | 103.48 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.05618 | 103.48 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.08459 | 103.48 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.04032 | 103.48 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 533653 WOLFCRK2 69.0 997459 WOLF CREEK T 69.0 1 |  | 110 | 0.04105 | 118.31 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 532797 WOLFCRK7 345 997459 WOLF CREEK T 69.0 1 |  | 110 | 0.04105 | 128.42 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03079 | 129.23 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0715 | 129.23 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03079 | 129.23 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.07165 | 129.23 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05508 | 129.23 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06719 | 128.7 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06773 | 128.7 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05043 | 128.7 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06483 | 103.23 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06536 | 103.23 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04806 | 103.23 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.05448 | 118.33 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.05192 | 118.33 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04151 | 118.33 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0514 | 117.86 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04917 | 117.86 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03818 | 117.86 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03079 | 123.34 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0715 | 123.34 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03079 | 123.34 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.07165 | 123.34 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05508 | 123.34 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06719 | 122.87 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06773 | 122.87 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05043 | 122.87 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0782 | 107.73 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07118 | 107.73 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0782 | 107.73 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03363 | 107.73 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04187 | 107.73 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07429 | 104.2 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.06741 | 104.2 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07429 | 104.2 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03046 | 104.2 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03764 | 104.2 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.08833 | 108.73 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.07914 | 108.73 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.08833 | 108.73 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.03724 | 108.73 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.04631 | 108.73 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.08352 | 105.08 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.0745 | 105.08 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.08352 | 105.08 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.03323 | 105.08 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.04115 | 105.08 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05555 | 109.79 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05605 | 109.79 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04378 | 109.79 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05154 | 108.97 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05232 | 108.97 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03952 | 108.97 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.044 | 105.24 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.042 | 105.24 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.034 | 105.24 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04114 | 104.58 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03938 | 104.58 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03094 | 104.58 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05555 | 107.34 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05605 | 107.34 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04378 | 107.34 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05154 | 106.62 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05232 | 106.62 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03952 | 106.62 | 543036 OLATHE 5 161 543045 SWITZER5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0505 | 111.18 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06007 | 111.18 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0456 | 111.18 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04656 | 110.69 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05638 | 110.69 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04143 | 110.69 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04092 | 107.53 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04545 | 107.53 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03577 | 107.53 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0381 | 107.16 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04285 | 107.16 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03277 | 107.16 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0505 | 108.47 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06007 | 108.47 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0456 | 108.47 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04656 | 108.03 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05638 | 108.03 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04143 | 108.03 | 543036 OLATHE 5 161 543046 OXFORD 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0505 | 116.11 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06007 | 116.11 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0456 | 116.11 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04656 | 115.55 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05638 | 115.55 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04143 | 115.55 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04092 | 111.51 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04545 | 111.51 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03577 | 111.51 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0381 | 111.07 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04285 | 111.07 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03277 | 111.07 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0505 | 112.53 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06007 | 112.53 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0456 | 112.53 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04656 | 112.03 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05638 | 112.03 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04143 | 112.03 | 543046 OXFORD 5 161 543050 ANTIOCH5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05262 | 102.78 | System Intact
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05467 | 102.78 | System Intact
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04265 | 102.78 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04871 | 102 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05104 | 102 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0385 | 102 | System Intact
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05262 | 101.56 | System Intact
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05467 | 101.56 | System Intact
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04265 | 101.56 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04871 | 100.88 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05104 | 100.88 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0385 | 100.88 | System Intact
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.03629 | 102.8 | P12:138:OKGE:BKRBKR248::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03565 | 100.9 | P12:138:OKGE:BKRBKR261::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03565 | 100.9 | P12:138:OKGE:BKRBKR261::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.04375 | 100.9 | P12:138:OKGE:BKRBKR261::::
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.04426 | 108.4 | P12:138:OKGE:BKRBKR261::::
Thermal | 00NR | 1 | 27SP | GEN-2020-015 | FROM->TO | 515120 RUSSET-4 138 515147 GLASSES4 138 1 |  | 153 | 0.03261 | 100.83 | P12:138:OKGE:BKRBKR345::::
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | FROM->TO | 515120 RUSSET-4 138 515147 GLASSES4 138 1 |  | 170 | 0.03268 | 100.02 | P12:138:OKGE:BKRBKR345::::
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03079 | 127.31 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0715 | 127.31 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03079 | 127.31 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.07165 | 127.31 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05508 | 127.31 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06719 | 126.77 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06773 | 126.77 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05043 | 126.77 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06483 | 101.63 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06536 | 101.63 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04806 | 101.63 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.05448 | 116.82 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.05192 | 116.82 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04151 | 116.82 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0514 | 116.35 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04917 | 116.35 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03818 | 116.35 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03079 | 121.76 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0715 | 121.76 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03079 | 121.76 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.07165 | 121.76 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05508 | 121.76 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06719 | 121.28 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06773 | 121.28 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05043 | 121.28 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-084 | FROM->TO | 646209 S1209 5 161 646231 S1231 5 161 1 |  | 250 | 0.05189 | 105.55 | P12:161:OPPD:S1209-S1231 CKT 2:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06027 | 109.04 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.10051 | 109.04 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04157 | 109.04 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05623 | 108.1 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.09649 | 108.1 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03729 | 108.1 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04727 | 104.71 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.07814 | 104.71 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03227 | 104.71 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04439 | 103.91 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.07527 | 103.91 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06027 | 106.79 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.10051 | 106.79 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04157 | 106.79 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05623 | 105.93 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.09649 | 105.93 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03729 | 105.93 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04959 | 103.38 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04959 | 103.38 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0306 | 103.38 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04702 | 103.38 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04947 | 102.21 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04947 | 102.21 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03065 | 102.21 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0469 | 102.21 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04959 | 107.19 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04959 | 107.19 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0306 | 107.19 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04702 | 107.19 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04947 | 105.93 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04947 | 105.93 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03065 | 105.93 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0469 | 105.93 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.05717 | 100.06 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.05717 | 100.06 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.04959 | 107.49 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.04959 | 107.49 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.0306 | 107.49 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.04702 | 107.49 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.04947 | 106.25 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.04947 | 106.25 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.03065 | 106.25 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.0469 | 106.25 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04959 | 112.11 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04959 | 112.11 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0306 | 112.11 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04702 | 112.11 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04947 | 110.82 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04947 | 110.82 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03065 | 110.82 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0469 | 110.82 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04959 | 115.91 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04959 | 115.91 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0306 | 115.91 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04702 | 115.91 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04947 | 114.53 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04947 | 114.53 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03065 | 114.53 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0469 | 114.53 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 00NR | 1 | 27SP | GEN-2020-084 | FROM->TO | 646209 S1209 5 161 646231 S1231 5 161 1 |  | 238 | 0.04517 | 100.01 | P21:161:OPPD:S1231-S1209 CKT2:LT::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-084 | FROM->TO | 646209 S1209 5 161 646231 S1231 5 161 1 |  | 250 | 0.05189 | 109.46 | P21:161:OPPD:S1231-S1209 CKT2:LT::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-084 | FROM->TO | 646209 S1209 5 161 646231 S1231 5 161 1 |  | 250 | 0.05199 | 103.28 | P21:161:OPPD:S1231-S1209 CKT2:LT::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.05496 | 102.74 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.05717 | 100.06 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05842 | 115.36 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.06048 | 115.36 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05154 | 115.36 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05351 | 114.82 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05592 | 114.82 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04634 | 114.82 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04628 | 109.74 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0454 | 109.74 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0399 | 109.74 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04276 | 109.3 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04217 | 109.3 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03614 | 109.3 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05842 | 111.98 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.06048 | 111.98 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05154 | 111.98 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05351 | 111.5 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05592 | 111.5 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04634 | 111.5 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05794 | 116.48 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05944 | 116.48 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05097 | 116.48 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05295 | 115.32 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05483 | 115.32 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04565 | 115.32 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04592 | 110.62 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04455 | 110.62 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03945 | 110.62 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04234 | 109.7 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0413 | 109.7 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0356 | 109.7 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05794 | 112.91 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05944 | 112.91 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05097 | 112.91 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05295 | 111.91 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05483 | 111.91 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04565 | 111.91 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0669 | 102.75 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04372 | 102.75 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0669 | 102.75 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03102 | 102.75 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0589 | 100.93 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03589 | 100.93 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0589 | 100.93 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.07793 | 107.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.05003 | 107.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.07793 | 107.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.03531 | 107.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.06822 | 105.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.04052 | 105.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO->FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 370 | 0.06822 | 105.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05243 | 112.59 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.05373 | 112.59 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04236 | 112.59 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.04707 | 112.11 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.0487 | 112.11 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 542993 STHTOWN5 161 542994 HICKMAN5 161 1 |  | 231 | 0.03671 | 112.11 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04162 | 107.66 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04018 | 107.66 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03286 | 107.66 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03769 | 107.3 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03654 | 107.3 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05243 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.05373 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04236 | 109.68 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.04707 | 109.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.0487 | 109.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 280 | 0.03671 | 109.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 533653 WOLFCRK2 69.0 997459 WOLF CREEK T 69.0 1 |  | 110 | 0.0411 | 118.02 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 532797 WOLFCRK7 345 997459 WOLF CREEK T 69.0 1 |  | 110 | 0.0411 | 128.05 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.05496 | 102.74 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.05717 | 100.06 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.04939 | 107.52 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.04939 | 107.52 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.03029 | 107.52 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.04683 | 107.52 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.04925 | 106.21 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.04925 | 106.21 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.0303 | 106.21 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 |  | 106 | 0.04667 | 106.21 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04939 | 112.14 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04939 | 112.14 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03029 | 112.14 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04683 | 112.14 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04925 | 110.78 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04925 | 110.78 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0303 | 110.78 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04667 | 110.78 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04939 | 115.94 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04939 | 115.94 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.03029 | 115.94 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04683 | 115.94 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04925 | 114.5 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04925 | 114.5 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.0303 | 114.5 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 |  | 106 | 0.04667 | 114.5 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27WP | GEN-2020-015 | TO->FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 155 | 0.05717 | 100.16 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 00NR | 1 | 24SP | GEN-2020-001 | TO->FROM | 653312 MORRILL7 115 659821 GERINGT_-TS7 115 1 |  | 91 | 0.03297 | 100.86 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-001 | TO->FROM | 653312 MORRILL7 115 659821 GERINGT_-TS7 115 1 |  | 91 | 0.0331 | 105.18 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03327 | 108.27 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03892 | 108.27 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03327 | 105.24 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03892 | 105.24 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.04604 | 105.34 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03252 | 108.77 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03791 | 108.77 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03252 | 105.79 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03791 | 105.79 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.04464 | 105.01 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03327 | 100.65 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03892 | 100.65 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03327 | 100.11 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03892 | 100.11 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03252 | 101.19 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03791 | 101.19 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03252 | 100.65 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO->FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 250 | 281 | 0.03791 | 100.65 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 374 | 374 | 0.07534 | 113.64 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 374 | 374 | 0.05077 | 113.64 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 374 | 374 | 0.07534 | 113.64 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 374 | 374 | 0.0349 | 113.64 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 374 | 374 | 0.07135 | 110.73 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 374 | 374 | 0.0469 | 110.73 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 374 | 374 | 0.07135 | 110.73 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 374 | 374 | 0.03062 | 110.73 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2
Thermal | 00NR | 1 | 27WP | GEN-2020-058 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 374 | 374 | 0.06667 | 101 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2
Thermal | 00NR | 1 | 27WP | GEN-2020-073 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 374 | 374 | 0.04223 | 101 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2
Thermal | 00NR | 1 | 27WP | GEN-2020-057 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 374 | 374 | 0.06667 | 101 | 542978 CRAIG 5 161 543038 LENEXA 5 161 2
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13736 | 115.14 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24374 | 115.14 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14126 | 115.14 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13934 | 115.14 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13737 | 116.1 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.2451 | 116.1 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1388 | 116.1 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13735 | 116.1 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13599 | 112.06 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24047 | 112.06 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14252 | 112.06 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14101 | 112.06 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.22163 | 134.25 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.22163 | 133.69 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13737 | 116.03 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2451 | 116.03 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1388 | 116.03 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13735 | 116.03 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13736 | 114.66 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24374 | 114.66 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14126 | 114.66 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13934 | 114.66 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13599 | 111.6 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24047 | 111.6 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14252 | 111.6 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14101 | 111.6 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13535 | 112.63 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23757 | 112.63 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.137 | 112.63 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13533 | 112.63 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1341 | 109.08 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23449 | 109.08 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13835 | 109.08 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13708 | 109.08 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13535 | 112.16 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23757 | 112.16 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.137 | 112.16 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13533 | 112.16 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1341 | 108.63 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23449 | 108.63 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13835 | 108.63 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13708 | 108.63 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.15708 | 113.12 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.2462 | 113.12 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14758 | 113.12 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1469 | 113.12 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.15711 | 114.25 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.2475 | 114.25 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14531 | 114.25 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14513 | 114.25 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.22521 | 130.38 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.22521 | 129.84 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.15711 | 114.25 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2475 | 114.25 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14531 | 114.25 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14513 | 114.25 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.15708 | 112.64 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2462 | 112.64 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14758 | 112.64 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1469 | 112.64 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652507 FTTHOMP4 230 996647 FT2 KU1A 230 1 |  | 313 | 0.26807 | 123.16 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652507 FTTHOMP4 230 996646 FT2 KU1B 230 1 |  | 313 | 0.2624 | 120.55 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652506 FTTHOMP3 345 996647 FT2 KU1A 230 1 |  | 313 | 0.26807 | 123.26 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652506 FTTHOMP3 345 996646 FT2 KU1B 230 1 |  | 313 | 0.2624 | 120.65 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.22104 | 129.74 | 652513 HANLON 4 230 652523 SIOUXFL4 230 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.22104 | 129.2 | 652513 HANLON 4 230 652523 SIOUXFL4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1351 | 113.56 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24228 | 113.56 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13852 | 113.56 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13662 | 113.56 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13506 | 114.54 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24361 | 114.54 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.136 | 114.54 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13458 | 114.54 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13398 | 110.5 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23924 | 110.5 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14007 | 110.5 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13859 | 110.5 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.22104 | 130.99 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.22104 | 130.44 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13506 | 114.51 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24361 | 114.51 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.136 | 114.51 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13458 | 114.51 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1351 | 113.09 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24228 | 113.09 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13852 | 113.09 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13662 | 113.09 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13398 | 110.04 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23924 | 110.04 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14007 | 110.04 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13859 | 110.04 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652507 FTTHOMP4 230 996647 FT2 KU1A 230 1 |  | 313 | 0.26807 | 123.19 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652507 FTTHOMP4 230 996646 FT2 KU1B 230 1 |  | 313 | 0.2624 | 120.58 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652506 FTTHOMP3 345 996647 FT2 KU1A 230 1 |  | 313 | 0.26807 | 123.29 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652506 FTTHOMP3 345 996646 FT2 KU1B 230 1 |  | 313 | 0.2624 | 120.68 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13483 | 114.64 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24322 | 114.64 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13773 | 114.64 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1359 | 114.64 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13479 | 115.52 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24454 | 115.52 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13522 | 115.52 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13387 | 115.52 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1337 | 111.65 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24018 | 111.65 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13926 | 111.65 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13785 | 111.65 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.22195 | 131.77 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.22195 | 131.22 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13479 | 115.48 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24454 | 115.48 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13522 | 115.48 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13387 | 115.48 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13483 | 114.16 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24322 | 114.16 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13773 | 114.16 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1359 | 114.16 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1337 | 111.18 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24018 | 111.18 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13926 | 111.18 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13785 | 111.18 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13535 | 112.64 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23757 | 112.64 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.137 | 112.64 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13533 | 112.64 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13535 | 113.3 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23888 | 113.3 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13462 | 113.3 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13342 | 113.3 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1341 | 109.11 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23449 | 109.11 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13835 | 109.11 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13708 | 109.11 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13535 | 113.31 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23888 | 113.31 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13462 | 113.31 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13342 | 113.31 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13535 | 112.17 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23757 | 112.17 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.137 | 112.17 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13533 | 112.17 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1341 | 108.65 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23449 | 108.65 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13835 | 108.65 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13708 | 108.65 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13031 | 113.41 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23526 | 113.41 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13432 | 113.41 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13244 | 113.41 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13029 | 114.15 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23655 | 114.15 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13191 | 114.15 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13049 | 114.15 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.12882 | 111.26 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23194 | 111.26 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13538 | 111.26 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1339 | 111.26 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13029 | 114.17 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23655 | 114.17 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13191 | 114.17 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13049 | 114.17 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13031 | 112.94 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23526 | 112.94 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13432 | 112.94 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13244 | 112.94 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12882 | 110.8 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23194 | 110.8 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13538 | 110.8 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1339 | 110.8 | P11:23:NPPD:GENTLM1G:1:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13024 | 113.89 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23518 | 113.89 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13425 | 113.89 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13237 | 113.89 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13021 | 114.61 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23648 | 114.61 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13184 | 114.61 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13042 | 114.61 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.12877 | 111.61 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.2319 | 111.61 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13533 | 111.61 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13385 | 111.61 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13021 | 114.63 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23648 | 114.63 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13184 | 114.63 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13042 | 114.63 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13024 | 113.42 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23518 | 113.42 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13425 | 113.42 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13237 | 113.42 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.12877 | 111.14 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2319 | 111.14 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13533 | 111.14 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13385 | 111.14 | P11:24:NPPD:GENTLM2G:2:757::
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1298 | 109.25 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23293 | 109.25 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13636 | 109.25 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13488 | 109.25 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.21539 | 129.37 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.21539 | 128.84 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1298 | 108.79 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23293 | 108.79 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13636 | 108.79 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13488 | 108.79 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13779 | 113.38 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24417 | 113.38 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14169 | 113.38 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13977 | 113.38 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1378 | 114.38 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24553 | 114.38 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13923 | 114.38 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13779 | 114.38 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13662 | 110.01 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24111 | 110.01 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14315 | 110.01 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14165 | 110.01 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.22349 | 129.83 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.22349 | 129.29 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1378 | 114.34 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24553 | 114.34 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13923 | 114.34 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13779 | 114.34 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13779 | 112.9 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24417 | 112.9 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14169 | 112.9 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13977 | 112.9 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13662 | 109.55 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24111 | 109.55 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14315 | 109.55 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14165 | 109.55 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1382 | 113.9 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24663 | 113.9 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14174 | 113.9 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13981 | 113.9 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13818 | 114.9 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24798 | 114.9 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1392 | 114.9 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13777 | 114.9 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13717 | 109.72 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24365 | 109.72 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1434 | 109.72 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1419 | 109.72 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.22577 | 130.73 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.22577 | 130.19 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13818 | 114.87 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24798 | 114.87 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1392 | 114.87 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13777 | 114.87 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1382 | 113.43 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24663 | 113.43 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14174 | 113.43 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13981 | 113.43 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13717 | 109.27 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24365 | 109.27 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1434 | 109.27 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1419 | 109.27 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13621 | 114.18 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24482 | 114.18 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13908 | 114.18 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13722 | 114.18 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13617 | 115.2 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24616 | 115.2 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13654 | 115.2 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13518 | 115.2 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13519 | 111.02 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24187 | 111.02 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14075 | 111.02 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13932 | 111.02 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.22388 | 131 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.22388 | 130.46 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13617 | 115.15 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24616 | 115.15 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13654 | 115.15 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13518 | 115.15 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13621 | 113.71 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24482 | 113.71 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13908 | 113.71 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13722 | 113.71 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13519 | 110.56 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24187 | 110.56 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14075 | 110.56 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13932 | 110.56 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13839 | 114.15 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.2469 | 114.15 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14191 | 114.15 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13999 | 114.15 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13836 | 115.12 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24826 | 115.12 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13937 | 115.12 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13794 | 115.12 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13736 | 109.98 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24393 | 109.98 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14358 | 109.98 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14208 | 109.98 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.22604 | 130.96 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.22604 | 130.42 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13836 | 115.08 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24826 | 115.08 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13937 | 115.08 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13794 | 115.08 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13839 | 113.67 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2469 | 113.67 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14191 | 113.67 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13999 | 113.67 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13736 | 109.52 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24393 | 109.52 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14358 | 109.52 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14208 | 109.52 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1382 | 114.16 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24663 | 114.16 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14174 | 114.16 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13981 | 114.16 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13818 | 115.14 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24798 | 115.14 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1392 | 115.14 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13777 | 115.14 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13717 | 110.08 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24365 | 110.08 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1434 | 110.08 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1419 | 110.08 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.22577 | 130.94 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.22577 | 130.39 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13818 | 115.11 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24798 | 115.11 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1392 | 115.11 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13777 | 115.11 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1382 | 113.68 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24663 | 113.68 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14174 | 113.68 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13981 | 113.68 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13717 | 109.62 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24365 | 109.62 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1434 | 109.62 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1419 | 109.62 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13305 | 109.02 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23494 | 109.02 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13999 | 109.02 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13855 | 109.02 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13305 | 108.56 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23494 | 108.56 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13999 | 108.56 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13855 | 108.56 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13648 | 113.41 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24197 | 113.41 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13893 | 113.41 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13743 | 113.41 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13648 | 113.39 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24197 | 113.39 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13893 | 113.39 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13743 | 113.39 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13634 | 112.81 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23985 | 112.81 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14145 | 112.81 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13946 | 112.81 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13633 | 113.81 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24118 | 113.81 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13901 | 113.81 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13749 | 113.81 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1351 | 109.28 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23675 | 109.28 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14281 | 109.28 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14123 | 109.28 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.21912 | 129.88 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.21912 | 129.34 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13633 | 113.78 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24118 | 113.78 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13901 | 113.78 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13749 | 113.78 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13634 | 112.34 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23985 | 112.34 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14145 | 112.34 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13946 | 112.34 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1351 | 108.82 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23675 | 108.82 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14281 | 108.82 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14123 | 108.82 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.21677 | 129.23 | P12:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.21677 | 128.69 | P12:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13535 | 112.62 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23757 | 112.62 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.137 | 112.62 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13533 | 112.62 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1341 | 109.07 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23449 | 109.07 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13835 | 109.07 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13708 | 109.07 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13535 | 112.15 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23757 | 112.15 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.137 | 112.15 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13533 | 112.15 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1341 | 108.62 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23449 | 108.62 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13835 | 108.62 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13708 | 108.62 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13648 | 113.41 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24197 | 113.41 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13893 | 113.41 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13743 | 113.41 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.21977 | 129.28 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.21977 | 128.74 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13648 | 113.39 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24197 | 113.39 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13893 | 113.39 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13743 | 113.39 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13634 | 112.81 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23985 | 112.81 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14145 | 112.81 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13946 | 112.81 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13633 | 113.81 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24118 | 113.81 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13901 | 113.81 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13749 | 113.81 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1351 | 109.28 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23675 | 109.28 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14281 | 109.28 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14123 | 109.28 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.21912 | 129.88 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.21912 | 129.34 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13633 | 113.78 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24118 | 113.78 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13901 | 113.78 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13749 | 113.78 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13634 | 112.34 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23985 | 112.34 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14145 | 112.34 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13946 | 112.34 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1351 | 108.82 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23675 | 108.82 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14281 | 108.82 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14123 | 108.82 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13659 | 112.58 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24077 | 112.58 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14144 | 112.58 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13949 | 112.58 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1366 | 113.52 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24211 | 113.52 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13904 | 113.52 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13754 | 113.52 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.21989 | 129.41 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.21989 | 128.87 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1366 | 113.5 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24211 | 113.5 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13904 | 113.5 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13754 | 113.5 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13659 | 112.11 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24077 | 112.11 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14144 | 112.11 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13949 | 112.11 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1)
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.21677 | 129.23 | P21:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.21677 | 128.69 | P21:500:XEL:AUTO-SINGLE:FORBES2:CHIS-N2:1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13634 | 112.81 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23985 | 112.81 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14145 | 112.81 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13946 | 112.81 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13634 | 113.81 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24119 | 113.81 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13901 | 113.81 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13749 | 113.81 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1351 | 109.28 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23676 | 109.28 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14281 | 109.28 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14123 | 109.28 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.21912 | 129.88 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.21912 | 129.34 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13634 | 113.78 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24119 | 113.78 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13901 | 113.78 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13749 | 113.78 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13634 | 112.34 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23985 | 112.34 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14145 | 112.34 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13946 | 112.34 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1351 | 108.82 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23676 | 108.82 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14281 | 108.82 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14123 | 108.82 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14006 | 114.16 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24447 | 114.16 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14509 | 114.16 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14307 | 114.16 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14008 | 115.26 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.24586 | 115.26 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14261 | 115.26 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14107 | 115.26 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13879 | 109.13 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.2413 | 109.13 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14649 | 109.13 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.14489 | 109.13 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.22325 | 132.06 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.22325 | 131.51 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14008 | 115.21 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24586 | 115.21 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14261 | 115.21 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14107 | 115.21 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14006 | 113.68 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.24447 | 113.68 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14509 | 113.68 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14307 | 113.68 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13879 | 108.67 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.2413 | 108.67 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14649 | 108.67 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.14489 | 108.67 | P23:345:XEL:396 BKR SPK
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13759 | 113.41 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23848 | 113.41 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13808 | 113.41 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13651 | 113.41 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.1376 | 114.16 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23979 | 114.16 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13572 | 114.16 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13462 | 114.16 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13633 | 109.93 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.23537 | 109.93 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13945 | 109.93 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.13828 | 109.93 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z |  | 717 | 0.21732 | 130.25 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.21732 | 129.71 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.1376 | 114.15 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23979 | 114.15 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13572 | 114.15 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13462 | 114.15 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13759 | 112.94 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23848 | 112.94 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13808 | 112.94 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13651 | 112.94 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13633 | 109.47 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.23537 | 109.47 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13945 | 109.47 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 |  | 720 | 0.13828 | 109.47 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.13099 | 109.06 | System Intact
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.23594 | 109.06 | System Intact
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.13501 | 109.06 | System Intact
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.13313 | 109.06 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.13097 | 110.03 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.23723 | 110.03 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.13259 | 110.03 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.13117 | 110.03 | System Intact
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.1298 | 105.84 | System Intact
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.23293 | 105.84 | System Intact
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.13636 | 105.84 | System Intact
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.13488 | 105.84 | System Intact
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 717 |  | 0.21539 | 126.07 | System Intact
Thermal | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.21539 | 125.55 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.13097 | 110.07 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.23723 | 110.07 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.13259 | 110.07 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.13117 | 110.07 | System Intact
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.13099 | 108.6 | System Intact
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.23594 | 108.6 | System Intact
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.13501 | 108.6 | System Intact
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.13313 | 108.6 | System Intact
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.1298 | 105.39 | System Intact
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.23293 | 105.39 | System Intact
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.13636 | 105.39 | System Intact
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO->FROM | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | 720 |  | 0.13488 | 105.39 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM->TO | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | 445 |  | 0.06328 | 115.17 | System Intact
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM->TO | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | 445 |  | 0.06311 | 113.43 | System Intact
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM->TO | 640510 HOLT.CO3 345 640520 ANTELOPE 3 345 1 | 445 |  | 0.06345 | 110.1 | System Intact
Thermal | 01NR | 1 | 27L | N/A | " | None |  |  |  |  | None
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48632 | 144.26 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48677 | 124.62 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48709 | 119.27 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48704 | 119.09 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48632 | 121.14 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48677 | 111.83 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.36982 | 109.14 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.36982 | 109.04 | 533322 BAILEYV3 115 533337 SENECA 3 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48632 | 137.82 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48704 | 113.42 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48709 | 112.95 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48632 | 114.85 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.29094 | 114.16 | 640076 BEATRCE7 115 640208 HARBINE7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.29099 | 114.15 | 640076 BEATRCE7 115 640208 HARBINE7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69217 | 133.36 | 640105 CARLJCT7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69213 | 132.94 | 640105 CARLJCT7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69252 | 123.07 | 640105 CARLJCT7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69253 | 121.98 | 640105 CARLJCT7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.69213 | 120.33 | 640105 CARLJCT7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.69217 | 110.68 | 640105 CARLJCT7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69217 | 140.97 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69252 | 136.4 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69253 | 135.43 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69213 | 135.33 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.69213 | 122.65 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.69217 | 118.2 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.69252 | 106.68 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.69253 | 105.58 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.49233 | 118.94 | 640153 CRETE__7 115 640174 FRIEND 7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 135.87 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 126.51 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 119.08 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 117.91 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.77 | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.78 | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.75 | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.74 | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48344 | 114.84 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.4836 | 107.12 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.49233 | 119.04 | 640174 FRIEND 7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.49233 | 106.47 | 640174 FRIEND 7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.94 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.93 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.82 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.8 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 1 | 137.11 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 1 | 126.99 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 1 | 121.02 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 1 | 120.72 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.73097 | 104.92 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | TO->FROM | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.55356 | 116.64 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | TO->FROM | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.55196 | 109.81 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | TO->FROM | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.55387 | 106.49 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48416 | 142.51 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48409 | 138.56 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48477 | 118.67 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48474 | 118.45 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48409 | 126.03 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48416 | 119.86 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.34301 | 104.35 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 1 | 175.73 | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 1 | 175.68 | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 1 | 175.65 | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 1 | 175.54 | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 1 | 175.49 | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 1 | 175.48 | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48416 | 131.06 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48409 | 119.46 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48477 | 108.64 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48474 | 108.42 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48416 | 108.43 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48409 | 106.96 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48308 | 131.11 | 640426 STEELEC7 115 640558 S.FLATS.PLT7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48263 | 125.87 | 640426 STEELEC7 115 640558 S.FLATS.PLT7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48263 | 112.43 | 640426 STEELEC7 115 640558 S.FLATS.PLT7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48308 | 107.81 | 640426 STEELEC7 115 640558 S.FLATS.PLT7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48308 | 131.12 | 640558 S.FLATS.PLT7 115 3WXFMR STL.FLTS GSU 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48263 | 125.88 | 640558 S.FLATS.PLT7 115 3WXFMR STL.FLTS GSU 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48263 | 112.44 | 640558 S.FLATS.PLT7 115 3WXFMR STL.FLTS GSU 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48308 | 107.82 | 640558 S.FLATS.PLT7 115 3WXFMR STL.FLTS GSU 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | TO->FROM | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.55356 | 116.61 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | TO->FROM | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.55196 | 109.84 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | TO->FROM | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.55387 | 106.45 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.99988 | 105.83 | 764441 G20-013-XFM2 34.5 764447 G20-013-SS2 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 104.21 | 764441 G20-013-XFM2 34.5 764447 G20-013-SS2 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 104.13 | 764441 G20-013-XFM2 34.5 764447 G20-013-SS2 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.99988 | 105.83 | 764444 G20-013-XFM3 34.5 764448 G20-013-SS3 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 104.21 | 764444 G20-013-XFM3 34.5 764448 G20-013-SS3 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 104.13 | 764444 G20-013-XFM3 34.5 764448 G20-013-SS3 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.99988 | 105.83 | 764447 G20-013-SS2 115 764448 G20-013-SS3 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 104.21 | 764447 G20-013-SS2 115 764448 G20-013-SS3 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 104.13 | 764447 G20-013-SS2 115 764448 G20-013-SS3 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.99988 | 164.31 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 162.74 | System Intact
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 162.65 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48344 | 123.54 | System Intact
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4836 | 112.1 | System Intact
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48403 | 103.52 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.484 | 103.41 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48344 | 100.91 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48344 | 130.83 | P11:1:NPPD:S.FLATS.:W:83::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4836 | 125.27 | P11:1:NPPD:S.FLATS.:W:83::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.4836 | 112.01 | P11:1:NPPD:S.FLATS.:W:83::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48344 | 107.67 | P11:1:NPPD:S.FLATS.:W:83::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48344 | 130.83 | P11:1:NPPD:S.FLATS.GENW:W:83::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4836 | 125.27 | P11:1:NPPD:S.FLATS.GENW:W:83::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.4836 | 112.01 | P11:1:NPPD:S.FLATS.GENW:W:83::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48386 | 108.52 | P11:14:NPPD:BPS GT1G:1:90::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48386 | 108.52 | P11:14:NPPD:BPS GT2G:2:90::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48389 | 108.51 | P11:14:NPPD:BPS GT2G:2:90::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48384 | 109.17 | P11:14:NPPD:BPS ST3G:3:110::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48387 | 109.13 | P11:14:NPPD:BPS ST3G:3:110::
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.99988 | 162.02 | P11:69:NPPD:ORLEANS8:2:4::
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 160.57 | P11:69:NPPD:ORLEANS8:2:4::
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 160.54 | P11:69:NPPD:ORLEANS8:2:4::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.61 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.64 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.6 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.59 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.36982 | 102.55 | P12:115:WERE:KELL-SSEN-115:::HV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.43876 | 132.66 | P12:115:WERE:KNOB-NPPD-115:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.44142 | 102 | P12:115:WERE:KNOB-NPPD-115:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48199 | 108.78 | P12:161:OPPD:HUMBOLT-S1280:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.10186 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.18855 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.15327 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-069 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.08404 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.08196 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-002 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06229 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-027 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06053 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-030 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06053 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-033 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06053 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-036 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.05902 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-078 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06013 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-084 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06039 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-094 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06408 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.48042 | 104.54 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.10186 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.18855 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.15327 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-069 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.08404 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.08196 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-002 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06229 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-027 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06053 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-030 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06053 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-033 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06053 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-036 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.05902 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-078 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06013 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-084 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06039 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-094 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06408 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.48042 | 103.65 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.05156 | 120.55 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.0927 | 120.55 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.07605 | 120.55 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.23057 | 120.55 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05426 | 104.2 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-011 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.09543 | 104.2 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.07878 | 104.2 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-070 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.23331 | 104.2 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05431 | 102.2 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-011 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.09547 | 102.2 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.07883 | 102.2 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-070 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.23326 | 102.2 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48283 | 131.93 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48285 | 121.65 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48351 | 109.3 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48346 | 109.11 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48283 | 109.29 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48285 | 109.12 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48647 | 136.69 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48628 | 130.19 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48721 | 112.68 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48716 | 112.66 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48628 | 117.55 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48647 | 114.01 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48469 | 134.77 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48537 | 111.07 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48542 | 110.87 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48469 | 111.85 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | TO->FROM | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.55356 | 116.59 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | TO->FROM | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.55196 | 109.78 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | TO->FROM | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.55387 | 106.43 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.10186 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.18855 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.15327 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-069 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.08404 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.08196 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-002 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06229 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-027 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06053 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-030 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06053 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-033 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06053 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-036 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.05902 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-078 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06013 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-084 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06039 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-094 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06408 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.48042 | 104.54 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.10186 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.18855 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.15327 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-069 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.08404 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.08196 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-002 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06229 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-027 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06053 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-030 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06053 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-033 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06053 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-036 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.05902 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-078 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06013 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-084 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06039 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-094 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06408 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.48042 | 103.65 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.05156 | 120.55 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.0927 | 120.55 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.07605 | 120.55 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.23057 | 120.55 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05426 | 104.2 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-011 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.09543 | 104.2 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.07878 | 104.2 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-070 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.23331 | 104.2 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05431 | 102.2 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-011 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.09547 | 102.2 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.07883 | 102.2 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-070 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.23326 | 102.2 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.10153 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.18829 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.15301 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-069 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.08383 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.08181 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-002 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06218 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-027 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06043 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-030 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06043 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-033 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06043 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-036 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.05892 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-078 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06002 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-084 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06028 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-094 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.06397 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | TO->FROM | 530584 POSTROCK6 230 997537 POSTROCK T1 230 1 |  | 600 | 0.48009 | 104.41 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.10153 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.18829 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.15301 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-069 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.08383 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.08181 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-002 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06218 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-027 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06043 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-030 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06043 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-033 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06043 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-036 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.05892 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-078 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06002 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-084 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06028 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-094 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.06397 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM->TO | 530583 POSTROCK7 345 997537 POSTROCK T1 230 1 |  | 600 | 0.48009 | 103.52 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.05082 | 119.93 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.0921 | 119.93 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.07546 | 119.93 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.22983 | 119.93 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05351 | 103.77 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-011 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.09481 | 103.77 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.07817 | 103.77 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-070 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.23256 | 103.77 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05356 | 101.75 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-011 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.09486 | 101.75 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.07823 | 101.75 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-070 | FROM->TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.23251 | 101.75 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48634 | 136.77 | P42:345:NPPD:BKR-MOR-3306::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48615 | 130.12 | P42:345:NPPD:BKR-MOR-3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48708 | 112.79 | P42:345:NPPD:BKR-MOR-3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48703 | 112.69 | P42:345:NPPD:BKR-MOR-3306::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48615 | 117.45 | P42:345:NPPD:BKR-MOR-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48634 | 114.05 | P42:345:NPPD:BKR-MOR-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48388 | 134.12 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48381 | 127.09 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48458 | 110.95 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48452 | 110.8 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48381 | 114.45 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48388 | 111.46 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48626 | 136.69 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48605 | 130.51 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48701 | 112.55 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48696 | 112.46 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48605 | 117.86 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48626 | 113.97 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48405 | 142.67 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 138.78 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48466 | 118.64 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48462 | 118.46 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48396 | 126.18 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48405 | 120.04 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.34265 | 104.8 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48626 | 136.69 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48605 | 130.51 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48701 | 112.55 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48696 | 112.46 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48605 | 117.86 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48626 | 113.97 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48634 | 136.77 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48615 | 130.12 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48708 | 112.79 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO->FROM | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48703 | 112.69 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48615 | 117.45 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM->TO | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48634 | 114.05 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | TO->FROM | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.59334 | 114.45 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | TO->FROM | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.5919 | 108.36 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | TO->FROM | 640302 OGALALA4 230 659134 SIDNEY___TS4 230 1 |  | 320 | 0.59362 | 103.62 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-069 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 956 | 956 | 0.0826 | 101.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 27SP | GEN-2020-084 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 956 | 956 | 0.67887 | 101.59 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 24SP | GEN-2020-069 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 956 | 956 | 0.08297 | 100.47 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 24SP | GEN-2020-084 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 956 | 956 | 0.67846 | 100.47 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4
Thermal | 02ALL | 1 | 27SP | GEN-2020-069 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 956 | 956 | 0.0826 | 100.46 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 27SP | GEN-2020-084 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 956 | 956 | 0.67887 | 100.46 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | FROM->TO | 653572 SIDNEY 7 115 659817 COLTON__-TS7 115 1 | 107 | 107 | 0.10763 | 101.27 | 640252 KEYSTON3 345 659425 SD.LS-KS-MB3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | FROM->TO | 653572 SIDNEY 7 115 659817 COLTON__-TS7 115 1 | 107 | 107 | 0.10763 | 100.95 | 659133 SIDNEY__-MB3 345 659425 SD.LS-KS-MB3 345 Z
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | FROM->TO | 653572 SIDNEY 7 115 659817 COLTON__-TS7 115 1 | 107 | 107 | 0.10763 | 100.93 | P14:345:UMZ:# 7214 #:: PROPER TAKE LINE WITH SIDNEY-KEYSTONE LINE REACTOR:EHV:
Thermal | 02NR | 1 | 27L | N/A | " | None |  |  |  |  | None
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74011 | 100.92 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74011 | 100.92 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.1203 | 100.92 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0812 | 100.92 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05213 | 116.06 | 300739 7BLACKBERRY 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05213 | 116.06 | 300739 7BLACKBERRY 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.7647 | 116.06 | 300739 7BLACKBERRY 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.7647 | 116.06 | 300739 7BLACKBERRY 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.27176 | 116.06 | 300739 7BLACKBERRY 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09698 | 116.06 | 300739 7BLACKBERRY 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0508 | 113.95 | 300739 7BLACKBERRY 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0508 | 113.95 | 300739 7BLACKBERRY 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76338 | 113.95 | 300739 7BLACKBERRY 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76338 | 113.95 | 300739 7BLACKBERRY 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.27044 | 113.95 | 300739 7BLACKBERRY 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09565 | 113.95 | 300739 7BLACKBERRY 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-079 | TO->FROM | 505486 NEO SPA5 161 547472 TIP292 5 161 1 |  | 222 | 0.11968 | 103.77 | 505486 NEO SPA5 161 505488 CARTHAG5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-088 | TO->FROM | 505486 NEO SPA5 161 547472 TIP292 5 161 1 |  | 222 | 0.09708 | 103.77 | 505486 NEO SPA5 161 505488 CARTHAG5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-079 | TO->FROM | 505486 NEO SPA5 161 547472 TIP292 5 161 1 |  | 222 | 0.11918 | 103.95 | 505486 NEO SPA5 161 505488 CARTHAG5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-088 | TO->FROM | 505486 NEO SPA5 161 547472 TIP292 5 161 1 |  | 222 | 0.09657 | 103.95 | 505486 NEO SPA5 161 505488 CARTHAG5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-088 | FROM->TO | 547479 LAR382 5 161 547480 MON383 5 161 1 |  | 223 | 0.40891 | 101.18 | 505492 SPRGFLD5 161 547479 LAR382 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73989 | 100.42 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73989 | 100.42 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11713 | 100.42 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.08353 | 100.42 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05224 | 101.08 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05103 | 101.08 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05224 | 101.08 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73073 | 101.08 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73073 | 101.08 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11294 | 101.08 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.08585 | 101.08 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06195 | 110.86 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05821 | 110.86 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06195 | 110.86 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.75653 | 110.86 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.75653 | 110.86 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.10237 | 110.86 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1195 | 0.84443 | 123.97 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1195 | 0.55894 | 123.97 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1195 | 0.55894 | 123.97 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.14752 | 108.23 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.41354 | 108.23 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | ASGI-2020-001 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.05467 | 108.23 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | ASGI-2020-003 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.05213 | 108.23 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.41354 | 108.23 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.08282 | 108.23 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.08282 | 108.23 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-072 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.05377 | 108.23 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.07782 | 108.23 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0517 | 102.53 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05022 | 102.53 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0517 | 102.53 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73869 | 102.53 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73869 | 102.53 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11067 | 102.53 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09634 | 102.53 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07051 | 117.35 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06451 | 117.35 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07051 | 117.35 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76858 | 117.35 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76858 | 117.35 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.12778 | 117.35 | 532793 NEOSHO 7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05224 | 101.99 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05103 | 101.99 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05224 | 101.99 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73073 | 101.99 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73073 | 101.99 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11294 | 101.99 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.08585 | 101.99 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06195 | 111.77 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05821 | 111.77 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06195 | 111.77 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.75653 | 111.77 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.75653 | 111.77 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.10237 | 111.77 | 532796 WICHITA7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05277 | 111.25 | 532797 WOLFCRK7 345 3WXFMR WOLF CREEK TX-6 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05277 | 111.25 | 532797 WOLFCRK7 345 3WXFMR WOLF CREEK TX-6 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76632 | 111.25 | 532797 WOLFCRK7 345 3WXFMR WOLF CREEK TX-6 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76632 | 111.25 | 532797 WOLFCRK7 345 3WXFMR WOLF CREEK TX-6 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09837 | 111.25 | 532797 WOLFCRK7 345 3WXFMR WOLF CREEK TX-6 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05213 | 110.56 | 532797 WOLFCRK7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05213 | 110.56 | 532797 WOLFCRK7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.7647 | 110.56 | 532797 WOLFCRK7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.7647 | 110.56 | 532797 WOLFCRK7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09698 | 110.56 | 532797 WOLFCRK7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0508 | 108.44 | 532797 WOLFCRK7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0508 | 108.44 | 532797 WOLFCRK7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76338 | 108.44 | 532797 WOLFCRK7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76338 | 108.44 | 532797 WOLFCRK7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09565 | 108.44 | 532797 WOLFCRK7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73752 | 100.79 | 532798 VIOLA 7 345 588364 G16-153-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73752 | 100.79 | 532798 VIOLA 7 345 588364 G16-153-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11328 | 100.79 | 532798 VIOLA 7 345 588364 G16-153-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07962 | 100.79 | 532798 VIOLA 7 345 588364 G16-153-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78448 | 101.91 | 532799 WAVERLY7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78448 | 101.91 | 532799 WAVERLY7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.1614 | 101.91 | 532799 WAVERLY7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85948 | 125.66 | 532799 WAVERLY7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85948 | 125.66 | 532799 WAVERLY7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05277 | 110.91 | 533626 BURLJCT2 69.0 533653 WOLFCRK2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05277 | 110.91 | 533626 BURLJCT2 69.0 533653 WOLFCRK2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76632 | 110.91 | 533626 BURLJCT2 69.0 533653 WOLFCRK2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76632 | 110.91 | 533626 BURLJCT2 69.0 533653 WOLFCRK2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09837 | 110.91 | 533626 BURLJCT2 69.0 533653 WOLFCRK2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0547 | 111.08 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0519 | 111.08 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0547 | 111.08 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76559 | 111.08 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76559 | 111.08 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.10112 | 111.08 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 |  | 334 | 0.06691 | 118.09 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 |  | 334 | 0.15105 | 118.09 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 |  | 334 | 0.06691 | 118.09 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 |  | 334 | 0.06753 | 118.63 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 |  | 334 | 0.15144 | 118.63 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 |  | 334 | 0.06753 | 118.63 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.15085 | 102.55 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.08915 | 102.55 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.15085 | 102.55 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.05704 | 102.55 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06285 | 102.55 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06285 | 102.55 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06286 | 102.55 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.1504 | 102.55 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06 | 111 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05065 | 111 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06 | 111 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76478 | 111 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76478 | 111 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09916 | 111 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74126 | 101.9 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74126 | 101.9 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11888 | 101.9 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09486 | 101.9 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76823 | 113.19 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76823 | 113.19 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11447 | 113.19 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO->FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.73762 | 111.91 | 542966 WGARDNR5 161 543077 PLSTVAL5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO->FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.34019 | 111.91 | 542966 WGARDNR5 161 543077 PLSTVAL5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74281 | 104.89 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74281 | 104.89 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.12002 | 104.89 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09877 | 104.89 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74185 | 100.34 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74185 | 100.34 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11906 | 100.34 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09781 | 100.34 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77064 | 117.26 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77064 | 117.26 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.1202 | 117.26 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0517 | 101.54 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05022 | 101.54 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0517 | 101.54 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73869 | 101.54 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73869 | 101.54 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11067 | 101.54 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09634 | 101.54 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07051 | 115.61 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06451 | 115.61 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07051 | 115.61 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76858 | 115.61 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76858 | 115.61 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.12778 | 115.61 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.48459 | 106.62 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.12285 | 106.62 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.12285 | 106.62 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78448 | 122.27 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78448 | 122.27 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.1614 | 122.27 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.31312 | 122.27 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78436 | 118.5 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78436 | 118.5 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.16127 | 118.5 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.31299 | 118.5 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85948 | 163.74 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85948 | 163.74 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.47635 | 163.74 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO->FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.23836 | 100.39 | 543057 BUCYRUS5 161 543068 WAGSTAF5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO->FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.73833 | 100.39 | 543057 BUCYRUS5 161 543068 WAGSTAF5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO->FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.99978 | 107.49 | 543065 CNTRVIL5 161 543650 DAKOTA_5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO->FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.99978 | 107.47 | 543065 CNTRVIL5 161 543650 DAKOTA_5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO->FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.23836 | 101.51 | 543067 CENTENL5 161 543068 WAGSTAF5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO->FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.73833 | 101.51 | 543067 CENTENL5 161 543068 WAGSTAF5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO->FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.23836 | 104.81 | 543067 CENTENL5 161 543069 PAOLA 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO->FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.73833 | 104.81 | 543067 CENTENL5 161 543069 PAOLA 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO->FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.73762 | 100.3 | 543077 PLSTVAL5 161 764400 G20-073-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO->FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.34019 | 100.3 | 543077 PLSTVAL5 161 764400 G20-073-TAP 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05198 | 108.96 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05198 | 108.96 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76385 | 108.96 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76385 | 108.96 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09685 | 108.96 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO->FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.36637 | 169.5 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO->FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.69745 | 169.5 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | TO->FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.36718 | 144.48 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-089 | TO->FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.69827 | 144.48 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO->FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.36676 | 140.67 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO->FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.69785 | 140.67 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO->FROM | 543065 CNTRVIL5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.99978 | 107.26 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO->FROM | 543065 CNTRVIL5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.99978 | 107.34 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | FROM->TO | 543065 CNTRVIL5 161 543069 PAOLA 5 161 1 |  | 255 | 0.99978 | 108.92 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | FROM->TO | 543065 CNTRVIL5 161 543069 PAOLA 5 161 1 |  | 255 | 0.99978 | 109.11 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73951 | 100.84 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73951 | 100.84 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11871 | 100.84 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.08221 | 100.84 | P12:345:AECI:SPRTSMN-GRDA1:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-079 | TO->FROM | 505486 NEO SPA5 161 547472 TIP292 5 161 1 |  | 222 | 0.10934 | 100.12 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-079 | TO->FROM | 505486 NEO SPA5 161 547472 TIP292 5 161 1 |  | 222 | 0.10911 | 100.25 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73825 | 100.57 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73825 | 100.57 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11616 | 100.57 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.08112 | 100.57 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85948 | 115.7 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85948 | 115.7 | P12:345:KCPL-WERE:LACYGNE-WAVERLY-WAVERLYWIND:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1195 | 0.8455 | 103.46 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1195 | 0.2134 | 103.46 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 |  | 1195 | 0.2134 | 103.46 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-072 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05079 | 118.45 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06054 | 118.45 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06058 | 118.45 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06054 | 118.45 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73731 | 118.45 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73731 | 118.45 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05158 | 118.45 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.15807 | 118.45 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11278 | 118.45 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05894 | 112.49 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05898 | 112.49 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05894 | 112.49 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73571 | 112.49 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73571 | 112.49 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.15647 | 112.49 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11118 | 112.49 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-072 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05337 | 138.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.08037 | 138.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0763 | 138.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.08037 | 138.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77669 | 138.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77669 | 138.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | ASGI-2020-001 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05382 | 138.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | ASGI-2020-003 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05112 | 138.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.14633 | 138.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85948 | 115.67 | P12:345:WERE:WAVS-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85948 | 115.67 | P12:345:WERE:WAVS-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05277 | 110.9 | P12:69:WERE:ATHE-WOLF-69:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05277 | 110.9 | P12:69:WERE:ATHE-WOLF-69:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76632 | 110.9 | P12:69:WERE:ATHE-WOLF-69:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76632 | 110.9 | P12:69:WERE:ATHE-WOLF-69:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09837 | 110.9 | P12:69:WERE:ATHE-WOLF-69:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-079 | TO->FROM | 505486 NEO SPA5 161 547472 TIP292 5 161 1 |  | 222 | 0.1093 | 100.17 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-079 | TO->FROM | 505486 NEO SPA5 161 547472 TIP292 5 161 1 |  | 222 | 0.10907 | 100.31 | P23:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74236 | 101.13 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74236 | 101.13 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.12236 | 101.13 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.10411 | 101.13 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76956 | 112.46 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76956 | 112.46 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.12458 | 112.46 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.10274 | 109.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.09001 | 109.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.10274 | 109.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-071 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.0722 | 109.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.0562 | 109.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.0562 | 109.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06256 | 109.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.05204 | 109.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.13538 | 109.24 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.10697 | 100.63 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.09424 | 100.63 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-052 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.05253 | 100.63 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.10697 | 100.63 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-071 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.07642 | 100.63 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06042 | 100.63 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06042 | 100.63 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-089 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06679 | 100.63 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.05626 | 100.63 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.1396 | 100.63 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.10552 | 111.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.09198 | 111.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.10552 | 111.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.07508 | 111.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06353 | 111.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06353 | 111.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06134 | 111.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.13981 | 111.03 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74321 | 105.46 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74321 | 105.46 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.12034 | 105.46 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0997 | 105.46 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74228 | 100.93 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74228 | 100.93 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.11941 | 100.93 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09876 | 100.93 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77135 | 118.16 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77135 | 118.16 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.1217 | 118.16 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.48458 | 106.49 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.12284 | 106.49 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.12284 | 106.49 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78461 | 122.69 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78461 | 122.69 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.16192 | 122.69 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.31342 | 122.69 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78448 | 118.84 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78448 | 118.84 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.16179 | 118.84 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.3133 | 118.84 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85948 | 163.74 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85948 | 163.74 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.47637 | 163.74 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85948 | 115.7 | P23:345:WERE:WAVS-BKRS:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85948 | 115.7 | P23:345:WERE:WAVS-BKRS:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74001 | 100.38 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74001 | 100.38 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.1173 | 100.38 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO->FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.08372 | 100.38 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 27SP | GEN-2020-079 | TO->FROM | 505486 NEO SPA5 161 547472 TIP292 5 161 1 |  | 222 | 0.1093 | 100.17 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-079 | TO->FROM | 505486 NEO SPA5 161 547472 TIP292 5 161 1 |  | 222 | 0.10907 | 100.31 | P42:345:GRDA:TONNECE CB9580:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-079 | TO->FROM | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 | 167 | 167 | 0.06108 | 103.99 | 547479 LAR382 5 161 547480 MON383 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-088 | TO->FROM | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 | 167 | 167 | 0.30695 | 103.99 | 547479 LAR382 5 161 547480 MON383 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | TO->FROM | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 | 167 | 167 | 0.36676 | 103.99 | 547479 LAR382 5 161 547480 MON383 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-089 | TO->FROM | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 | 167 | 167 | 0.69785 | 103.99 | 547479 LAR382 5 161 547480 MON383 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | FROM->TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 160 | 189 | 0.10781 | 109.29 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | FROM->TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 160 | 189 | 0.56354 | 109.29 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | FROM->TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 160 | 189 | 0.10783 | 109 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | FROM->TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 160 | 189 | 0.56356 | 109 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | FROM->TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 160 | 189 | 0.10734 | 107.02 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-089 | FROM->TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 160 | 189 | 0.56307 | 107.02 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | FROM->TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 160 | 189 | 0.10737 | 106.94 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-089 | FROM->TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 160 | 189 | 0.56311 | 106.94 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | FROM->TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 160 | 189 | 0.10857 | 105.99 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | FROM->TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 160 | 189 | 0.56345 | 105.99 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | FROM->TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 160 | 189 | 0.10859 | 105.59 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | FROM->TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 160 | 189 | 0.56347 | 105.59 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1
Thermal | 03NR | 1 | 27L | N/A | " | None |  |  |  |  | None
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 525832 TUCO_INT 7 345 997627 UPDATE LATER 230 1 |  | 559 | 0.06746 | 126.14 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 525832 TUCO_INT 7 345 997627 UPDATE LATER 230 1 |  | 559 | 0.08544 | 126.14 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 525832 TUCO_INT 7 345 997627 UPDATE LATER 230 1 |  | 559 | 0.0534 | 126.14 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 525832 TUCO_INT 7 345 997627 UPDATE LATER 230 1 |  | 559 | 0.05226 | 126.14 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 525832 TUCO_INT 7 345 997627 UPDATE LATER 230 1 |  | 559 | 0.06746 | 126.14 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 525832 TUCO_INT 7 345 997627 UPDATE LATER 230 1 |  | 559 | 0.08544 | 126.14 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.06783 | 129.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.08476 | 129.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.0543 | 129.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.05265 | 129.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.06783 | 129.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.08476 | 129.46 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 525830 TUCO_INT 6 230 997627 UPDATE LATER 230 1 |  | 559 | 0.06746 | 128.38 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 525830 TUCO_INT 6 230 997627 UPDATE LATER 230 1 |  | 559 | 0.08544 | 128.38 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 525830 TUCO_INT 6 230 997627 UPDATE LATER 230 1 |  | 559 | 0.0534 | 128.38 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 525830 TUCO_INT 6 230 997627 UPDATE LATER 230 1 |  | 559 | 0.05226 | 128.38 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 525830 TUCO_INT 6 230 997627 UPDATE LATER 230 1 |  | 559 | 0.06746 | 128.38 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 525830 TUCO_INT 6 230 997627 UPDATE LATER 230 1 |  | 559 | 0.08544 | 128.38 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.06783 | 131.52 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.08476 | 131.52 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.0543 | 131.52 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.05265 | 131.52 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.06783 | 131.52 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.08476 | 131.52 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1 |  | 169 | 1 | 117.44 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27L | GEN-2020-016 | TO->FROM | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1 |  | 169 | 1 | 117.29 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1 |  | 169 | 1 | 117.44 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 521106 GRNDFLD4 138 997736 GRNDFLD 69.0 1 |  | 56 | 0.2818 | 105.79 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27L | GEN-2020-016 | TO->FROM | 521106 GRNDFLD4 138 997734 GRNDFLD 69.0 1 |  | 56 | 0.27958 | 132.63 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 521106 GRNDFLD4 138 997734 GRNDFLD 69.0 1 |  | 56 | 0.28035 | 110.28 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-016 | TO->FROM | 521106 GRNDFLD4 138 997734 GRNDFLD 69.0 1 |  | 56 | 0.2802 | 114.59 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 169 | 1 | 117.43 | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27L | GEN-2020-016 | TO->FROM | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 169 | 1 | 117.29 | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 169 | 1 | 117.42 | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27L | GEN-2020-016 | TO->FROM | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 169 | 0.81563 | 118.39 | P12:138:WFEC:ANADRKO_CHRYRD::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 520926 GRANFLD2 69.0 997736 GRNDFLD 69.0 1 |  | 56 | 0.2818 | 107.24 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27L | GEN-2020-016 | TO->FROM | 520926 GRANFLD2 69.0 997734 GRNDFLD 69.0 1 |  | 56 | 0.27958 | 135.5 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 520926 GRANFLD2 69.0 997734 GRNDFLD 69.0 1 |  | 56 | 0.28035 | 111.84 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-016 | TO->FROM | 520926 GRANFLD2 69.0 997734 GRNDFLD 69.0 1 |  | 56 | 0.2802 | 116.04 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27L | GEN-2020-016 | TO->FROM | 520814 ANADARK4 138 521129 CHERRYRD 4 138 1 |  | 169 | 0.71451 | 102.8 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 |  | 283 | 0.08821 | 108.76 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 |  | 283 | 0.0983 | 108.76 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 |  | 283 | 0.11792 | 108.76 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 520508 CLVLDSW4 138 520814 ANADARK4 138 1 |  | 283 | 0.08821 | 108.76 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515802 GRACMNT4 138 997779 GRACMNT3 138 3 |  | 478 | 0.0896 | 107.1 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515802 GRACMNT4 138 997779 GRACMNT3 138 3 |  | 478 | 0.0937 | 105.1 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 515802 GRACMNT4 138 997779 GRACMNT3 138 3 |  | 478 | 0.23164 | 107.1 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 515802 GRACMNT4 138 997779 GRACMNT3 138 3 |  | 478 | 0.24135 | 105.1 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 515802 GRACMNT4 138 997779 GRACMNT3 138 3 |  | 478 | 0.05769 | 107.1 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 515802 GRACMNT4 138 997779 GRACMNT3 138 3 |  | 478 | 0.0612 | 105.1 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515802 GRACMNT4 138 997779 GRACMNT3 138 3 |  | 478 | 0.0896 | 107.1 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515802 GRACMNT4 138 997779 GRACMNT3 138 3 |  | 478 | 0.0937 | 105.1 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 515802 GRACMNT4 138 997779 GRACMNT3 138 3 |  | 478 | 0.23164 | 107.1 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 515802 GRACMNT4 138 997779 GRACMNT3 138 3 |  | 478 | 0.24135 | 105.1 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05341 | 125.27 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.13739 | 125.27 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.0563 | 125.27 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05341 | 125.27 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.13739 | 125.27 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515800 GRACMNT7 345 997779 GRACMNT3 138 3 |  | 478 | 0.0896 | 105.77 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515800 GRACMNT7 345 997779 GRACMNT3 138 3 |  | 478 | 0.0937 | 103.77 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 515800 GRACMNT7 345 997779 GRACMNT3 138 3 |  | 478 | 0.23164 | 105.77 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 515800 GRACMNT7 345 997779 GRACMNT3 138 3 |  | 478 | 0.24135 | 103.77 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 515800 GRACMNT7 345 997779 GRACMNT3 138 3 |  | 478 | 0.05769 | 105.77 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 515800 GRACMNT7 345 997779 GRACMNT3 138 3 |  | 478 | 0.0612 | 103.77 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515800 GRACMNT7 345 997779 GRACMNT3 138 3 |  | 478 | 0.0896 | 105.77 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515800 GRACMNT7 345 997779 GRACMNT3 138 3 |  | 478 | 0.0937 | 103.77 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 515800 GRACMNT7 345 997779 GRACMNT3 138 3 |  | 478 | 0.23164 | 105.77 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 515800 GRACMNT7 345 997779 GRACMNT3 138 3 |  | 478 | 0.24135 | 103.77 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10372 | 105.69 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10163 | 105.61 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10372 | 119.25 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10163 | 119.05 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.0696 | 112.38 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.0682 | 110.4 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07961 | 108.69 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07742 | 105.24 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10371 | 119.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.05725 | 112.38 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.05641 | 110.4 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10162 | 119.02 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10371 | 119.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10162 | 119.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10372 | 105.69 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10163 | 105.61 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10372 | 119.25 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10163 | 119.05 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.0696 | 112.38 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.0682 | 110.4 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07961 | 108.69 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07742 | 105.24 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10371 | 119.22 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10162 | 119.02 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10371 | 119.22 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10162 | 119.02 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515138 CARTER 4 138 515171 CHIKSAW4 138 1 |  | 191 | 0.05478 | 116.88 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515138 CARTER 4 138 515171 CHIKSAW4 138 1 |  | 191 | 0.05478 | 116.88 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10372 | 110.88 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10163 | 111.13 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10372 | 124.53 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10163 | 124.7 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.0696 | 117.53 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.0682 | 115.9 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07961 | 113.84 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07742 | 110.72 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10371 | 124.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.05725 | 117.53 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.05641 | 115.9 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10162 | 124.67 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10371 | 124.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10162 | 124.67 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10372 | 110.88 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10163 | 111.13 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10372 | 124.53 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10163 | 124.7 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.0696 | 117.53 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.0682 | 115.9 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07961 | 113.84 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07742 | 110.72 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10371 | 124.5 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10162 | 124.67 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10371 | 124.5 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.10162 | 124.67 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 997852 SUNNYSD3 138 3 |  | 330 | 0.10801 | 111.2 | P13:138-345:OKGE:BKRBKR_3W045::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 997852 SUNNYSD3 138 3 |  | 330 | 0.10523 | 109.19 | P13:138-345:OKGE:BKRBKR_3W045::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 997852 SUNNYSD3 138 3 |  | 330 | 0.10801 | 111.2 | P13:138-345:OKGE:BKRBKR_3W045::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 997852 SUNNYSD3 138 3 |  | 330 | 0.10523 | 109.19 | P13:138-345:OKGE:BKRBKR_3W045::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 122.98 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 123.04 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 123.26 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146.52 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146.99 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146.52 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 147 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146.52 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 147 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 122.98 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 123.04 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 123.26 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146.52 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146.99 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146.52 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 147 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 146.52 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 |  | 1195 | 1 | 147 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 997852 SUNNYSD3 138 3 |  | 330 | 0.10801 | 112.7 | P13:138-345:OKGE:BKRBKR_3W045::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 997852 SUNNYSD3 138 3 |  | 330 | 0.10523 | 110.22 | P13:138-345:OKGE:BKRBKR_3W045::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 997852 SUNNYSD3 138 3 |  | 330 | 0.10801 | 112.7 | P13:138-345:OKGE:BKRBKR_3W045::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 997852 SUNNYSD3 138 3 |  | 330 | 0.10523 | 110.22 | P13:138-345:OKGE:BKRBKR_3W045::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.05725 | 127.99 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.05641 | 126.69 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07274 | 105.94 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07102 | 102.61 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07212 | 109.19 | 515164 ROCKYPT4 138 515172 SPRNDAL4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07124 | 109.07 | 515164 ROCKYPT4 138 515172 SPRNDAL4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10372 | 121.42 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10163 | 121.91 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10372 | 135.17 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10163 | 135.69 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06782 | 101.94 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06628 | 106.11 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06507 | 106.38 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.0696 | 127.99 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.0682 | 126.69 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06572 | 105.68 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06452 | 105.42 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06782 | 101.87 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07961 | 124.37 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07742 | 121.51 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06533 | 101.02 | P12:138:OKGE:BKRBKR249::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06889 | 100.5 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06782 | 101.87 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07086 | 102.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06874 | 101.76 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10371 | 135.14 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10162 | 135.66 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07274 | 105.94 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07102 | 102.61 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07212 | 109.19 | 515164 ROCKYPT4 138 515172 SPRNDAL4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07124 | 109.07 | 515164 ROCKYPT4 138 515172 SPRNDAL4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10372 | 121.42 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10163 | 121.91 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10372 | 135.17 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10163 | 135.69 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06782 | 101.94 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06628 | 106.11 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06507 | 106.38 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.0696 | 127.99 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.0682 | 126.69 | P13:138-345:OKGE:BKRBKR_3W013::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06572 | 105.68 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06452 | 105.42 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06782 | 101.87 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07961 | 124.37 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07742 | 121.51 | P12:138:OKGE:BKRBKR257::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06533 | 101.02 | P12:138:OKGE:BKRBKR249::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06889 | 100.5 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06782 | 101.87 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07086 | 102.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06874 | 101.76 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10371 | 135.14 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10162 | 135.66 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06889 | 100.5 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06782 | 101.87 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07086 | 102.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06874 | 101.76 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10371 | 135.14 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10162 | 135.66 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06782 | 101.87 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06889 | 100.5 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06782 | 101.87 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.07086 | 102.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06874 | 101.76 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10371 | 135.14 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.10162 | 135.66 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 222 | 0.06782 | 101.87 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 194 |  | 0.05804 | 102.22 | System Intact
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 194 |  | 0.05662 | 100.62 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 194 |  | 0.05804 | 102.22 | System Intact
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 194 |  | 0.05662 | 100.62 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05878 | 101.73 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05927 | 104.49 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05877 | 101.71 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05927 | 104.46 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05877 | 101.71 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05927 | 104.46 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05878 | 101.73 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05927 | 104.49 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05877 | 101.71 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05927 | 104.46 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05877 | 101.71 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515129 RATLIFF4 138 515561 CARTRCO4 138 1 |  | 177 | 0.05927 | 104.46 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.16723 | 102.08 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.1664 | 101.05 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.16723 | 101.91 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.1664 | 100.9 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.16723 | 101.91 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.1664 | 100.9 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.17084 | 103.38 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.17195 | 102.93 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.16723 | 101.91 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.1664 | 100.9 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.17084 | 103.38 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.17195 | 102.93 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.16723 | 101.91 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.1664 | 100.9 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 102.08 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 101.05 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 101.91 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 100.9 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 101.91 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 100.9 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07695 | 103.38 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07877 | 102.93 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 101.91 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 100.9 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07695 | 103.38 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07877 | 102.93 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 101.91 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 100.9 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 102.08 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 101.05 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 101.91 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 100.9 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 101.91 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 100.9 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07695 | 103.38 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07877 | 102.93 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 101.91 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 100.9 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07695 | 103.38 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07877 | 102.93 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 101.91 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 100.9 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.16723 | 114.21 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.1664 | 113.02 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.16723 | 114.01 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.1664 | 112.84 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.14467 | 100.72 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.16723 | 114.01 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.1664 | 112.85 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.17084 | 115.73 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.17195 | 115.2 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.11881 | 101.61 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.14467 | 100.72 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.16723 | 114.01 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.1664 | 112.85 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.17084 | 115.73 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.17195 | 115.2 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.11881 | 101.61 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.16723 | 114.01 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.1664 | 112.84 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.06893 | 100.72 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.06893 | 100.72 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.0572 | 100.72 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.0572 | 100.72 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07429 | 114.21 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07279 | 113.02 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07429 | 114.01 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07279 | 112.84 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.06383 | 100.72 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07429 | 114.01 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07279 | 112.85 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07695 | 115.73 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07877 | 115.2 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.0654 | 101.61 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.06383 | 100.72 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07429 | 114.01 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07279 | 112.85 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07695 | 115.73 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07877 | 115.2 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.0654 | 101.61 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07429 | 114.01 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07279 | 112.84 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07429 | 114.21 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07279 | 113.02 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07429 | 114.01 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07279 | 112.84 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.06383 | 100.72 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07429 | 114.01 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07279 | 112.85 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07695 | 115.73 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07877 | 115.2 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.0654 | 101.61 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.06383 | 100.72 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07429 | 114.01 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07279 | 112.85 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07695 | 115.73 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07877 | 115.2 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.0654 | 101.61 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07429 | 114.01 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07279 | 112.84 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.17084 | 115.73 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07695 | 115.73 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 |  | 191 | 0.07695 | 115.73 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28397 | 119.18 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28463 | 119.66 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28479 | 114.96 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28397 | 119.29 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28463 | 119.77 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28479 | 115.07 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.23216 | 104.08 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.23232 | 107.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28397 | 119.29 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28463 | 119.77 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28479 | 115.07 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28829 | 119.95 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28869 | 121.01 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28869 | 114.22 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.23216 | 104.08 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.23232 | 107.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28397 | 119.29 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28463 | 119.77 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28479 | 115.07 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28829 | 119.95 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28869 | 121.01 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28869 | 114.22 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28397 | 119.29 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28463 | 119.77 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.28479 | 115.07 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.08466 | 104.08 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.08452 | 107.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.08466 | 104.08 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.08452 | 107.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.06964 | 104.08 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.06948 | 107.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.06964 | 104.08 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.06948 | 107.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.18 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.66 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 114.96 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.29 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.77 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 115.07 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.09703 | 104.08 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.09711 | 107.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.29 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.77 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 115.07 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12441 | 119.95 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 121.01 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 114.22 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.09703 | 104.08 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.09711 | 107.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.29 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.77 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 115.07 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12441 | 119.95 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 121.01 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 114.22 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.29 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.77 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 115.07 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.05082 | 104.08 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.05064 | 107.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.18 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.66 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 114.96 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.29 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.77 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 115.07 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.09703 | 104.08 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.09711 | 107.49 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.29 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.77 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 115.07 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12441 | 119.95 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 121.01 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 114.22 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.09703 | 104.08 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.09711 | 107.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.29 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.77 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 115.07 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12441 | 119.95 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 121.01 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 114.22 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.29 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.77 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 115.07 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.05082 | 104.08 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO->FROM | 514809 JOHNCO 7 345 997891 JOHNCOT3 138 3 |  | 478 | 0.05064 | 107.49 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28397 | 119.8 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28463 | 119.74 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28479 | 114.83 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28397 | 119.84 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28463 | 119.79 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28479 | 114.88 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.23216 | 104.68 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.23232 | 107.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28397 | 119.84 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28463 | 119.79 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28479 | 114.88 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28829 | 120.48 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28869 | 120.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28869 | 113.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.23216 | 104.68 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.23232 | 107.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28397 | 119.84 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28463 | 119.79 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28479 | 114.88 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28829 | 120.48 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28869 | 120.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28869 | 113.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28397 | 119.84 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28463 | 119.79 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.28479 | 114.88 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.08466 | 104.68 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.08452 | 107.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.08466 | 104.68 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.08452 | 107.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.06964 | 104.68 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.06948 | 107.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.06964 | 104.68 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.06948 | 107.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.8 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.74 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 114.83 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.84 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.79 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 114.88 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.09703 | 104.68 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.09711 | 107.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.84 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.79 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 114.88 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12441 | 120.48 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 120.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 113.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.09703 | 104.68 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.09711 | 107.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.84 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.79 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 114.88 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12441 | 120.48 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 120.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 113.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.84 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.79 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 114.88 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.05082 | 104.68 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.05064 | 107.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.8 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.74 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 114.83 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.84 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.79 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 114.88 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.09703 | 104.68 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.09711 | 107.54 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.84 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.79 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 114.88 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12441 | 120.48 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 120.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 113.99 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.09703 | 104.68 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.09711 | 107.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.84 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.79 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 114.88 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12441 | 120.48 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 120.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12464 | 113.99 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.1204 | 119.84 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12092 | 119.79 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.12108 | 114.88 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.05082 | 104.68 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO->FROM | 514808 JOHNCO 4 138 997891 JOHNCOT3 138 3 |  | 478 | 0.05064 | 107.54 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.16723 | 102.93 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.1664 | 101.9 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.16723 | 102.76 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.1664 | 101.75 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.16723 | 102.76 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.1664 | 101.75 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.17084 | 104.24 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.17195 | 103.78 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.16723 | 102.76 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.1664 | 101.75 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.17084 | 104.24 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.17195 | 103.78 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.16723 | 102.76 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.1664 | 101.75 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 102.93 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 101.9 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 102.76 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 101.75 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 102.76 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 101.75 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07695 | 104.24 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07877 | 103.78 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 102.76 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 101.75 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07695 | 104.24 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07877 | 103.78 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 102.76 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 101.75 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 102.93 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 101.9 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 102.76 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 101.75 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 102.76 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 101.75 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07695 | 104.24 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07877 | 103.78 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 102.76 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 101.75 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07695 | 104.24 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07877 | 103.78 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07429 | 102.76 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 |  | 222 | 0.07279 | 101.75 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-023 | TO->FROM | 514715 WOODRNG7 345 997902 WOODRNG2 138 2 |  | 359 | 0.255 | 125.92 | P42:345:OKGE:SB_WONG7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-023 | TO->FROM | 514715 WOODRNG7 345 997902 WOODRNG2 138 2 |  | 359 | 0.25596 | 125.11 | P42:345:OKGE:SB_WONG7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-023 | TO->FROM | 514715 WOODRNG7 345 997902 WOODRNG2 138 2 |  | 359 | 0.25611 | 113.43 | P42:345:OKGE:SB_WONG7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-023 | TO->FROM | 514714 WOODRNG4 138 997902 WOODRNG2 138 2 |  | 359 | 0.255 | 126.92 | P42:345:OKGE:SB_WONG7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-023 | TO->FROM | 514714 WOODRNG4 138 997902 WOODRNG2 138 2 |  | 359 | 0.25596 | 126.01 | P42:345:OKGE:SB_WONG7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-023 | TO->FROM | 514714 WOODRNG4 138 997902 WOODRNG2 138 2 |  | 359 | 0.25611 | 114.46 | P42:345:OKGE:SB_WONG7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 113.64 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 113.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 113.64 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 113.65 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05032 | 106.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0631 | 117.93 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.06294 | 117.77 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.06288 | 117.67 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.06282 | 117.63 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.06288 | 100.41 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.06282 | 100.12 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.05032 | 106.61 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.0631 | 117.93 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.06294 | 117.77 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.06288 | 117.67 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.06282 | 117.63 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.06288 | 100.41 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 |  | 171 | 0.06282 | 100.12 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO->FROM | 511475 SNYDER-2 69.0 997968 SNYDER 69.0 1 |  | 75 | 0.16092 | 142.04 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO->FROM | 511475 SNYDER-2 69.0 997968 SNYDER 69.0 1 |  | 75 | 0.16074 | 144.19 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-012 | TO->FROM | 511475 SNYDER-2 69.0 997968 SNYDER 69.0 1 |  | 75 | 0.16085 | 101.16 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 511475 SNYDER-2 69.0 997968 SNYDER 69.0 1 |  | 75 | 0.10517 | 142.04 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 511475 SNYDER-2 69.0 997968 SNYDER 69.0 1 |  | 75 | 0.10488 | 144.19 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-016 | TO->FROM | 511475 SNYDER-2 69.0 997968 SNYDER 69.0 1 |  | 75 | 0.10499 | 101.16 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO->FROM | 511475 SNYDER-2 69.0 511495 TOMSTEED2 69.0 1 |  | 35 | 0.08984 | 100.07 | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 511475 SNYDER-2 69.0 511495 TOMSTEED2 69.0 1 |  | 35 | 0.06432 | 100.07 | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.6 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.51 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.62 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.54 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.6 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.51 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.62 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.54 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1549 | 1 | 111.36 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 132.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 132.64 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 132.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 132.64 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1549 | 1 | 111.36 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.05032 | 115.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06288 | 106.88 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06282 | 106.38 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.0631 | 127.45 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06294 | 127.3 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-087 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06332 | 104.99 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06288 | 127.17 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06282 | 127.13 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-087 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06319 | 104.75 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06288 | 108.48 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06282 | 108.18 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.05032 | 115.21 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06288 | 106.88 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06282 | 106.38 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.0631 | 127.45 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06294 | 127.3 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-075 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06332 | 104.99 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06288 | 127.17 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06282 | 127.13 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-075 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06319 | 104.75 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06288 | 108.48 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 |  | 158 | 0.06282 | 108.18 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO->FROM | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1 |  | 152 | 0.14506 | 101.15 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 511446 CL-AFTP4 138 511463 HOB-JCT4 138 1 |  | 152 | 0.10506 | 101.15 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO->FROM | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1 |  | 152 | 0.14847 | 101.47 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 511446 CL-AFTP4 138 511458 ELKCTY-4 138 1 |  | 152 | 0.10764 | 101.47 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.09967 | 115.38 | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.0998 | 115.12 | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.07351 | 115.38 | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.07371 | 115.12 | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.09967 | 115.38 | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.0998 | 115.12 | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.09104 | 114.11 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.09116 | 113.56 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.09967 | 107.74 | 529298 OMPVET-4 138 529345 OMPARK-4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.07351 | 115.38 | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.07371 | 115.12 | 511440 ALTUSJT4 138 529345 OMPARK-4 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.06352 | 114.11 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.06372 | 113.56 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 511444 ROSVTAP2 69.0 511465 HOBART-2 69.0 1 |  | 35 | 0.07351 | 107.74 | 529298 OMPVET-4 138 529345 OMPARK-4 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO->FROM | 511441 ALTUSJT2 69.0 511543 TIPTN T2 69.0 1 |  | 50 | 0.08409 | 114.1 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO->FROM | 511441 ALTUSJT2 69.0 511543 TIPTN T2 69.0 1 |  | 50 | 0.08396 | 116.63 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 511441 ALTUSJT2 69.0 511543 TIPTN T2 69.0 1 |  | 50 | 0.05605 | 114.1 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 511441 ALTUSJT2 69.0 511543 TIPTN T2 69.0 1 |  | 50 | 0.05586 | 116.63 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO->FROM | 511435 SNYDER-4 138 997968 SNYDER 69.0 1 |  | 75 | 0.16092 | 141.88 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO->FROM | 511435 SNYDER-4 138 997968 SNYDER 69.0 1 |  | 75 | 0.16074 | 143.78 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-012 | TO->FROM | 511435 SNYDER-4 138 997968 SNYDER 69.0 1 |  | 75 | 0.16085 | 101.57 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 511435 SNYDER-4 138 997968 SNYDER 69.0 1 |  | 75 | 0.10517 | 141.88 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 511435 SNYDER-4 138 997968 SNYDER 69.0 1 |  | 75 | 0.10488 | 143.78 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-016 | TO->FROM | 511435 SNYDER-4 138 997968 SNYDER 69.0 1 |  | 75 | 0.10499 | 101.57 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.06986 | 115.01 | P12:69:AEPW:COMANC-2:L.E.S.-2:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO->FROM | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.06965 | 115.43 | P12:69:AEPW:COMANC-2:L.E.S.-2:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO->FROM | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.07064 | 100.14 | P12:138:WFEC:ANADRKO_CHRYRD::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05814 | 103.99 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05814 | 103.99 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.13917 | 103.99 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.13917 | 103.99 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.20089 | 103.99 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.20089 | 103.99 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05499 | 103.99 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05499 | 103.99 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.13396 | 103.99 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.13396 | 103.99 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05499 | 103.99 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 |  | 776 | 0.05499 | 103.99 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08062 | 106.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.08042 | 103.4 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08062 | 106.46 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.08042 | 103.4 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.1743 | 106.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-020 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.17414 | 103.4 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.1743 | 106.46 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-020 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.17414 | 103.4 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.2601 | 106.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-054 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.25997 | 103.4 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.2601 | 106.46 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-054 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.25997 | 103.4 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.07692 | 106.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.07682 | 103.4 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.07692 | 106.46 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.07682 | 103.4 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.07692 | 106.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.07682 | 103.4 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.07692 | 106.46 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.07682 | 103.4 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-081 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.26664 | 103.4 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-081 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.26664 | 103.4 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.26662 | 106.46 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO->FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.26662 | 106.46 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04NR | 1 | 27L | N/A | " | None |  |  |  |  | None
Thermal | 05ALL | 1 | 24SP | GEN-2020-009 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 |  | 0.03318 | 106.23 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2020-009 | TO->FROM | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 121 |  | 0.03194 | 102.02 | System Intact
Thermal | 05ALL | 1 | 24SP | GEN-2020-009 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 |  | 0.03318 | 106.06 | System Intact
Thermal | 05ALL | 1 | 27SP | GEN-2020-009 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 121 |  | 0.03194 | 101.88 | System Intact
Thermal | 05NR | 1 | 27L | N/A | " | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00NR | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 00ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 00ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 00ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 00NR | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 00NR | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 01ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 01ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 01ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 01ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 01NR | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 02NR | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 03ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 03ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 03ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 03ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 03NR | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 04NR | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 05NR | 2 | 27L | N/A | None | [7 empty] | None

## Stability Analysis Results
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
01 - North | 25S | Transfer | G01_P1_Local_Fault_001 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_002 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_003 | 3 Phase fault on MATHSON7 115.00 (661019) 115 kV Bus a. Apply fault at the MATHSON7 115.00 (661019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINS2-BE7 (659195) 115.0 kV to MATHSON7 (661019) 115.0 kV Transmission Circuit #1 b.2. MATHSON7 (661019) 115.0 kV to DIXGREENRVR7 (661020) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_004 | 3 Phase fault on N ENGLN7 115.00 (661070) 115 kV Bus a. Apply fault at the N ENGLN7 115.00 (661070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTIPED-UM7 (655730) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 b.2. DICKINSN-BE7 (659125) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_005 | 3 Phase fault on ESTBMRK7 115.00 (661029) 115 kV Bus a. Apply fault at the ESTBMRK7 115.00 (661029) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK7 (652427) 115.0 kV to ESTBMRK7 (661029) 115.0 kV Transmission Circuit #1 b.2. BISEXP 7 (661009) 115.0 kV to ESTBMRK7 (661029) 115.0 kV Transmission Circuit #1 b.3. ESTBMRK7 (661029) 115.0 kV to LINTON 7 (661060) 115.0 kV Transmission Circuit #1 b.4. ESTBMRK7 (661029) 115.0 kV to 26TH&D 7 (661119) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Base | G01_P1_Local_Fault_006 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes after fault application. | Reduce acceleration factor and reduce clearing time to 3.5 cycles.
01 - North | 25S | Transfer | G01_P1_Local_Fault_006 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes after fault application. This issue is also present in the Base case. | Reduce acceleration factor and reduce clearing time to 3.5 cycles.
01 - North | 25S | Transfer | G01_P1_Local_Fault_007 | 3 Phase fault on HETINGR7 115.00 (661048) 115 kV Bus a. Apply fault at the HETINGR7 115.00 (661048) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HETINGR7 (661048) 115.0 kV to GASCOYN7 (661050) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_008 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_009 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_010 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_011 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_012 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_013 | 3 Phase fault on BAKER 7 115.00 (661005) 115 kV Bus a. Apply fault at the BAKER 7 115.00 (661005) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 7 (661005) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_014 | 3 Phase fault on HETINGR7 115.00 (661048) 115 kV Bus a. Apply fault at the HETINGR7 115.00 (661048) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HETINGR7 (661048) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_015 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_016 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_017 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_018 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_019 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_020 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_021 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_022 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_023 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_024 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_025 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_026 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_027 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_028 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_029 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 6 cycles.
01 - North | 25S | Base | G01_P1_Local_Fault_029 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduce clearing time to 6 cycles.
01 - North | 25S | Transfer | G01_P1_Local_Fault_030 | 3 Phase fault on SQBUTTE4 230.00 (657756) 230 kV Bus a. Apply fault at the SQBUTTE4 230.00 (657756) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBUTTE4 (657756) 230.0 kV to YNG2 4 (657848) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_031 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_032 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_033 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_034 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_035 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_036 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 b.5. GRE-MCHENRYT (615349) 12.5 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_037 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_038 | 3 Phase fault on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_039 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_040 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_041 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_042 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_043 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_044 | 3 Phase fault on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_045 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_046 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_047 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_048 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_049 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_050 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_051 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_052 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_053 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_054 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_055 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_056 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_057 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_058 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_059 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_060 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_061 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_062 | 3 Phase fault on SB.LS-WK-ER4230.00 (655510) 230 kV Bus a. Apply fault at the SB.LS-WK-ER4230.00 (655510) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SB.LS-WK-ER4 (655510) 230.0 kV to WHITLOCK_-RM (655765) 230.0 kV Transmission Circuit #1 b.2. WHITLOCK_-RM (655765) 230.0 kV to GLENHAM4 (661038) 230.0 kV Transmission Circuit #1 b.3. SULLYBT-ER4 (655487) 230.0 kV to SB.LS-WK-ER4 (655510) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_063 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_064 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.4. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_065 | 3 Phase fault on FAITH 7 115.00 (652243) 115 kV Bus a. Apply fault at the FAITH 7 115.00 (652243) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAITH 7 (652243) 115.0 kV to EAGLEBT7 (652476) 115.0 kV Transmission Circuit #1 b.2. FAITH 7 (652243) 115.0 kV to MAURINE7 (652480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_066 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_067 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_068 | 3 Phase fault on WOONSKT7 115.00 (652528) 115 kV Bus a. Apply fault at the WOONSKT7 115.00 (652528) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.3. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.4. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_069 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_070 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_071 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_072 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_073 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_074 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_075 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_076 | 3 Phase fault on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_077 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.KU2A_-BE9 (659204) 13.8 kV to BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV Three Winding #1 b.2. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.3. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.6. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_078 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_079 | 3 Phase fault on WATERTNCAP 4230.00 (652630) 230 kV Bus a. Apply fault at the WATERTNCAP 4230.00 (652630) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTNCAP 4 (652630) 230.0 kV Fixed Shunt Device | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_080 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_081 | 3 Phase fault on TYNDALL7 115.00 (652525) 115 kV Bus a. Apply fault at the TYNDALL7 115.00 (652525) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.4. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_082 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_083 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_084 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_085 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_086 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_087 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_088 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_089 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_090 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_091 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.2. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.3. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_092 | 3 Phase fault on PWRSLKTP-MW7115.00 (655947) 115 kV Bus a. Apply fault at the PWRSLKTP-MW7115.00 (655947) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINDAHLS-MW7 (655910) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.2. PWRSLKTP-MW7 (655947) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.3. POWERSLK-MW7 (655946) 115.0 kV to PWRSLKTP-MW7 (655947) 115.0 kV Transmission Circuit #1 b.4. PWRSLKTP-MW7 (655947) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_093 | 3 Phase fault on MOE -MW7115.00 (655900) 115 kV Bus a. Apply fault at the MOE -MW7115.00 (655900) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOE -MW7 (655900) 115.0 kV to PLSNTV_T-MW7 (655902) 115.0 kV Transmission Circuit #1 b.2. MOE -MW7 (655900) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 b.3. MOE -MW7 (655900) 115.0 kV to E.NESSON-MW7 (655965) 115.0 kV Transmission Circuit #1 b.4. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.5. ROSS -MW7 (655903) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.6. BROOKBNK-MW7 (655901) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 b.7. BROOKBNK-MW7 (655901) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_094 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_095 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 b.7. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_096 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_097 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_098 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_099 | 3 Phase fault on EAGLEBT7 115.00 (652476) 115 kV Bus a. Apply fault at the EAGLEBT7 115.00 (652476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLEBT7 (652476) 115.0 kV to OAHE 7 (652520) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_100 | 3 Phase fault on OAHE 7 115.00 (652520) 115 kV Bus a. Apply fault at the OAHE 7 115.00 (652520) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 7 (652520) 115.0 kV to IRVSIMM7 (658174) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_101 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_102 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_103 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_104 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_105 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_106 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_107 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 29 (652598) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_108 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_109 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_110 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_111 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_112 | 3 Phase fault on MOE -MW7115.00 (655900) 115 kV Bus a. Apply fault at the MOE -MW7115.00 (655900) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOE -MW7 (655900) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 b.2. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.3. MOE -MW7 (655900) 115.0 kV to PLSNTV_T-MW7 (655902) 115.0 kV Transmission Circuit #1 b.4. MOE -MW7 (655900) 115.0 kV to E.NESSON-MW7 (655965) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_113 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. AV.LS-BD-BE3 (659420) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_114 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. BD.LS-AV-BE3 (659421) 345.0 kV Fixed Shunt Device b.13. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.14. GR.LS-LO-BE3 (659423) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_115 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_116 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.4. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_117 | 3 Phase fault on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit #1 b.2. ARNEGARD-MK7 (655841) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.4. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_118 | 3 Phase fault on BISON___-GE4230.00 (659351) 230 kV Bus a. Apply fault at the BISON___-GE4230.00 (659351) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.2. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.3. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.4. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_119 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_120 | 3 Phase fault on E.BISMRK-CP7115.00 (655652) 115 kV Bus a. Apply fault at the E.BISMRK-CP7115.00 (655652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK7 (652427) 115.0 kV to E.BISMRK-CP7 (655652) 115.0 kV Transmission Circuit #1 b.2. E.BISMRK-CP7 (655652) 115.0 kV to HAYCREEK-CP7 (655689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_121 | 3 Phase fault on FAITH 7 115.00 (652243) 115 kV Bus a. Apply fault at the FAITH 7 115.00 (652243) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAITH 7 (652243) 115.0 kV to EAGLEBT7 (652476) 115.0 kV Transmission Circuit #1 b.2. FAITH 7 (652243) 115.0 kV to MAURINE7 (652480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_122 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.3. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.4. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.5. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.6. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.7. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_123 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 b.2. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 b.3. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_124 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_125 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_126 | 3 Phase fault on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Base | G01_P1_Local_Fault_127 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes after fault application. | Reduce acceleration factor and reduce clearing time to 3.5 cycles.
01 - North | 25S | Transfer | G01_P1_Local_Fault_127 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Simulation crashes after fault application. This issue is also present in the Base case. | Reduce acceleration factor and reduce clearing time to 3.5 cycles.
01 - North | 25S | Transfer | G01_P1_Local_Fault_128 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_129 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_130 | 3 Phase fault on OSBORN -MW7115.00 (655919) 115 kV Bus a. Apply fault at the OSBORN -MW7115.00 (655919) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_131 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_132 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_133 | 3 Phase fault on PWRSLKTP-MW7115.00 (655947) 115 kV Bus a. Apply fault at the PWRSLKTP-MW7115.00 (655947) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POWERSLK-MW7 (655946) 115.0 kV to PWRSLKTP-MW7 (655947) 115.0 kV Transmission Circuit #1 b.2. PWRSLKTP-MW7 (655947) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.3. PWRSLKTP-MW7 (655947) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_134 | 3 Phase fault on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_135 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_136 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_137 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_138 | 3 Phase fault on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_139 | 3 Phase fault on TWNVLYTP-MK7115.00 (655867) 115 kV Bus a. Apply fault at the TWNVLYTP-MK7115.00 (655867) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNVLYTP-MK7 (655867) 115.0 kV to TWINVLLY-MK7 (655869) 115.0 kV Transmission Circuit #1 b.2. TWNVLYTP-MK7 (655867) 115.0 kV to TBGARDEN-MK7 (655870) 115.0 kV Transmission Circuit #1 b.3. TWNVLYTP-MK7 (655867) 115.0 kV to BANKS -MK7 (655888) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_140 | 3 Phase fault on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.2. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_141 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_142 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_143 | 3 Phase fault on WOONSKT7 115.00 (652528) 115 kV Bus a. Apply fault at the WOONSKT7 115.00 (652528) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.3. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.4. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_144 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_145 | 3 Phase fault on E.SIDNEY-LY7115.00 (659186) 115 kV Bus a. Apply fault at the E.SIDNEY-LY7115.00 (659186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_146 | 3 Phase fault on TYNDALL7 115.00 (652525) 115 kV Bus a. Apply fault at the TYNDALL7 115.00 (652525) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.4. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_147 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_148 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_149 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_150 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_151 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_152 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_153 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_154 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_155 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_157 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_158 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_159 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_160 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_161 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_162 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_163 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_164 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_165 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_166 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_167 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_168 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_169 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GEN-2017-210 (761208) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_170 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_171 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_172 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_173 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_174 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_175 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_176 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_177 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GEN-2017-144 (760767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_178 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to PR BRZ 4 (648506) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_179 | 3 Phase fault on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR1 3 (648513) 345.0 kV to GRPR2 3 (648520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_180 | 3 Phase fault on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR1 3 (648513) 345.0 kV to GRPR3 3 (648527) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_181 | 3 Phase fault on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR1 3 (648513) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_183 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_184 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_185 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_186 | 3 Phase fault on FAITH 7 115.00 (652243) 115 kV Bus a. Apply fault at the FAITH 7 115.00 (652243) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAITH 7 (652243) 115.0 kV to MAURINE7 (652480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_187 | 3 Phase fault on FTTHOMP8 69.000 (652276) 69 kV Bus a. Apply fault at the FTTHOMP8 69.000 (652276) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP8 (652276) 69.0 kV to MOS-AMES-ER8 (655153) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_188 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_189 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_190 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_191 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_192 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_193 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_194 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_195 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_196 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_198 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_199 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_200 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_201 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_202 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_203 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_204 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_205 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_207 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_209 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_210 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_211 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_212 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_213 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_214 | 3 Phase fault on BISMARK7 115.00 (652427) 115 kV Bus a. Apply fault at the BISMARK7 115.00 (652427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK7 (652427) 115.0 kV to E.BISMRK-CP7 (655652) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_215 | 3 Phase fault on BISMARK7 115.00 (652427) 115 kV Bus a. Apply fault at the BISMARK7 115.00 (652427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK7 (652427) 115.0 kV to ESTBMRK7 (661029) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_216 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_217 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_218 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_219 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_220 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_221 | 3 Phase fault on HILKEN 4 230.00 (652466) 230 kV Bus a. Apply fault at the HILKEN 4 230.00 (652466) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_222 | 3 Phase fault on HEBRON 4 230.00 (652468) 230 kV Bus a. Apply fault at the HEBRON 4 230.00 (652468) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 4 (652468) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_223 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_224 | 3 Phase fault on MAURINE7 115.00 (652480) 115 kV Bus a. Apply fault at the MAURINE7 115.00 (652480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE7 (652480) 115.0 kV to SULPHUR (652491) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_225 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_226 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_227 | 3 Phase fault on WINCHESTER4 230.00 (652496) 230 kV Bus a. Apply fault at the WINCHESTER4 230.00 (652496) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINCHESTER4 (652496) 230.0 kV to CAMPBELL 4 (652499) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_228 | 3 Phase fault on MAURINE4 230.00 (652497) 230 kV Bus a. Apply fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_229 | 3 Phase fault on MAURINE4 230.00 (652497) 230 kV Bus a. Apply fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_230 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_231 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_232 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_233 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_234 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_235 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_236 | 3 Phase fault on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_237 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_238 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_239 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_240 | 3 Phase fault on HANLON 4 230.00 (652513) 230 kV Bus a. Apply fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_241 | 3 Phase fault on HANLON 4 230.00 (652513) 230 kV Bus a. Apply fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_242 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_243 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_244 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_245 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_246 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_247 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_248 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_249 | 3 Phase fault on OAHE 7 115.00 (652520) 115 kV Bus a. Apply fault at the OAHE 7 115.00 (652520) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 7 (652520) 115.0 kV to ASH TAP (652600) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_250 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_251 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_252 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to PRVLNG16 (654457) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_253 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_254 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_255 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_256 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_257 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_258 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_259 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GEN-2018-056 (762911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_260 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_261 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_262 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_263 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_264 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_265 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON_G-BE7 (659275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_266 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_267 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_268 | 3 Phase fault on WESSINGTON 4230.00 (652607) 230 kV Bus a. Apply fault at the WESSINGTON 4230.00 (652607) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_269 | 3 Phase fault on WESSINGTON 4230.00 (652607) 230 kV Bus a. Apply fault at the WESSINGTON 4230.00 (652607) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_270 | 3 Phase fault on LETCHER7 115.00 (652609) 115 kV Bus a. Apply fault at the LETCHER7 115.00 (652609) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER7 (652609) 115.0 kV to ROSWELL-ER7 (655417) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_271 | 3 Phase fault on LETCHER7 115.00 (652609) 115 kV Bus a. Apply fault at the LETCHER7 115.00 (652609) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_272 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_273 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_274 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_275 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_276 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_277 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_278 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_279 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_280 | 3 Phase fault on MOS-POLO-ER869.000 (655060) 69 kV Bus a. Apply fault at the MOS-POLO-ER869.000 (655060) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-POLO-ER8 (655060) 69.0 kV to POLO-ER8 (655233) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_281 | 3 Phase fault on MOS-POLO-ER869.000 (655060) 69 kV Bus a. Apply fault at the MOS-POLO-ER869.000 (655060) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-POLO-ER8 (655060) 69.0 kV to MILLER-ER8 (655234) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_282 | 3 Phase fault on MOS-AMES-ER869.000 (655153) 69 kV Bus a. Apply fault at the MOS-AMES-ER869.000 (655153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-AMES-ER8 (655153) 69.0 kV to MOS-HYDE-ER8 (655158) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_283 | 3 Phase fault on MOS-AMES-ER869.000 (655153) 69 kV Bus a. Apply fault at the MOS-AMES-ER869.000 (655153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-AMES-ER8 (655153) 69.0 kV to BIGBEND-ER8 (655328) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_284 | 3 Phase fault on MOS-AMES-ER869.000 (655153) 69 kV Bus a. Apply fault at the MOS-AMES-ER869.000 (655153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-AMES-ER8 (655153) 69.0 kV to AMES-ER8 (655352) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_285 | 3 Phase fault on MOS-HYDE-ER869.000 (655158) 69 kV Bus a. Apply fault at the MOS-HYDE-ER869.000 (655158) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-HYDE-ER8 (655158) 69.0 kV to NWPS8645-ER8 (655384) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_286 | 3 Phase fault on HGHMORE-ER8 69.000 (655240) 69 kV Bus a. Apply fault at the HGHMORE-ER8 69.000 (655240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HGHMORE-ER8 (655240) 69.0 kV to NWPS8645-ER8 (655384) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_287 | 3 Phase fault on CHMBRLAN-ER869.000 (655250) 69 kV Bus a. Apply fault at the CHMBRLAN-ER869.000 (655250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHMBRLAN-ER8 (655250) 69.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_288 | 3 Phase fault on GANNVALL-ER869.000 (655329) 69 kV Bus a. Apply fault at the GANNVALL-ER869.000 (655329) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GANNVALL-ER8 (655329) 69.0 kV to AMES-ER8 (655352) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_289 | 3 Phase fault on MOS-LKPL-ER869.000 (655385) 69 kV Bus a. Apply fault at the MOS-LKPL-ER869.000 (655385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-LKPL-ER8 (655385) 69.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_290 | 3 Phase fault on CRANDALL-ER7115.00 (655411) 115 kV Bus a. Apply fault at the CRANDALL-ER7115.00 (655411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_291 | 3 Phase fault on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_292 | 3 Phase fault on SULLYBT-ER4 230.00 (655487) 230 kV Bus a. Apply fault at the SULLYBT-ER4 230.00 (655487) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SULLYBT-ER4 (655487) 230.0 kV to SB.LS-WK-ER4 (655510) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_293 | 3 Phase fault on CENTIPED-UM7115.00 (655730) 115 kV Bus a. Apply fault at the CENTIPED-UM7115.00 (655730) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTIPED-UM7 (655730) 115.0 kV to HETINGR7 (661048) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_294 | 3 Phase fault on CENTIPED-UM7115.00 (655730) 115 kV Bus a. Apply fault at the CENTIPED-UM7115.00 (655730) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTIPED-UM7 (655730) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_295 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_296 | 3 Phase fault on HELMUT -LY7115.00 (655790) 115 kV Bus a. Apply fault at the HELMUT -LY7115.00 (655790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_297 | 3 Phase fault on MOUNTAIN-MK7115.00 (655830) 115 kV Bus a. Apply fault at the MOUNTAIN-MK7115.00 (655830) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNTAIN-MK7 (655830) 115.0 kV to OAKDALE -MK7 (655836) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_298 | 3 Phase fault on BLUEBUTE-MK7115.00 (655832) 115 kV Bus a. Apply fault at the BLUEBUTE-MK7115.00 (655832) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBUTE-MK7 (655832) 115.0 kV to VEEDER -MK7 (655849) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_299 | 3 Phase fault on BLUEBUTE-MK7115.00 (655832) 115 kV Bus a. Apply fault at the BLUEBUTE-MK7115.00 (655832) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBUTE-MK7 (655832) 115.0 kV to STATION8-MK7 (655865) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_300 | 3 Phase fault on LITTLKNF-MK7115.00 (655835) 115 kV Bus a. Apply fault at the LITTLKNF-MK7115.00 (655835) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTLKNF-MK7 (655835) 115.0 kV to OAKDALE -MK7 (655836) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_301 | 3 Phase fault on OAKDALE -MK7115.00 (655836) 115 kV Bus a. Apply fault at the OAKDALE -MK7115.00 (655836) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKDALE -MK7 (655836) 115.0 kV to BEARCREK-MK7 (655853) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_302 | 3 Phase fault on ELMTREE -MK7115.00 (655837) 115 kV Bus a. Apply fault at the ELMTREE -MK7115.00 (655837) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMTREE -MK7 (655837) 115.0 kV to TABLEBUT-MK7 (655858) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_303 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_304 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to NRTINDHL-MK7 (655850) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_305 | 3 Phase fault on SATHERDM-MK7115.00 (655839) 115 kV Bus a. Apply fault at the SATHERDM-MK7115.00 (655839) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SATHERDM-MK7 (655839) 115.0 kV to TRUEOIL -MK7 (655843) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_306 | 3 Phase fault on SATHERDM-MK7115.00 (655839) 115 kV Bus a. Apply fault at the SATHERDM-MK7115.00 (655839) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SATHERDM-MK7 (655839) 115.0 kV to SKAAR___-MK7 (655860) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_307 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_308 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_309 | 3 Phase fault on ARNEGARD-MK7115.00 (655841) 115 kV Bus a. Apply fault at the ARNEGARD-MK7115.00 (655841) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNEGARD-MK7 (655841) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_310 | 3 Phase fault on HAYBUTTE-MK7115.00 (655842) 115 kV Bus a. Apply fault at the HAYBUTTE-MK7115.00 (655842) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_311 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_312 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_313 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_314 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_315 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to GARDN-FB-MK7 (655895) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_316 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_317 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to BANKS -MK7 (655888) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_318 | 3 Phase fault on SWENSON -MK7115.00 (655847) 115 kV Bus a. Apply fault at the SWENSON -MK7115.00 (655847) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWENSON -MK7 (655847) 115.0 kV to BERG -MK7 (655848) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_319 | 3 Phase fault on SWENSON -MK7115.00 (655847) 115 kV Bus a. Apply fault at the SWENSON -MK7115.00 (655847) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWENSON -MK7 (655847) 115.0 kV to SNDCRKTP-MK7 (655866) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_320 | 3 Phase fault on SWENSON -MK7115.00 (655847) 115 kV Bus a. Apply fault at the SWENSON -MK7115.00 (655847) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWENSON -MK7 (655847) 115.0 kV to KEENECRN-MK7 (655896) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_321 | 3 Phase fault on BERG -MK7115.00 (655848) 115 kV Bus a. Apply fault at the BERG -MK7115.00 (655848) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG -MK7 (655848) 115.0 kV to TABLEBUT-MK7 (655858) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_322 | 3 Phase fault on BERG -MK7115.00 (655848) 115 kV Bus a. Apply fault at the BERG -MK7115.00 (655848) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG -MK7 (655848) 115.0 kV to BBCOMPTP-MK7 (655873) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_323 | 3 Phase fault on BERG -MK7115.00 (655848) 115 kV Bus a. Apply fault at the BERG -MK7115.00 (655848) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG -MK7 (655848) 115.0 kV to KEENE -MK7 (655886) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_324 | 3 Phase fault on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VEEDER -MK7 (655849) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_325 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_326 | 3 Phase fault on ROOSEVLT-MK7115.00 (655855) 115 kV Bus a. Apply fault at the ROOSEVLT-MK7115.00 (655855) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVLT-MK7 (655855) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_327 | 3 Phase fault on ROOSEVLT-MK7115.00 (655855) 115 kV Bus a. Apply fault at the ROOSEVLT-MK7115.00 (655855) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVLT-MK7 (655855) 115.0 kV to CRESTWD_-MK7 (655878) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_328 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_329 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_330 | 3 Phase fault on HORSECRK-MK7115.00 (655861) 115 kV Bus a. Apply fault at the HORSECRK-MK7115.00 (655861) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HORSECRK-MK7 (655861) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_331 | 3 Phase fault on GRAIL -MK7115.00 (655864) 115 kV Bus a. Apply fault at the GRAIL -MK7115.00 (655864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAIL -MK7 (655864) 115.0 kV to STATION8-MK7 (655865) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_332 | 3 Phase fault on TWNVLYTP-MK7115.00 (655867) 115 kV Bus a. Apply fault at the TWNVLYTP-MK7115.00 (655867) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNVLYTP-MK7 (655867) 115.0 kV to TWINVLLY-MK7 (655869) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_333 | 3 Phase fault on TWNVLYTP-MK7115.00 (655867) 115 kV Bus a. Apply fault at the TWNVLYTP-MK7115.00 (655867) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNVLYTP-MK7 (655867) 115.0 kV to TBGARDEN-MK7 (655870) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_334 | 3 Phase fault on TWNVLYTP-MK7115.00 (655867) 115 kV Bus a. Apply fault at the TWNVLYTP-MK7115.00 (655867) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNVLYTP-MK7 (655867) 115.0 kV to BANKS -MK7 (655888) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_335 | 3 Phase fault on G9______-MK7115.00 (655871) 115 kV Bus a. Apply fault at the G9______-MK7115.00 (655871) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G9______-MK7 (655871) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_336 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to BBCMPRSS-MK7 (655874) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_337 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_338 | 3 Phase fault on DPLWC___-MK7115.00 (655875) 115 kV Bus a. Apply fault at the DPLWC___-MK7115.00 (655875) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWC___-MK7 (655875) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_339 | 3 Phase fault on DPLWCTAP-MK7115.00 (655876) 115 kV Bus a. Apply fault at the DPLWCTAP-MK7115.00 (655876) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWCTAP-MK7 (655876) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_340 | 3 Phase fault on CRESTWD_-MK7115.00 (655878) 115 kV Bus a. Apply fault at the CRESTWD_-MK7115.00 (655878) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTWD_-MK7 (655878) 115.0 kV to SCHAFER -MK7 (655898) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_341 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to COYOTCHR-MK7 (655897) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_342 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to FNCYBTAP-MK7 (655899) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_343 | 3 Phase fault on DAP_____-MK7115.00 (655881) 115 kV Bus a. Apply fault at the DAP_____-MK7115.00 (655881) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAP_____-MK7 (655881) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_344 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_345 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_346 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_347 | 3 Phase fault on NRTHFORK-MK7115.00 (655885) 115 kV Bus a. Apply fault at the NRTHFORK-MK7115.00 (655885) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTHFORK-MK7 (655885) 115.0 kV to KEENE -MK7 (655886) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_348 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_349 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to HALLIDAY-MK7 (655894) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_350 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_351 | 3 Phase fault on FNCYBTAP-MK7115.00 (655899) 115 kV Bus a. Apply fault at the FNCYBTAP-MK7115.00 (655899) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNCYBTAP-MK7 (655899) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_352 | 3 Phase fault on BROOKBNK-MW7115.00 (655901) 115 kV Bus a. Apply fault at the BROOKBNK-MW7115.00 (655901) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKBNK-MW7 (655901) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_353 | 3 Phase fault on BROOKBNK-MW7115.00 (655901) 115 kV Bus a. Apply fault at the BROOKBNK-MW7115.00 (655901) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKBNK-MW7 (655901) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_354 | 3 Phase fault on ROSS -MW7115.00 (655903) 115 kV Bus a. Apply fault at the ROSS -MW7115.00 (655903) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSS -MW7 (655903) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_355 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_356 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to AUSTIN -MW7 (655912) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_357 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_358 | 3 Phase fault on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_359 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_360 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_361 | 3 Phase fault on E.NEWTWN-MW7115.00 (655907) 115 kV Bus a. Apply fault at the E.NEWTWN-MW7115.00 (655907) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_362 | 3 Phase fault on E.NEWTWN-MW7115.00 (655907) 115 kV Bus a. Apply fault at the E.NEWTWN-MW7115.00 (655907) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_363 | 3 Phase fault on E.NEWTWN-MW7115.00 (655907) 115 kV Bus a. Apply fault at the E.NEWTWN-MW7115.00 (655907) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to BIGBEND -MW7 (655960) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_364 | 3 Phase fault on E.NEWTWN-MW7115.00 (655907) 115 kV Bus a. Apply fault at the E.NEWTWN-MW7115.00 (655907) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to SATTER -MW7 (655967) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_365 | 3 Phase fault on PARSHALL-MW7115.00 (655908) 115 kV Bus a. Apply fault at the PARSHALL-MW7115.00 (655908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_366 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_367 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_368 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_369 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_370 | 3 Phase fault on RATLAKE -MW7115.00 (655929) 115 kV Bus a. Apply fault at the RATLAKE -MW7115.00 (655929) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_371 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_372 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_373 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_374 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_375 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_376 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_377 | 3 Phase fault on N.WILSTN-MW7115.00 (655936) 115 kV Bus a. Apply fault at the N.WILSTN-MW7115.00 (655936) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_378 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_379 | 3 Phase fault on FARMVL_T-MW7115.00 (655943) 115 kV Bus a. Apply fault at the FARMVL_T-MW7115.00 (655943) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_380 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_381 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_382 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_383 | 3 Phase fault on ELLISVIL-MW7115.00 (655954) 115 kV Bus a. Apply fault at the ELLISVIL-MW7115.00 (655954) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_384 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_385 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_386 | 3 Phase fault on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_387 | 3 Phase fault on SATTER -MW7115.00 (655967) 115 kV Bus a. Apply fault at the SATTER -MW7115.00 (655967) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SATTER -MW7 (655967) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_388 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_389 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_399 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_400 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_401 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to GEN-2019-037 (763703) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_402 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_403 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_404 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_405 | 3 Phase fault on DICKINSN-BE7115.00 (659125) 115 kV Bus a. Apply fault at the DICKINSN-BE7115.00 (659125) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE7 (659125) 115.0 kV to DICKINS2-BE7 (659195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_406 | 3 Phase fault on DICKINSN-BE7115.00 (659125) 115 kV Bus a. Apply fault at the DICKINSN-BE7115.00 (659125) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE7 (659125) 115.0 kV to WDICKSN7 (661024) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_407 | 3 Phase fault on DICKINSN-BE7115.00 (659125) 115 kV Bus a. Apply fault at the DICKINSN-BE7115.00 (659125) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE7 (659125) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_408 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_409 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_410 | 3 Phase fault on NRTSHORE-BE7115.00 (659141) 115 kV Bus a. Apply fault at the NRTSHORE-BE7115.00 (659141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE7 (659141) 115.0 kV to BEPCPRXCC2 7 (659580) 115.0 kV Transmission Circuit #x1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_411 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_412 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_413 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_414 | 3 Phase fault on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_CT4-5-BE7 (659154) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_415 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_416 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_417 | 3 Phase fault on CROCKER_-BE3345.00 (659165) 345 kV Bus a. Apply fault at the CROCKER_-BE3345.00 (659165) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_418 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_419 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_422 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_423 | 3 Phase fault on DICKINS2-BE7115.00 (659195) 115 kV Bus a. Apply fault at the DICKINS2-BE7115.00 (659195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINS2-BE7 (659195) 115.0 kV to MATHSON7 (661019) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_424 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_425 | 3 Phase fault on HEADRESS-CM7115.00 (659259) 115 kV Bus a. Apply fault at the HEADRESS-CM7115.00 (659259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRESS-CM7 (659259) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_426 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_427 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_429 | 3 Phase fault on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RHAME___-BE4 (659266) 230.0 kV to BOWMAN__-BE4 (659339) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | 1 - Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. 2- Reclosing removed. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25S | Transfer | G01_P1_Local_Fault_430 | 3 Phase fault on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RHAME___-BE4 (659266) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_431 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to 32STREET-RR7 (659442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_432 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to PRNGHORN-RR7 (659544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_433 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_434 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_435 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_436 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_437 | 3 Phase fault on BOWMAN__-BE4230.00 (659339) 230 kV Bus a. Apply fault at the BOWMAN__-BE4230.00 (659339) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN__-BE4 (659339) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | 1 - Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. 2- Reclosing removed. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25S | Transfer | G01_P1_Local_Fault_438 | 3 Phase fault on BOWMAN__-BE7115.00 (659340) 115 kV Bus a. Apply fault at the BOWMAN__-BE7115.00 (659340) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN__-BE7 (659340) 115.0 kV to NBURR___-GE7 (659341) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_439 | 3 Phase fault on LC_SWY.S-BE7115.00 (659346) 115 kV Bus a. Apply fault at the LC_SWY.S-BE7115.00 (659346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.S-BE7 (659346) 115.0 kV to GEN-2020-014 (764180) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_440 | 3 Phase fault on LC_CT1-3-BE7115.00 (659348) 115 kV Bus a. Apply fault at the LC_CT1-3-BE7115.00 (659348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_CT1-3-BE7 (659348) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_441 | 3 Phase fault on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_442 | 3 Phase fault on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_443 | 3 Phase fault on BISON___-GE4230.00 (659351) 230 kV Bus a. Apply fault at the BISON___-GE4230.00 (659351) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_444 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_445 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_446 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_447 | 3 Phase fault on KUMMERDG-MK7115.00 (659388) 115 kV Bus a. Apply fault at the KUMMERDG-MK7115.00 (659388) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to BEPCPRXCC3 7 (659584) 115.0 kV Transmission Circuit #x1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_448 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_449 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_450 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_451 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_452 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_453 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_456 | 3 Phase fault on WDICKSN7 115.00 (661024) 115 kV Bus a. Apply fault at the WDICKSN7 115.00 (661024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WDICKSN7 (661024) 115.0 kV to DIXREF 7 (661028) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_457 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_458 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_459 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_460 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_461 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_462 | 3 Phase fault on MAURINE7 115.00 (652480) 115 kV Bus a. Apply fault at the MAURINE7 115.00 (652480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE8 (652248) 69.0 kV to MAURINE7 (652480) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_463 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_464 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_465 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_466 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_467 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_468 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_470 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_471 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_472 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_473 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_474 | 3 Phase fault on MAURINE4 230.00 (652497) 230 kV Bus a. Apply fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV to MAURINE9 (652247) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_475 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_476 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_477 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_478 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_479 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_480 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_482 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_483 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF29 (652233) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_484 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_485 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_486 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_487 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_488 | 3 Phase fault on LETCHER4 230.00 (652606) 230 kV Bus a. Apply fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_489 | 3 Phase fault on CARPENTER 4 230.00 (652614) 230 kV Bus a. Apply fault at the CARPENTER 4 230.00 (652614) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARPENTER 4 (652614) 230.0 kV to CARPENTR-ER8 (655499) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_490 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_491 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_492 | 3 Phase fault on SULLYBT-ER4 230.00 (655487) 230 kV Bus a. Apply fault at the SULLYBT-ER4 230.00 (655487) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SULLYBT-ER4 (655487) 230.0 kV to SULLYBT-ER8 (655488) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_493 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_494 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_495 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_496 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_497 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_498 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_499 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_500 | 3 Phase fault on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_501 | 3 Phase fault on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DICKNSON 9 (560122) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_502 | 3 Phase fault on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DK.KW1A_-BE9 (659197) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_503 | 3 Phase fault on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE4 (659124) 230.0 kV to DICKINS2-BE7 (659195) 115.0 kV to DK.KW1A_-BE9 (659196) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_504 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_505 | 3 Phase fault on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_506 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_507 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_508 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE8 (659198) 115.0 kV to GRT.KU2A-BE8 (659699) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_509 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_510 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_511 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_512 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_513 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_514 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_515 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_517 | 3 Phase fault on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RHAME___-BE4 (659266) 230.0 kV to RHAME___-BE7 (659267) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25S | Transfer | G01_P1_Local_Fault_518 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_519 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_520 | 3 Phase fault on BOWMAN__-BE4230.00 (659339) 230 kV Bus a. Apply fault at the BOWMAN__-BE4230.00 (659339) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN__-BE7 (659340) 115.0 kV to BOWMAN__-BE4 (659339) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25S | Transfer | G01_P1_Local_Fault_521 | 3 Phase fault on BISON___-GE4230.00 (659351) 230 kV Bus a. Apply fault at the BISON___-GE4230.00 (659351) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_522 | 3 Phase fault on BISON___-GE4230.00 (659351) 230 kV Bus a. Apply fault at the BISON___-GE4230.00 (659351) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_523 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_524 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_525 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_526 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_527 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_528 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_529 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_531 | 3 Phase fault on HETINGR4 230.00 (661047) 230 kV Bus a. Apply fault at the HETINGR4 230.00 (661047) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HETINGR4 (661047) 230.0 kV to HETINGR7 (661048) 115.0 kV to HETINGR9 (661902) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25S | Transfer | G01_P1_Local_Fault_532 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_533 | 3 Phase fault on BDV 4230.00 (672603) 230 kV Bus a. Apply fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_534 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_535 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_536 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_537 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_538 | 3 Phase fault on MAURINE7 115.00 (652480) 115 kV Bus a. Apply fault at the MAURINE7 115.00 (652480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE7 (652480) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_539 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_540 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_541 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_542 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_543 | 3 Phase fault on GRPRAR2-LNX3345.00 (652833) 345 kV Bus a. Apply fault at the GRPRAR2-LNX3345.00 (652833) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_544 | 3 Phase fault on NUNDRWD-LNX3230.00 (652884) 230 kV Bus a. Apply fault at the NUNDRWD-LNX3230.00 (652884) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD-LNX3 (652884) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_545 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_546 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_547 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_548 | 3 Phase fault on E.NEWTWN-MW7115.00 (655907) 115 kV Bus a. Apply fault at the E.NEWTWN-MW7115.00 (655907) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_549 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_552 | 3 Phase fault on NBURR___-GE7115.00 (659341) 115 kV Bus a. Apply fault at the NBURR___-GE7115.00 (659341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBURR___-GE7 (659341) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_554 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_555 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_556 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_557 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_558 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_559 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_560 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Local_Fault_561 | 3 Phase fault on BRADYWND 4230.00 (659450) 230 kV Bus a. Apply fault at the BRADYWND 4230.00 (659450) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRADYWND 4 (659450) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_001 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_002 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_003 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_004 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_005 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_006 | 3 Phase fault on BISON 3 345.00 (601067) 345 kV Bus a. Apply fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_007 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_008 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_009 | 3 Phase fault on HANKSON4 230.00 (620327) 230 kV Bus a. Apply fault at the HANKSON4 230.00 (620327) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_010 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_011 | 3 Phase fault on OAKES 4 230.00 (620362) 230 kV Bus a. Apply fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_012 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_013 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_014 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_015 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_016 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_017 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_018 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_019 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_020 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_021 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_022 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_023 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_025 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_026 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.5. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_027 | 3 Phase fault on OAKES 4 230.00 (620362) 230 kV Bus a. Apply fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 b.8. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.9. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_028 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_029 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_030 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 b.4. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_031 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_032 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_033 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_034 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_035 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_036 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_037 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_038 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_039 | 3 Phase fault on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAIR-ER4 (655465) 230.0 kV to BLAIR-ER8 (655466) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_040 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_041 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_042 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_043 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_044 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_045 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_046 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_047 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_048 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_049 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_050 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_051 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_052 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_053 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_054 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_055 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_056 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_057 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_058 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_059 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_060 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_061 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_062 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_063 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_064 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_065 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_066 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_067 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to DEERCREK-BE3 (659286) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_068 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_069 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_070 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_071 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_072 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_073 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_074 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_075 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_076 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_077 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_078 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_079 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_080 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_081 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_082 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P1_Regional_Fault_083 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_001 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE8 (659198) 115.0 kV to GRT.KU2A-BE8 (659699) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_002 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_003 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_004 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_005 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_006 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_007 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_008 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_009 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_010 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_011 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_012 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_013 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_014 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_015 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_016 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_017 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_018 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_019 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_020 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_021 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_022 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_023 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_024 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_025 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_026 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_027 | Single Phase Fault with Stuck Breaker on CROCKER_-BE3345.00 (659165) 345 kV Bus a. Apply Fault at the CROCKER_-BE3345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_028 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_029 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_030 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_031 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_032 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_033 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_034 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_035 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_036 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_037 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_038 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_039 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_040 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_041 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_042 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_043 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_044 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_045 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_046 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.11. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_047 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 12 cycles.
01 - North | 25S | Base | G01_P4_Local_Fault_047 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduce clearing time to 12 cycles.
01 - North | 25S | Transfer | G01_P4_Local_Fault_048 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 12 cycles.
01 - North | 25S | Base | G01_P4_Local_Fault_048 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduce clearing time to 12 cycles.
01 - North | 25S | Transfer | G01_P4_Local_Fault_049 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_050 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_051 | Single Phase Fault with Stuck Breaker on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply Fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.5. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reduce clearing time to 12 cycles.
01 - North | 25S | Base | G01_P4_Local_Fault_051 | Single Phase Fault with Stuck Breaker on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply Fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.5. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduce clearing time to 12 cycles.
01 - North | 25S | Transfer | G01_P4_Local_Fault_052 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_053 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 b.2. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_054 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_055 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_056 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_057 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_058 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_059 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_060 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_061 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_062 | Single Phase Fault with Stuck Breaker on BD 6138.00 (672501) 138 kV Bus a. Apply Fault at the BD 6138.00 (672501) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD 4 (672601) 230.0 kV to BD 6 (672501) 138.0 kV Two Winding #1 b.2. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.3. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 b.4. BD 6 (672501) 138.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_063 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD 4 (672601) 230.0 kV to BD 6 (672501) 138.0 kV Two Winding #1 b.2. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.3. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_064 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 b.3. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_065 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 b.3. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_066 | Single Phase Fault with Stuck Breaker on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply Fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RHAME___-BE4 (659266) 230.0 kV to BOWMAN__-BE4 (659339) 230.0 kV Transmission Circuit #1 b.2. RHAME___-BE4 (659266) 230.0 kV to LITTL_MS-BE4 (659265) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25S | Transfer | G01_P4_Local_Fault_067 | Single Phase Fault with Stuck Breaker on HETINGR4 230.00 (661047) 230 kV Bus a. Apply Fault at the HETINGR4 230.00 (661047) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HETINGR4 (661047) 230.0 kV to BOWMAN__-BE4 (659339) 230.0 kV Transmission Circuit #1 b.2. HETINGR4 (661047) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25S | Transfer | G01_P4_Local_Fault_068 | Single Phase Fault with Stuck Breaker on GEN-2020-014115.00 (764180) 115 kV Bus a. Apply Fault at the GEN-2020-014115.00 (764180) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-014 (764180) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 b.2. GEN-2020-014 (764180) 115.0 kV to G20-014-GEN1 (764181) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_069 | Single Phase Fault with Stuck Breaker on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply Fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_070 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_071 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.2. CC.LS-LO-BE3 (659428) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_072 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_073 | Single Phase Fault with Stuck Breaker on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply Fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.2. RICHLAND-BE7 (659151) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_074 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_075 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU17A-BE7 (659466) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. PG.KU17A-BE7 (659466) 115.0 kV to PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_076 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU19A-BE7 (659467) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. PG.KU19A-BE7 (659467) 115.0 kV to PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_077 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_078 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_079 | Single Phase Fault with Stuck Breaker on RHAME___-BE4 (659266) 230 kV Bus a. Apply Fault at the RHAME___-BE4 (659266) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RHAME___-BE4 (659266) 230.0 kV bus tripped | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25S | Transfer | G01_P4_Local_Fault_080 | Single Phase Fault with Stuck Breaker on BOWMAN__-BE7 (659340) 115 kV Bus a. Apply Fault at the BOWMAN__-BE7 (659340) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWMAN__-BE7 (659340) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_081 | Single Phase Fault with Stuck Breaker on HETINGR4 (661047) 230 kV Bus a. Apply Fault at the HETINGR4 (661047) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HETINGR4 (661047) 230.0 kV bus tripped | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25S | Transfer | G01_P4_Local_Fault_082 | Single Phase Fault with Stuck Breaker on ARNEGARD-MK7 (655841) 115 kV Bus a. Apply Fault at the ARNEGARD-MK7 (655841) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNEGARD-MK7 (655841) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_083 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_CT4-5-BE7 (659154) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_084 | Single Phase Fault with Stuck Breaker on GEN-2020-014 (764180) 115 kV Bus a. Apply Fault at the GEN-2020-014 (764180) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-014 (764180) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_085 | Single Phase Fault with Stuck Breaker on LC_SWY.N-BE7 (659349) 115 kV Bus a. Apply Fault at the LC_SWY.N-BE7 (659349) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_086 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_087 | Single Phase Fault with Stuck Breaker on GEN-2020-021 (764210) 345 kV Bus a. Apply Fault at the GEN-2020-021 (764210) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-021 (764210) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_088 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_089 | Single Phase Fault with Stuck Breaker on WILISTN7 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_090 | Single Phase Fault with Stuck Breaker on SPRINGLK-LY7 (655791) 115 kV Bus a. Apply Fault at the SPRINGLK-LY7 (655791) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRINGLK-LY7 (655791) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_091 | Single Phase Fault with Stuck Breaker on NOHLEY -LY7 (655792) 115 kV Bus a. Apply Fault at the NOHLEY -LY7 (655792) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOHLEY -LY7 (655792) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_092 | Single Phase Fault with Stuck Breaker on RICHLAND-BE7 (659151) 115 kV Bus a. Apply Fault at the RICHLAND-BE7 (659151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAND-BE7 (659151) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_093 | Single Phase Fault with Stuck Breaker on GEN-2020-091 (764225) 345 kV Bus a. Apply Fault at the GEN-2020-091 (764225) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-091 (764225) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_094 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_095 | Single Phase Fault with Stuck Breaker on PG.KU17A-BE7 (659466) 115 kV Bus a. Apply Fault at the PG.KU17A-BE7 (659466) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU17A-BE7 (659466) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_096 | Single Phase Fault with Stuck Breaker on PG.KU19A-BE7 (659467) 115 kV Bus a. Apply Fault at the PG.KU19A-BE7 (659467) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU19A-BE7 (659467) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_097 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Local_Fault_098 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_001 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_003 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_004 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_005 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_006 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_007 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_008 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_009 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_010 | Single Phase Fault with Stuck Breaker on BISON 3 345.00 (601067) 345 kV Bus a. Apply Fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.2. MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV to MAPLER19 (620359) 13.8 kV Three Winding #1 b.3. MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV to MAPLER29 (620360) 13.8 kV Three Winding #2 b.6. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_011 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_012 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 b.4. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_013 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_014 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_015 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_016 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_017 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_018 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_019 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_020 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_021 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_022 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_023 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_024 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_025 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 b.3. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | G01_P4_Regional_Fault_026 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 b.3. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_001 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_002 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_003 | 3 Phase fault on MATHSON7 115.00 (661019) 115 kV Bus a. Apply fault at the MATHSON7 115.00 (661019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINS2-BE7 (659195) 115.0 kV to MATHSON7 (661019) 115.0 kV Transmission Circuit #1 b.2. MATHSON7 (661019) 115.0 kV to DIXGREENRVR7 (661020) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_004 | 3 Phase fault on N ENGLN7 115.00 (661070) 115 kV Bus a. Apply fault at the N ENGLN7 115.00 (661070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTIPED-UM7 (655730) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 b.2. DICKINSN-BE7 (659125) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_005 | 3 Phase fault on ESTBMRK7 115.00 (661029) 115 kV Bus a. Apply fault at the ESTBMRK7 115.00 (661029) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK7 (652427) 115.0 kV to ESTBMRK7 (661029) 115.0 kV Transmission Circuit #1 b.2. BISEXP 7 (661009) 115.0 kV to ESTBMRK7 (661029) 115.0 kV Transmission Circuit #1 b.3. ESTBMRK7 (661029) 115.0 kV to LINTON 7 (661060) 115.0 kV Transmission Circuit #1 b.4. ESTBMRK7 (661029) 115.0 kV to 26TH&D 7 (661119) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_006 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_007 | 3 Phase fault on HETINGR7 115.00 (661048) 115 kV Bus a. Apply fault at the HETINGR7 115.00 (661048) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HETINGR7 (661048) 115.0 kV to GASCOYN7 (661050) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_008 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_009 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_010 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_011 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_012 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_013 | 3 Phase fault on BAKER 7 115.00 (661005) 115 kV Bus a. Apply fault at the BAKER 7 115.00 (661005) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 7 (661005) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_014 | 3 Phase fault on HETINGR7 115.00 (661048) 115 kV Bus a. Apply fault at the HETINGR7 115.00 (661048) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HETINGR7 (661048) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_015 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_016 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_017 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_018 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_019 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_020 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_021 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_022 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_023 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_024 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_025 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_026 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_027 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_028 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_029 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_030 | 3 Phase fault on SQBUTTE4 230.00 (657756) 230 kV Bus a. Apply fault at the SQBUTTE4 230.00 (657756) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBUTTE4 (657756) 230.0 kV to YNG2 4 (657848) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_031 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_032 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_033 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_034 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_035 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_036 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 b.5. GRE-MCHENRYT (615349) 12.5 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_037 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_038 | 3 Phase fault on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_039 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_040 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_041 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_042 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_043 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_044 | 3 Phase fault on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_045 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_046 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_047 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_048 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_049 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_050 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_051 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_052 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_053 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_054 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_055 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_056 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_057 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_058 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_059 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_060 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_061 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_062 | 3 Phase fault on SB.LS-WK-ER4230.00 (655510) 230 kV Bus a. Apply fault at the SB.LS-WK-ER4230.00 (655510) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SB.LS-WK-ER4 (655510) 230.0 kV to WHITLOCK_-RM (655765) 230.0 kV Transmission Circuit #1 b.2. WHITLOCK_-RM (655765) 230.0 kV to GLENHAM4 (661038) 230.0 kV Transmission Circuit #1 b.3. SULLYBT-ER4 (655487) 230.0 kV to SB.LS-WK-ER4 (655510) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_063 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_064 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.4. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_065 | 3 Phase fault on FAITH 7 115.00 (652243) 115 kV Bus a. Apply fault at the FAITH 7 115.00 (652243) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAITH 7 (652243) 115.0 kV to EAGLEBT7 (652476) 115.0 kV Transmission Circuit #1 b.2. FAITH 7 (652243) 115.0 kV to MAURINE7 (652480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_066 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_067 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_068 | 3 Phase fault on WOONSKT7 115.00 (652528) 115 kV Bus a. Apply fault at the WOONSKT7 115.00 (652528) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.3. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.4. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_069 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_070 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_071 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_072 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_073 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_074 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_075 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_076 | 3 Phase fault on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_077 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.KU2A_-BE9 (659204) 13.8 kV to BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV Three Winding #1 b.2. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.3. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.6. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_078 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_079 | 3 Phase fault on WATERTNCAP 4230.00 (652630) 230 kV Bus a. Apply fault at the WATERTNCAP 4230.00 (652630) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTNCAP 4 (652630) 230.0 kV Fixed Shunt Device | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_080 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_081 | 3 Phase fault on TYNDALL7 115.00 (652525) 115 kV Bus a. Apply fault at the TYNDALL7 115.00 (652525) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.4. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_082 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_083 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_084 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_085 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_086 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_087 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_088 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_089 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_090 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_091 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.2. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.3. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_092 | 3 Phase fault on PWRSLKTP-MW7115.00 (655947) 115 kV Bus a. Apply fault at the PWRSLKTP-MW7115.00 (655947) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINDAHLS-MW7 (655910) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.2. PWRSLKTP-MW7 (655947) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.3. POWERSLK-MW7 (655946) 115.0 kV to PWRSLKTP-MW7 (655947) 115.0 kV Transmission Circuit #1 b.4. PWRSLKTP-MW7 (655947) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_093 | 3 Phase fault on MOE -MW7115.00 (655900) 115 kV Bus a. Apply fault at the MOE -MW7115.00 (655900) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOE -MW7 (655900) 115.0 kV to PLSNTV_T-MW7 (655902) 115.0 kV Transmission Circuit #1 b.2. MOE -MW7 (655900) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 b.3. MOE -MW7 (655900) 115.0 kV to E.NESSON-MW7 (655965) 115.0 kV Transmission Circuit #1 b.4. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.5. ROSS -MW7 (655903) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.6. BROOKBNK-MW7 (655901) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 b.7. BROOKBNK-MW7 (655901) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_094 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_095 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 b.7. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_096 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_097 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_098 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_099 | 3 Phase fault on EAGLEBT7 115.00 (652476) 115 kV Bus a. Apply fault at the EAGLEBT7 115.00 (652476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLEBT7 (652476) 115.0 kV to OAHE 7 (652520) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_100 | 3 Phase fault on OAHE 7 115.00 (652520) 115 kV Bus a. Apply fault at the OAHE 7 115.00 (652520) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 7 (652520) 115.0 kV to IRVSIMM7 (658174) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_101 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_102 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_103 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_104 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_105 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_106 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_107 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 29 (652598) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_108 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_109 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_110 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_111 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_112 | 3 Phase fault on MOE -MW7115.00 (655900) 115 kV Bus a. Apply fault at the MOE -MW7115.00 (655900) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOE -MW7 (655900) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 b.2. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.3. MOE -MW7 (655900) 115.0 kV to PLSNTV_T-MW7 (655902) 115.0 kV Transmission Circuit #1 b.4. MOE -MW7 (655900) 115.0 kV to E.NESSON-MW7 (655965) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_113 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. AV.LS-BD-BE3 (659420) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_114 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. BD.LS-AV-BE3 (659421) 345.0 kV Fixed Shunt Device b.13. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.14. GR.LS-LO-BE3 (659423) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_115 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_116 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.4. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_117 | 3 Phase fault on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit #1 b.2. ARNEGARD-MK7 (655841) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.4. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_118 | 3 Phase fault on BISON___-GE4230.00 (659351) 230 kV Bus a. Apply fault at the BISON___-GE4230.00 (659351) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.2. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.3. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.4. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_119 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_120 | 3 Phase fault on E.BISMRK-CP7115.00 (655652) 115 kV Bus a. Apply fault at the E.BISMRK-CP7115.00 (655652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK7 (652427) 115.0 kV to E.BISMRK-CP7 (655652) 115.0 kV Transmission Circuit #1 b.2. E.BISMRK-CP7 (655652) 115.0 kV to HAYCREEK-CP7 (655689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_121 | 3 Phase fault on FAITH 7 115.00 (652243) 115 kV Bus a. Apply fault at the FAITH 7 115.00 (652243) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAITH 7 (652243) 115.0 kV to EAGLEBT7 (652476) 115.0 kV Transmission Circuit #1 b.2. FAITH 7 (652243) 115.0 kV to MAURINE7 (652480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_122 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.3. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.4. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.5. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.6. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.7. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_123 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 b.2. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 b.3. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_124 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_125 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_126 | 3 Phase fault on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_127 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_128 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_129 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_130 | 3 Phase fault on OSBORN -MW7115.00 (655919) 115 kV Bus a. Apply fault at the OSBORN -MW7115.00 (655919) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_131 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_132 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_133 | 3 Phase fault on PWRSLKTP-MW7115.00 (655947) 115 kV Bus a. Apply fault at the PWRSLKTP-MW7115.00 (655947) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POWERSLK-MW7 (655946) 115.0 kV to PWRSLKTP-MW7 (655947) 115.0 kV Transmission Circuit #1 b.2. PWRSLKTP-MW7 (655947) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.3. PWRSLKTP-MW7 (655947) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_134 | 3 Phase fault on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_135 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_136 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_137 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_138 | 3 Phase fault on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_139 | 3 Phase fault on TWNVLYTP-MK7115.00 (655867) 115 kV Bus a. Apply fault at the TWNVLYTP-MK7115.00 (655867) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNVLYTP-MK7 (655867) 115.0 kV to TWINVLLY-MK7 (655869) 115.0 kV Transmission Circuit #1 b.2. TWNVLYTP-MK7 (655867) 115.0 kV to TBGARDEN-MK7 (655870) 115.0 kV Transmission Circuit #1 b.3. TWNVLYTP-MK7 (655867) 115.0 kV to BANKS -MK7 (655888) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_140 | 3 Phase fault on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.2. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_141 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_142 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_143 | 3 Phase fault on WOONSKT7 115.00 (652528) 115 kV Bus a. Apply fault at the WOONSKT7 115.00 (652528) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.3. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.4. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_144 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_145 | 3 Phase fault on E.SIDNEY-LY7115.00 (659186) 115 kV Bus a. Apply fault at the E.SIDNEY-LY7115.00 (659186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_146 | 3 Phase fault on TYNDALL7 115.00 (652525) 115 kV Bus a. Apply fault at the TYNDALL7 115.00 (652525) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.4. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_147 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_148 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_149 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_150 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_151 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_152 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_153 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_154 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_155 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_157 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_158 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_159 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_160 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_161 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_162 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_163 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_164 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_165 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_166 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_167 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_168 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_169 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GEN-2017-210 (761208) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_170 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_171 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_172 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_173 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_174 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_175 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_176 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_177 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GEN-2017-144 (760767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_178 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to PR BRZ 4 (648506) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_179 | 3 Phase fault on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR1 3 (648513) 345.0 kV to GRPR2 3 (648520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_180 | 3 Phase fault on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR1 3 (648513) 345.0 kV to GRPR3 3 (648527) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_181 | 3 Phase fault on GRPR1 3 345.00 (648513) 345 kV Bus a. Apply fault at the GRPR1 3 345.00 (648513) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPR1 3 (648513) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_183 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_184 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_185 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_186 | 3 Phase fault on FAITH 7 115.00 (652243) 115 kV Bus a. Apply fault at the FAITH 7 115.00 (652243) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAITH 7 (652243) 115.0 kV to MAURINE7 (652480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_187 | 3 Phase fault on FTTHOMP8 69.000 (652276) 69 kV Bus a. Apply fault at the FTTHOMP8 69.000 (652276) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP8 (652276) 69.0 kV to MOS-AMES-ER8 (655153) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_188 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_189 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_190 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_191 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_192 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_193 | 3 Phase fault on VFODNES4 230.00 (652398) 230 kV Bus a. Apply fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_194 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_195 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_196 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_198 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_199 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_200 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_201 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_202 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_203 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_204 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_205 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_207 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_209 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_210 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_211 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_212 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_213 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_214 | 3 Phase fault on BISMARK7 115.00 (652427) 115 kV Bus a. Apply fault at the BISMARK7 115.00 (652427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK7 (652427) 115.0 kV to E.BISMRK-CP7 (655652) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_215 | 3 Phase fault on BISMARK7 115.00 (652427) 115 kV Bus a. Apply fault at the BISMARK7 115.00 (652427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK7 (652427) 115.0 kV to ESTBMRK7 (661029) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_216 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_217 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_218 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_219 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_220 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_221 | 3 Phase fault on HILKEN 4 230.00 (652466) 230 kV Bus a. Apply fault at the HILKEN 4 230.00 (652466) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_222 | 3 Phase fault on HEBRON 4 230.00 (652468) 230 kV Bus a. Apply fault at the HEBRON 4 230.00 (652468) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 4 (652468) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_223 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_224 | 3 Phase fault on MAURINE7 115.00 (652480) 115 kV Bus a. Apply fault at the MAURINE7 115.00 (652480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE7 (652480) 115.0 kV to SULPHUR (652491) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_225 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_226 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_227 | 3 Phase fault on WINCHESTER4 230.00 (652496) 230 kV Bus a. Apply fault at the WINCHESTER4 230.00 (652496) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINCHESTER4 (652496) 230.0 kV to CAMPBELL 4 (652499) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_228 | 3 Phase fault on MAURINE4 230.00 (652497) 230 kV Bus a. Apply fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_229 | 3 Phase fault on MAURINE4 230.00 (652497) 230 kV Bus a. Apply fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_230 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_231 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_232 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_233 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_234 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_235 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_236 | 3 Phase fault on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_237 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_238 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_239 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_240 | 3 Phase fault on HANLON 4 230.00 (652513) 230 kV Bus a. Apply fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_241 | 3 Phase fault on HANLON 4 230.00 (652513) 230 kV Bus a. Apply fault at the HANLON 4 230.00 (652513) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_242 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_243 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_244 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_245 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_246 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_247 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_248 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_249 | 3 Phase fault on OAHE 7 115.00 (652520) 115 kV Bus a. Apply fault at the OAHE 7 115.00 (652520) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 7 (652520) 115.0 kV to ASH TAP (652600) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_250 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_251 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_252 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to PRVLNG16 (654457) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_253 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_254 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_255 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_256 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_257 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_258 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_259 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GEN-2018-056 (762911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_260 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_261 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_262 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_263 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_264 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_265 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON_G-BE7 (659275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_266 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_267 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_268 | 3 Phase fault on WESSINGTON 4230.00 (652607) 230 kV Bus a. Apply fault at the WESSINGTON 4230.00 (652607) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_269 | 3 Phase fault on WESSINGTON 4230.00 (652607) 230 kV Bus a. Apply fault at the WESSINGTON 4230.00 (652607) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_270 | 3 Phase fault on LETCHER7 115.00 (652609) 115 kV Bus a. Apply fault at the LETCHER7 115.00 (652609) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER7 (652609) 115.0 kV to ROSWELL-ER7 (655417) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_271 | 3 Phase fault on LETCHER7 115.00 (652609) 115 kV Bus a. Apply fault at the LETCHER7 115.00 (652609) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_272 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_273 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_274 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_275 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_276 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_277 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_278 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_279 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_280 | 3 Phase fault on MOS-POLO-ER869.000 (655060) 69 kV Bus a. Apply fault at the MOS-POLO-ER869.000 (655060) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-POLO-ER8 (655060) 69.0 kV to POLO-ER8 (655233) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_281 | 3 Phase fault on MOS-POLO-ER869.000 (655060) 69 kV Bus a. Apply fault at the MOS-POLO-ER869.000 (655060) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-POLO-ER8 (655060) 69.0 kV to MILLER-ER8 (655234) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_282 | 3 Phase fault on MOS-AMES-ER869.000 (655153) 69 kV Bus a. Apply fault at the MOS-AMES-ER869.000 (655153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-AMES-ER8 (655153) 69.0 kV to MOS-HYDE-ER8 (655158) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_283 | 3 Phase fault on MOS-AMES-ER869.000 (655153) 69 kV Bus a. Apply fault at the MOS-AMES-ER869.000 (655153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-AMES-ER8 (655153) 69.0 kV to BIGBEND-ER8 (655328) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_284 | 3 Phase fault on MOS-AMES-ER869.000 (655153) 69 kV Bus a. Apply fault at the MOS-AMES-ER869.000 (655153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-AMES-ER8 (655153) 69.0 kV to AMES-ER8 (655352) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_285 | 3 Phase fault on MOS-HYDE-ER869.000 (655158) 69 kV Bus a. Apply fault at the MOS-HYDE-ER869.000 (655158) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-HYDE-ER8 (655158) 69.0 kV to NWPS8645-ER8 (655384) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_286 | 3 Phase fault on HGHMORE-ER8 69.000 (655240) 69 kV Bus a. Apply fault at the HGHMORE-ER8 69.000 (655240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HGHMORE-ER8 (655240) 69.0 kV to NWPS8645-ER8 (655384) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_287 | 3 Phase fault on CHMBRLAN-ER869.000 (655250) 69 kV Bus a. Apply fault at the CHMBRLAN-ER869.000 (655250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHMBRLAN-ER8 (655250) 69.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_288 | 3 Phase fault on GANNVALL-ER869.000 (655329) 69 kV Bus a. Apply fault at the GANNVALL-ER869.000 (655329) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GANNVALL-ER8 (655329) 69.0 kV to AMES-ER8 (655352) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_289 | 3 Phase fault on MOS-LKPL-ER869.000 (655385) 69 kV Bus a. Apply fault at the MOS-LKPL-ER869.000 (655385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-LKPL-ER8 (655385) 69.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_290 | 3 Phase fault on CRANDALL-ER7115.00 (655411) 115 kV Bus a. Apply fault at the CRANDALL-ER7115.00 (655411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_291 | 3 Phase fault on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_292 | 3 Phase fault on SULLYBT-ER4 230.00 (655487) 230 kV Bus a. Apply fault at the SULLYBT-ER4 230.00 (655487) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SULLYBT-ER4 (655487) 230.0 kV to SB.LS-WK-ER4 (655510) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_293 | 3 Phase fault on CENTIPED-UM7115.00 (655730) 115 kV Bus a. Apply fault at the CENTIPED-UM7115.00 (655730) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTIPED-UM7 (655730) 115.0 kV to HETINGR7 (661048) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_294 | 3 Phase fault on CENTIPED-UM7115.00 (655730) 115 kV Bus a. Apply fault at the CENTIPED-UM7115.00 (655730) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTIPED-UM7 (655730) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_295 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_296 | 3 Phase fault on HELMUT -LY7115.00 (655790) 115 kV Bus a. Apply fault at the HELMUT -LY7115.00 (655790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_297 | 3 Phase fault on MOUNTAIN-MK7115.00 (655830) 115 kV Bus a. Apply fault at the MOUNTAIN-MK7115.00 (655830) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNTAIN-MK7 (655830) 115.0 kV to OAKDALE -MK7 (655836) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_298 | 3 Phase fault on BLUEBUTE-MK7115.00 (655832) 115 kV Bus a. Apply fault at the BLUEBUTE-MK7115.00 (655832) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBUTE-MK7 (655832) 115.0 kV to VEEDER -MK7 (655849) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_299 | 3 Phase fault on BLUEBUTE-MK7115.00 (655832) 115 kV Bus a. Apply fault at the BLUEBUTE-MK7115.00 (655832) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBUTE-MK7 (655832) 115.0 kV to STATION8-MK7 (655865) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_300 | 3 Phase fault on LITTLKNF-MK7115.00 (655835) 115 kV Bus a. Apply fault at the LITTLKNF-MK7115.00 (655835) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTLKNF-MK7 (655835) 115.0 kV to OAKDALE -MK7 (655836) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_301 | 3 Phase fault on OAKDALE -MK7115.00 (655836) 115 kV Bus a. Apply fault at the OAKDALE -MK7115.00 (655836) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKDALE -MK7 (655836) 115.0 kV to BEARCREK-MK7 (655853) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_302 | 3 Phase fault on ELMTREE -MK7115.00 (655837) 115 kV Bus a. Apply fault at the ELMTREE -MK7115.00 (655837) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMTREE -MK7 (655837) 115.0 kV to TABLEBUT-MK7 (655858) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_303 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_304 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to NRTINDHL-MK7 (655850) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_305 | 3 Phase fault on SATHERDM-MK7115.00 (655839) 115 kV Bus a. Apply fault at the SATHERDM-MK7115.00 (655839) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SATHERDM-MK7 (655839) 115.0 kV to TRUEOIL -MK7 (655843) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_306 | 3 Phase fault on SATHERDM-MK7115.00 (655839) 115 kV Bus a. Apply fault at the SATHERDM-MK7115.00 (655839) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SATHERDM-MK7 (655839) 115.0 kV to SKAAR___-MK7 (655860) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_307 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_308 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_309 | 3 Phase fault on ARNEGARD-MK7115.00 (655841) 115 kV Bus a. Apply fault at the ARNEGARD-MK7115.00 (655841) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNEGARD-MK7 (655841) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_310 | 3 Phase fault on HAYBUTTE-MK7115.00 (655842) 115 kV Bus a. Apply fault at the HAYBUTTE-MK7115.00 (655842) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_311 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_312 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_313 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_314 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_315 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to GARDN-FB-MK7 (655895) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_316 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_317 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to BANKS -MK7 (655888) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_318 | 3 Phase fault on SWENSON -MK7115.00 (655847) 115 kV Bus a. Apply fault at the SWENSON -MK7115.00 (655847) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWENSON -MK7 (655847) 115.0 kV to BERG -MK7 (655848) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_319 | 3 Phase fault on SWENSON -MK7115.00 (655847) 115 kV Bus a. Apply fault at the SWENSON -MK7115.00 (655847) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWENSON -MK7 (655847) 115.0 kV to SNDCRKTP-MK7 (655866) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_320 | 3 Phase fault on SWENSON -MK7115.00 (655847) 115 kV Bus a. Apply fault at the SWENSON -MK7115.00 (655847) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWENSON -MK7 (655847) 115.0 kV to KEENECRN-MK7 (655896) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_321 | 3 Phase fault on BERG -MK7115.00 (655848) 115 kV Bus a. Apply fault at the BERG -MK7115.00 (655848) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG -MK7 (655848) 115.0 kV to TABLEBUT-MK7 (655858) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_322 | 3 Phase fault on BERG -MK7115.00 (655848) 115 kV Bus a. Apply fault at the BERG -MK7115.00 (655848) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG -MK7 (655848) 115.0 kV to BBCOMPTP-MK7 (655873) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_323 | 3 Phase fault on BERG -MK7115.00 (655848) 115 kV Bus a. Apply fault at the BERG -MK7115.00 (655848) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG -MK7 (655848) 115.0 kV to KEENE -MK7 (655886) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_324 | 3 Phase fault on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VEEDER -MK7 (655849) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_325 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_326 | 3 Phase fault on ROOSEVLT-MK7115.00 (655855) 115 kV Bus a. Apply fault at the ROOSEVLT-MK7115.00 (655855) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVLT-MK7 (655855) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_327 | 3 Phase fault on ROOSEVLT-MK7115.00 (655855) 115 kV Bus a. Apply fault at the ROOSEVLT-MK7115.00 (655855) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVLT-MK7 (655855) 115.0 kV to CRESTWD_-MK7 (655878) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_328 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_329 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_330 | 3 Phase fault on HORSECRK-MK7115.00 (655861) 115 kV Bus a. Apply fault at the HORSECRK-MK7115.00 (655861) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HORSECRK-MK7 (655861) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_331 | 3 Phase fault on GRAIL -MK7115.00 (655864) 115 kV Bus a. Apply fault at the GRAIL -MK7115.00 (655864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAIL -MK7 (655864) 115.0 kV to STATION8-MK7 (655865) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_332 | 3 Phase fault on TWNVLYTP-MK7115.00 (655867) 115 kV Bus a. Apply fault at the TWNVLYTP-MK7115.00 (655867) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNVLYTP-MK7 (655867) 115.0 kV to TWINVLLY-MK7 (655869) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_333 | 3 Phase fault on TWNVLYTP-MK7115.00 (655867) 115 kV Bus a. Apply fault at the TWNVLYTP-MK7115.00 (655867) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNVLYTP-MK7 (655867) 115.0 kV to TBGARDEN-MK7 (655870) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_334 | 3 Phase fault on TWNVLYTP-MK7115.00 (655867) 115 kV Bus a. Apply fault at the TWNVLYTP-MK7115.00 (655867) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNVLYTP-MK7 (655867) 115.0 kV to BANKS -MK7 (655888) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_335 | 3 Phase fault on G9______-MK7115.00 (655871) 115 kV Bus a. Apply fault at the G9______-MK7115.00 (655871) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G9______-MK7 (655871) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_336 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to BBCMPRSS-MK7 (655874) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_337 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_338 | 3 Phase fault on DPLWC___-MK7115.00 (655875) 115 kV Bus a. Apply fault at the DPLWC___-MK7115.00 (655875) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWC___-MK7 (655875) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_339 | 3 Phase fault on DPLWCTAP-MK7115.00 (655876) 115 kV Bus a. Apply fault at the DPLWCTAP-MK7115.00 (655876) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWCTAP-MK7 (655876) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_340 | 3 Phase fault on CRESTWD_-MK7115.00 (655878) 115 kV Bus a. Apply fault at the CRESTWD_-MK7115.00 (655878) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTWD_-MK7 (655878) 115.0 kV to SCHAFER -MK7 (655898) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_341 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to COYOTCHR-MK7 (655897) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_342 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to FNCYBTAP-MK7 (655899) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_343 | 3 Phase fault on DAP_____-MK7115.00 (655881) 115 kV Bus a. Apply fault at the DAP_____-MK7115.00 (655881) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAP_____-MK7 (655881) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_344 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_345 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_346 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_347 | 3 Phase fault on NRTHFORK-MK7115.00 (655885) 115 kV Bus a. Apply fault at the NRTHFORK-MK7115.00 (655885) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTHFORK-MK7 (655885) 115.0 kV to KEENE -MK7 (655886) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_348 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_349 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to HALLIDAY-MK7 (655894) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_350 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_351 | 3 Phase fault on FNCYBTAP-MK7115.00 (655899) 115 kV Bus a. Apply fault at the FNCYBTAP-MK7115.00 (655899) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNCYBTAP-MK7 (655899) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_352 | 3 Phase fault on BROOKBNK-MW7115.00 (655901) 115 kV Bus a. Apply fault at the BROOKBNK-MW7115.00 (655901) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKBNK-MW7 (655901) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_353 | 3 Phase fault on BROOKBNK-MW7115.00 (655901) 115 kV Bus a. Apply fault at the BROOKBNK-MW7115.00 (655901) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROOKBNK-MW7 (655901) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_354 | 3 Phase fault on ROSS -MW7115.00 (655903) 115 kV Bus a. Apply fault at the ROSS -MW7115.00 (655903) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSS -MW7 (655903) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_355 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_356 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to AUSTIN -MW7 (655912) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_357 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_358 | 3 Phase fault on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_359 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_360 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_361 | 3 Phase fault on E.NEWTWN-MW7115.00 (655907) 115 kV Bus a. Apply fault at the E.NEWTWN-MW7115.00 (655907) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_362 | 3 Phase fault on E.NEWTWN-MW7115.00 (655907) 115 kV Bus a. Apply fault at the E.NEWTWN-MW7115.00 (655907) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_363 | 3 Phase fault on E.NEWTWN-MW7115.00 (655907) 115 kV Bus a. Apply fault at the E.NEWTWN-MW7115.00 (655907) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to BIGBEND -MW7 (655960) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_364 | 3 Phase fault on E.NEWTWN-MW7115.00 (655907) 115 kV Bus a. Apply fault at the E.NEWTWN-MW7115.00 (655907) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to SATTER -MW7 (655967) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_365 | 3 Phase fault on PARSHALL-MW7115.00 (655908) 115 kV Bus a. Apply fault at the PARSHALL-MW7115.00 (655908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_366 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_367 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_368 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_369 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_370 | 3 Phase fault on RATLAKE -MW7115.00 (655929) 115 kV Bus a. Apply fault at the RATLAKE -MW7115.00 (655929) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_371 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_372 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_373 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_374 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_375 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_376 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_377 | 3 Phase fault on N.WILSTN-MW7115.00 (655936) 115 kV Bus a. Apply fault at the N.WILSTN-MW7115.00 (655936) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_378 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_379 | 3 Phase fault on FARMVL_T-MW7115.00 (655943) 115 kV Bus a. Apply fault at the FARMVL_T-MW7115.00 (655943) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_380 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_381 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_382 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_383 | 3 Phase fault on ELLISVIL-MW7115.00 (655954) 115 kV Bus a. Apply fault at the ELLISVIL-MW7115.00 (655954) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_384 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_385 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_386 | 3 Phase fault on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_387 | 3 Phase fault on SATTER -MW7115.00 (655967) 115 kV Bus a. Apply fault at the SATTER -MW7115.00 (655967) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SATTER -MW7 (655967) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_388 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_389 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_399 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_400 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_401 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to GEN-2019-037 (763703) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_402 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_403 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_404 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_405 | 3 Phase fault on DICKINSN-BE7115.00 (659125) 115 kV Bus a. Apply fault at the DICKINSN-BE7115.00 (659125) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE7 (659125) 115.0 kV to DICKINS2-BE7 (659195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_406 | 3 Phase fault on DICKINSN-BE7115.00 (659125) 115 kV Bus a. Apply fault at the DICKINSN-BE7115.00 (659125) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE7 (659125) 115.0 kV to WDICKSN7 (661024) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_407 | 3 Phase fault on DICKINSN-BE7115.00 (659125) 115 kV Bus a. Apply fault at the DICKINSN-BE7115.00 (659125) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE7 (659125) 115.0 kV to N ENGLN7 (661070) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_408 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_409 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_410 | 3 Phase fault on NRTSHORE-BE7115.00 (659141) 115 kV Bus a. Apply fault at the NRTSHORE-BE7115.00 (659141) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE7 (659141) 115.0 kV to BEPCPRXCC2 7 (659580) 115.0 kV Transmission Circuit #x1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_411 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_412 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_413 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_414 | 3 Phase fault on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_CT4-5-BE7 (659154) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_415 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_416 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_417 | 3 Phase fault on CROCKER_-BE3345.00 (659165) 345 kV Bus a. Apply fault at the CROCKER_-BE3345.00 (659165) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_418 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_419 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_422 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_423 | 3 Phase fault on DICKINS2-BE7115.00 (659195) 115 kV Bus a. Apply fault at the DICKINS2-BE7115.00 (659195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINS2-BE7 (659195) 115.0 kV to MATHSON7 (661019) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_424 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_425 | 3 Phase fault on HEADRESS-CM7115.00 (659259) 115 kV Bus a. Apply fault at the HEADRESS-CM7115.00 (659259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRESS-CM7 (659259) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_426 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_427 | 3 Phase fault on LITTL_MS-BE4230.00 (659265) 230 kV Bus a. Apply fault at the LITTL_MS-BE4230.00 (659265) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_429 | 3 Phase fault on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RHAME___-BE4 (659266) 230.0 kV to BOWMAN__-BE4 (659339) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | 1 - Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. 2- Reclosing removed. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25W | Transfer | G01_P1_Local_Fault_430 | 3 Phase fault on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RHAME___-BE4 (659266) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_431 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to 32STREET-RR7 (659442) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_432 | 3 Phase fault on S.HEART_-RR7115.00 (659306) 115 kV Bus a. Apply fault at the S.HEART_-RR7115.00 (659306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HEART_-RR7 (659306) 115.0 kV to PRNGHORN-RR7 (659544) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_433 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_434 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_435 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_436 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_437 | 3 Phase fault on BOWMAN__-BE4230.00 (659339) 230 kV Bus a. Apply fault at the BOWMAN__-BE4230.00 (659339) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN__-BE4 (659339) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | 1 - Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. 2- Reclosing removed. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25W | Transfer | G01_P1_Local_Fault_438 | 3 Phase fault on BOWMAN__-BE7115.00 (659340) 115 kV Bus a. Apply fault at the BOWMAN__-BE7115.00 (659340) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN__-BE7 (659340) 115.0 kV to NBURR___-GE7 (659341) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_439 | 3 Phase fault on LC_SWY.S-BE7115.00 (659346) 115 kV Bus a. Apply fault at the LC_SWY.S-BE7115.00 (659346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.S-BE7 (659346) 115.0 kV to GEN-2020-014 (764180) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_440 | 3 Phase fault on LC_CT1-3-BE7115.00 (659348) 115 kV Bus a. Apply fault at the LC_CT1-3-BE7115.00 (659348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_CT1-3-BE7 (659348) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_441 | 3 Phase fault on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_442 | 3 Phase fault on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_443 | 3 Phase fault on BISON___-GE4230.00 (659351) 230 kV Bus a. Apply fault at the BISON___-GE4230.00 (659351) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_444 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_445 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_446 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_447 | 3 Phase fault on KUMMERDG-MK7115.00 (659388) 115 kV Bus a. Apply fault at the KUMMERDG-MK7115.00 (659388) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to BEPCPRXCC3 7 (659584) 115.0 kV Transmission Circuit #x1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_448 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_449 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_450 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_451 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_452 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_453 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_456 | 3 Phase fault on WDICKSN7 115.00 (661024) 115 kV Bus a. Apply fault at the WDICKSN7 115.00 (661024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WDICKSN7 (661024) 115.0 kV to DIXREF 7 (661028) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_457 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_458 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_459 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_460 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_461 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_462 | 3 Phase fault on MAURINE7 115.00 (652480) 115 kV Bus a. Apply fault at the MAURINE7 115.00 (652480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE8 (652248) 69.0 kV to MAURINE7 (652480) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_463 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_464 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_465 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_466 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_467 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_468 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_470 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_471 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_472 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_473 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_474 | 3 Phase fault on MAURINE4 230.00 (652497) 230 kV Bus a. Apply fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV to MAURINE9 (652247) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_475 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_476 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_477 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_478 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_479 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_480 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_482 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_483 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF29 (652233) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_484 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_485 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_486 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_487 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_488 | 3 Phase fault on LETCHER4 230.00 (652606) 230 kV Bus a. Apply fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_489 | 3 Phase fault on CARPENTER 4 230.00 (652614) 230 kV Bus a. Apply fault at the CARPENTER 4 230.00 (652614) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARPENTER 4 (652614) 230.0 kV to CARPENTR-ER8 (655499) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_490 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_491 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_492 | 3 Phase fault on SULLYBT-ER4 230.00 (655487) 230 kV Bus a. Apply fault at the SULLYBT-ER4 230.00 (655487) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SULLYBT-ER4 (655487) 230.0 kV to SULLYBT-ER8 (655488) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_493 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_494 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_495 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_496 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_497 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_498 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_499 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_500 | 3 Phase fault on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_501 | 3 Phase fault on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DICKNSON 9 (560122) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_502 | 3 Phase fault on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DK.KW1A_-BE9 (659197) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_503 | 3 Phase fault on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKINSN-BE4 (659124) 230.0 kV to DICKINS2-BE7 (659195) 115.0 kV to DK.KW1A_-BE9 (659196) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_504 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_505 | 3 Phase fault on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_506 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_507 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_508 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE8 (659198) 115.0 kV to GRT.KU2A-BE8 (659699) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_509 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_510 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_511 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_512 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_513 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_514 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_515 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_517 | 3 Phase fault on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RHAME___-BE4 (659266) 230.0 kV to RHAME___-BE7 (659267) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_518 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_519 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_520 | 3 Phase fault on BOWMAN__-BE4230.00 (659339) 230 kV Bus a. Apply fault at the BOWMAN__-BE4230.00 (659339) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN__-BE7 (659340) 115.0 kV to BOWMAN__-BE4 (659339) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25W | Transfer | G01_P1_Local_Fault_521 | 3 Phase fault on BISON___-GE4230.00 (659351) 230 kV Bus a. Apply fault at the BISON___-GE4230.00 (659351) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_522 | 3 Phase fault on BISON___-GE4230.00 (659351) 230 kV Bus a. Apply fault at the BISON___-GE4230.00 (659351) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_523 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_524 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_525 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_526 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_527 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_528 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_529 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_531 | 3 Phase fault on HETINGR4 230.00 (661047) 230 kV Bus a. Apply fault at the HETINGR4 230.00 (661047) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HETINGR4 (661047) 230.0 kV to HETINGR7 (661048) 115.0 kV to HETINGR9 (661902) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25W | Transfer | G01_P1_Local_Fault_532 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_533 | 3 Phase fault on BDV 4230.00 (672603) 230 kV Bus a. Apply fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_534 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_535 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_536 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_537 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_538 | 3 Phase fault on MAURINE7 115.00 (652480) 115 kV Bus a. Apply fault at the MAURINE7 115.00 (652480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAURINE7 (652480) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_539 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_540 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_541 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_542 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_543 | 3 Phase fault on GRPRAR2-LNX3345.00 (652833) 345 kV Bus a. Apply fault at the GRPRAR2-LNX3345.00 (652833) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_544 | 3 Phase fault on NUNDRWD-LNX3230.00 (652884) 230 kV Bus a. Apply fault at the NUNDRWD-LNX3230.00 (652884) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD-LNX3 (652884) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_545 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_546 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_547 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_548 | 3 Phase fault on E.NEWTWN-MW7115.00 (655907) 115 kV Bus a. Apply fault at the E.NEWTWN-MW7115.00 (655907) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_549 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_552 | 3 Phase fault on NBURR___-GE7115.00 (659341) 115 kV Bus a. Apply fault at the NBURR___-GE7115.00 (659341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBURR___-GE7 (659341) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_554 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_555 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_556 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_557 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_558 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Local_Fault_559 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_560 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Local_Fault_561 | 3 Phase fault on BRADYWND 4230.00 (659450) 230 kV Bus a. Apply fault at the BRADYWND 4230.00 (659450) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRADYWND 4 (659450) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_001 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_002 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_003 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_004 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_005 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_006 | 3 Phase fault on BISON 3 345.00 (601067) 345 kV Bus a. Apply fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_007 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_008 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_009 | 3 Phase fault on HANKSON4 230.00 (620327) 230 kV Bus a. Apply fault at the HANKSON4 230.00 (620327) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_010 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_011 | 3 Phase fault on OAKES 4 230.00 (620362) 230 kV Bus a. Apply fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_012 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_013 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_014 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_015 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_016 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_017 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_018 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_019 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_020 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_021 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Base | G01_P1_Regional_Fault_022 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reclosing removed.
01 - North | 25W | Transfer | G01_P1_Regional_Fault_022 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in the base case. | Reclosing removed.
01 - North | 25W | Transfer | G01_P1_Regional_Fault_023 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_025 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_026 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.5. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_027 | 3 Phase fault on OAKES 4 230.00 (620362) 230 kV Bus a. Apply fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 b.8. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.9. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_028 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_029 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_030 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 b.4. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_031 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_032 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_033 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_034 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_035 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_036 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_037 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_038 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_039 | 3 Phase fault on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAIR-ER4 (655465) 230.0 kV to BLAIR-ER8 (655466) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_040 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_041 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_042 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_043 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_044 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_045 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_046 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_047 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_048 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_049 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_050 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_051 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_052 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_053 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_054 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_055 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_056 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_057 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_058 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_059 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_060 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_061 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_062 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_063 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_064 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_065 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_066 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_067 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to DEERCREK-BE3 (659286) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_068 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_069 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_070 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_071 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_072 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_073 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_074 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_075 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_076 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_077 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_078 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_079 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_080 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P1_Regional_Fault_081 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_082 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P1_Regional_Fault_083 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_001 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE8 (659198) 115.0 kV to GRT.KU2A-BE8 (659699) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_002 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_003 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_004 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_005 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_006 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_007 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_008 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_009 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_010 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_011 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_012 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_013 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_014 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_015 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_016 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_017 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_018 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_019 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_020 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_021 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_022 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_023 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_024 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_025 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_026 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_027 | Single Phase Fault with Stuck Breaker on CROCKER_-BE3345.00 (659165) 345 kV Bus a. Apply Fault at the CROCKER_-BE3345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_028 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_029 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_030 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_031 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_032 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_033 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_034 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_035 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_036 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_037 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_038 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_039 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_040 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_041 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_042 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_043 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_044 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_045 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_046 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.11. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_047 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_048 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_049 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_050 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_051 | Single Phase Fault with Stuck Breaker on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply Fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.5. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_052 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_053 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 b.2. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_054 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_055 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_056 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_057 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_058 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_059 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_060 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_061 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_062 | Single Phase Fault with Stuck Breaker on BD 6138.00 (672501) 138 kV Bus a. Apply Fault at the BD 6138.00 (672501) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD 4 (672601) 230.0 kV to BD 6 (672501) 138.0 kV Two Winding #1 b.2. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.3. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 b.4. BD 6 (672501) 138.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_063 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD 4 (672601) 230.0 kV to BD 6 (672501) 138.0 kV Two Winding #1 b.2. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.3. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_064 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 b.3. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_065 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 b.3. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_066 | Single Phase Fault with Stuck Breaker on RHAME___-BE4230.00 (659266) 230 kV Bus a. Apply Fault at the RHAME___-BE4230.00 (659266) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RHAME___-BE4 (659266) 230.0 kV to BOWMAN__-BE4 (659339) 230.0 kV Transmission Circuit #1 b.2. RHAME___-BE4 (659266) 230.0 kV to LITTL_MS-BE4 (659265) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_067 | Single Phase Fault with Stuck Breaker on HETINGR4 230.00 (661047) 230 kV Bus a. Apply Fault at the HETINGR4 230.00 (661047) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HETINGR4 (661047) 230.0 kV to BOWMAN__-BE4 (659339) 230.0 kV Transmission Circuit #1 b.2. HETINGR4 (661047) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Post fault steady state voltage at Bowman (659340), NBURR (659341), and HETINGR4 (661047) do not recover above 0.9 p.u. Additionally, Unit GEN-20-006 is unable to provide VAR support during the fault and eventually drops out due to the action of the unit's voltage protection causing voltages to rise above the threshold. | Adding a 80 MVAr STATCOM at Bowman 230 kV (659340) substation. | The issue may also be resolved by adjusting the controller of GEN-2020-006 to provide a more suitable response in terms of reactive support during the fault and after the fault is cleared.
01 - North | 25W | Transfer | G01_P4_Local_Fault_068 | Single Phase Fault with Stuck Breaker on GEN-2020-014115.00 (764180) 115 kV Bus a. Apply Fault at the GEN-2020-014115.00 (764180) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-014 (764180) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 b.2. GEN-2020-014 (764180) 115.0 kV to G20-014-GEN1 (764181) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_069 | Single Phase Fault with Stuck Breaker on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply Fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_070 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_071 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.2. CC.LS-LO-BE3 (659428) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_072 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_073 | Single Phase Fault with Stuck Breaker on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply Fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.2. RICHLAND-BE7 (659151) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_074 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_075 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU17A-BE7 (659466) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. PG.KU17A-BE7 (659466) 115.0 kV to PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_076 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU19A-BE7 (659467) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. PG.KU19A-BE7 (659467) 115.0 kV to PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_077 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_078 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_079 | Single Phase Fault with Stuck Breaker on RHAME___-BE4 (659266) 230 kV Bus a. Apply Fault at the RHAME___-BE4 (659266) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RHAME___-BE4 (659266) 230.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_080 | Single Phase Fault with Stuck Breaker on BOWMAN__-BE7 (659340) 115 kV Bus a. Apply Fault at the BOWMAN__-BE7 (659340) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOWMAN__-BE7 (659340) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_081 | Single Phase Fault with Stuck Breaker on HETINGR4 (661047) 230 kV Bus a. Apply Fault at the HETINGR4 (661047) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HETINGR4 (661047) 230.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_082 | Single Phase Fault with Stuck Breaker on ARNEGARD-MK7 (655841) 115 kV Bus a. Apply Fault at the ARNEGARD-MK7 (655841) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARNEGARD-MK7 (655841) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_083 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_CT4-5-BE7 (659154) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_084 | Single Phase Fault with Stuck Breaker on GEN-2020-014 (764180) 115 kV Bus a. Apply Fault at the GEN-2020-014 (764180) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-014 (764180) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_085 | Single Phase Fault with Stuck Breaker on LC_SWY.N-BE7 (659349) 115 kV Bus a. Apply Fault at the LC_SWY.N-BE7 (659349) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_086 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_087 | Single Phase Fault with Stuck Breaker on GEN-2020-021 (764210) 345 kV Bus a. Apply Fault at the GEN-2020-021 (764210) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-021 (764210) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_088 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_089 | Single Phase Fault with Stuck Breaker on WILISTN7 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_090 | Single Phase Fault with Stuck Breaker on SPRINGLK-LY7 (655791) 115 kV Bus a. Apply Fault at the SPRINGLK-LY7 (655791) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRINGLK-LY7 (655791) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_091 | Single Phase Fault with Stuck Breaker on NOHLEY -LY7 (655792) 115 kV Bus a. Apply Fault at the NOHLEY -LY7 (655792) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOHLEY -LY7 (655792) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_092 | Single Phase Fault with Stuck Breaker on RICHLAND-BE7 (659151) 115 kV Bus a. Apply Fault at the RICHLAND-BE7 (659151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAND-BE7 (659151) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Local_Fault_093 | Single Phase Fault with Stuck Breaker on GEN-2020-091 (764225) 345 kV Bus a. Apply Fault at the GEN-2020-091 (764225) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-091 (764225) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_094 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_095 | Single Phase Fault with Stuck Breaker on PG.KU17A-BE7 (659466) 115 kV Bus a. Apply Fault at the PG.KU17A-BE7 (659466) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU17A-BE7 (659466) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_096 | Single Phase Fault with Stuck Breaker on PG.KU19A-BE7 (659467) 115 kV Bus a. Apply Fault at the PG.KU19A-BE7 (659467) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU19A-BE7 (659467) 115.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_097 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Local_Fault_098 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV bus tripped | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_001 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_003 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_004 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_005 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_006 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Regional_Fault_007 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Regional_Fault_008 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_009 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_010 | Single Phase Fault with Stuck Breaker on BISON 3 345.00 (601067) 345 kV Bus a. Apply Fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.2. MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV to MAPLER19 (620359) 13.8 kV Three Winding #1 b.3. MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV to MAPLER29 (620360) 13.8 kV Three Winding #2 b.6. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_011 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_012 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 b.4. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_013 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_014 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Regional_Fault_015 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Regional_Fault_016 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Regional_Fault_017 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_018 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_019 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_020 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_021 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Regional_Fault_022 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillatory response observed in the active power output of GARISN5G (652461) unit which was also observed in the BC case. | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | G01_P4_Regional_Fault_023 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Regional_Fault_024 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Regional_Fault_025 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 b.3. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | G01_P4_Regional_Fault_026 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #1 b.3. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_001 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_002 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_003 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_004 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_005 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_006 | 3 Phase fault on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_006 | 3 Phase fault on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_007 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.2. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_008 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_009 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_010 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_011 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_012 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_013 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_014 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_015 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_016 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_017 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_018 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_019 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON4 (603149) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_020 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_021 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_022 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_023 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to PROSE CAP7 (603265) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_024 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_025 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_026 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_027 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_028 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_029 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_030 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_031 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.2. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_032 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_033 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to ROCK CO5 (602039) 161.0 kV Transmission Circuit #1 b.2. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_034 | 3 Phase fault on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_035 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_036 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_037 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_038 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_039 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_040 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_041 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_042 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_043 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_044 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_045 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_046 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_047 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_048 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_050 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_051 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_052 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_053 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_054 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_055 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_056 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_057 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_058 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_059 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_060 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_061 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_062 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_063 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_064 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_065 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_066 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_067 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_068 | 3 Phase fault on BRULE 7 115.00 (640091) 115 kV Bus a. Apply fault at the BRULE 7 115.00 (640091) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 b.2. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.3. BRULE 7 (640091) 115.0 kV to BRULE 9 (640092) 34.5 kV to BRULE T1 9 (643025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_069 | 3 Phase fault on INTERST_-TS7115.00 (659819) 115 kV Bus a. Apply fault at the INTERST_-TS7115.00 (659819) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to JULSTAP7 (640246) 115.0 kV Transmission Circuit #1 b.2. JULSTAP7 (640246) 115.0 kV to CHAPPEL7 (653300) 115.0 kV Transmission Circuit #1 b.3. JULSTAP7 (640246) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 b.4. CHAPPEL7 (653300) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.5. CHAPPEL7 (653300) 115.0 kV to CHAPPEL9 (653301) 34.5 kV Two Winding #1 b.6. SIDNEY 7 (653572) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.7. GEN-2016-147 (588220) 115.0 kV to SIDNEY 7 (653572) 115.0 kV Transmission Circuit #1 b.8. SIDNEY 7 (653572) 115.0 kV to SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 b.9. JULESBG7 (653302) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 b.10. HIGHLINE (653303) 115.0 kV to INTERST_-TS7 (659819) 115.0 kV Transmission Circuit #1 b.11. INTERST_-TS7 (659819) 115.0 kV to INTERSTW-TS8 (659827) 69.0 kV Two Winding #1 b.12. INTERST_-TS7 (659819) 115.0 kV to INTERSTE-TS8 (659828) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_070 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_071 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_072 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_073 | 3 Phase fault on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_074 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT_REACT7 (541517) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_075 | 3 Phase fault on MC REAC1 345.00 (541411) 345 kV Bus a. Apply fault at the MC REAC1 345.00 (541411) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MC REAC1 (541411) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_076 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MC REAC2 (541412) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_077 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MC REAC3 (541413) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_078 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_079 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_080 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_081 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_082 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_083 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_084 | 3 Phase fault on BYPASS 7 115.00 (641082) 115 kV Bus a. Apply fault at the BYPASS 7 115.00 (641082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_085 | 3 Phase fault on E7THST 7 115.00 (641085) 115 kV Bus a. Apply fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_086 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_087 | 3 Phase fault on E7THST 7 115.00 (641085) 115 kV Bus a. Apply fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_088 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_089 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.2. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_090 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_091 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_092 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_093 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_094 | 3 Phase fault on MC REAC1 345.00 (541411) 345 kV Bus a. Apply fault at the MC REAC1 345.00 (541411) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MC REAC1 (541411) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_095 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MC REAC2 (541412) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_096 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MC REAC3 (541413) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_097 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT_REACT7 (541517) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_098 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_099 | 3 Phase fault on NW70FAIRFD7 115.00 (650210) 115 kV Bus a. Apply fault at the NW70FAIRFD7 115.00 (650210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_100 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_101 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.6. 2&N 7 (650230) 115.0 kV Fixed Shunt Device | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_102 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_103 | 3 Phase fault on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.2. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.3. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_104 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_105 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_106 | 3 Phase fault on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_107 | 3 Phase fault on 84LEIGHTON7 115.00 (650267) 115 kV Bus a. Apply fault at the 84LEIGHTON7 115.00 (650267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_108 | 3 Phase fault on DAVEY 7 115.00 (640155) 115 kV Bus a. Apply fault at the DAVEY 7 115.00 (640155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVEY 7 (640155) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_109 | 3 Phase fault on 70&BLUFF 7 115.00 (650269) 115 kV Bus a. Apply fault at the 70&BLUFF 7 115.00 (650269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_110 | 3 Phase fault on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_111 | 3 Phase fault on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_112 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_113 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_114 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_115 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_116 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_117 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_118 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_119 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_120 | 3 Phase fault on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 b.4. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_121 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_122 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_123 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_124 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_125 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_126 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_127 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_128 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_129 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_130 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_131 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_132 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_133 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_134 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_135 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_136 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_137 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_138 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_139 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_140 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_141 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_142 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_143 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_144 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_145 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_146 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_147 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_148 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_149 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_150 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_151 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_152 | 3 Phase fault on WKNNY 3 115.00 (530560) 115 kV Bus a. Apply fault at the WKNNY 3 115.00 (530560) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_153 | 3 Phase fault on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_154 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_155 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_156 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_157 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_158 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_159 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_160 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_161 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_162 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_163 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_164 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_165 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_166 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_167 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_168 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_169 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_170 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_171 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_172 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_173 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_174 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_175 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_176 | 3 Phase fault on HARMONY7 115.00 (640210) 115 kV Bus a. Apply fault at the HARMONY7 115.00 (640210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARMONY7 (640210) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.2. HARMONY7 (640210) 115.0 kV to ST.FRANC (640351) 115.0 kV Transmission Circuit #1 b.3. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_177 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.2. STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_178 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_179 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.2 7 (640242) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 b.2. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_180 | 3 Phase fault on GOTHNBG7 115.00 (640196) 115 kV Bus a. Apply fault at the GOTHNBG7 115.00 (640196) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTHNBG7 (640196) 115.0 kV to JEFFREY7 (640238) 115.0 kV Transmission Circuit #1 b.2. COZAD 7 (640144) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_181 | 3 Phase fault on WESTMIN7 115.00 (640407) 115 kV Bus a. Apply fault at the WESTMIN7 115.00 (640407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.2 7 (640242) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.2. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_182 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_183 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_184 | 3 Phase fault on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.3. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_185 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_186 | 3 Phase fault on HEBRON 7 115.00 (640220) 115 kV Bus a. Apply fault at the HEBRON 7 115.00 (640220) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 7 (640220) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 b.2. HEBRN N7 (640218) 115.0 kV to HEBRON 7 (640220) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_187 | 3 Phase fault on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRYG (640170) 34.5 kV to FAIRBRY7 (640169) 115.0 kV to FAIRBURY T19 (643056) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_188 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_189 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_190 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.6. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_191 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_192 | 3 Phase fault on DAVEY 7 115.00 (640155) 115 kV Bus a. Apply fault at the DAVEY 7 115.00 (640155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVEY 7 (640155) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.2. DAVEY 7 (640155) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_193 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_194 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_195 | 3 Phase fault on W.POINT7 115.00 (640400) 115 kV Bus a. Apply fault at the W.POINT7 115.00 (640400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.2. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_196 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 b.2. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_197 | 3 Phase fault on COLTON__-TS7115.00 (659817) 115 kV Bus a. Apply fault at the COLTON__-TS7115.00 (659817) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY 7 (653572) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.2. CHAPPEL7 (653300) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.3. JULSTAP7 (640246) 115.0 kV to CHAPPEL7 (653300) 115.0 kV Transmission Circuit #1 b.4. B.SPRGS7 (640068) 115.0 kV to JULSTAP7 (640246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_198 | 3 Phase fault on BRULE 7 115.00 (640091) 115 kV Bus a. Apply fault at the BRULE 7 115.00 (640091) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 b.2. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_199 | 3 Phase fault on BLUECK 7 115.00 (640086) 115 kV Bus a. Apply fault at the BLUECK 7 115.00 (640086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECK 7 (640086) 115.0 kV to W.HORSE_-TS7 (659812) 115.0 kV Transmission Circuit #1 b.2. B.SPRGS7 (640068) 115.0 kV to BLUECK 7 (640086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_200 | 3 Phase fault on SPCREEK_-TS7115.00 (659810) 115 kV Bus a. Apply fault at the SPCREEK_-TS7115.00 (659810) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR___-TS7 (659804) 115.0 kV to SPCREEK_-TS7 (659810) 115.0 kV Transmission Circuit #1 b.2. GRANTNB_-TS7 (659800) 115.0 kV to SPCREEK_-TS7 (659810) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_201 | 3 Phase fault on CRETE___-TS7115.00 (659813) 115 kV Bus a. Apply fault at the CRETE___-TS7115.00 (659813) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR___-TS7 (659804) 115.0 kV to CRETE___-TS7 (659813) 115.0 kV Transmission Circuit #1 b.2. CRETE___-TS7 (659813) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 b.3. ATHEY 7 (641244) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 b.4. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_202 | 3 Phase fault on ROSCOE__-TS7115.00 (659809) 115 kV Bus a. Apply fault at the ROSCOE__-TS7115.00 (659809) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA_-TS7 (659801) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.2. ELSIETP_-TS7 (659807) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_203 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_204 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_205 | 3 Phase fault on CANADAY4 230.00 (640102) 230 kV Bus a. Apply fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_206 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_207 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_208 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_209 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_210 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_211 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_212 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_213 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_214 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_215 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_216 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_217 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_218 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_219 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_220 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_221 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_222 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_223 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_224 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_225 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_226 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_227 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_228 | 3 Phase fault on BOBCAT.C 3345.00 (640529) 345 kV Bus a. Apply fault at the BOBCAT.C 3345.00 (640529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT.C 7 (640530) 115.0 kV to BOBCAT.C 3 (640529) 345.0 kV to BOBCAT.C 9 (640531) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_229 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_230 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_231 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_232 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_233 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_234 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_235 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_236 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_237 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 b.4. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_238 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 b.4. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_239 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_240 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_241 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_242 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_243 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_244 | 3 Phase fault on GENEVA 8 69.000 (640179) 69 kV Bus a. Apply fault at the GENEVA 8 69.000 (640179) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 8 (640179) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_245 | 3 Phase fault on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRN N7 (640218) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_246 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_247 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_248 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_249 | 3 Phase fault on MCCOOK 8 69.000 (640270) 69 kV Bus a. Apply fault at the MCCOOK 8 69.000 (640270) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_250 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_251 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_252 | 3 Phase fault on ORLEANS8 69.000 (640311) 69 kV Bus a. Apply fault at the ORLEANS8 69.000 (640311) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS8 (640311) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_253 | 3 Phase fault on SUTTON 8 69.000 (640373) 69 kV Bus a. Apply fault at the SUTTON 8 69.000 (640373) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 8 (640373) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_254 | 3 Phase fault on VALENTN7 115.00 (640392) 115 kV Bus a. Apply fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALENTN7 (640392) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_255 | 3 Phase fault on STEELEC7 115.00 (640426) 115 kV Bus a. Apply fault at the STEELEC7 115.00 (640426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEELEC7 (640426) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_256 | 3 Phase fault on HILDRTH8 69.000 (640223) 69 kV Bus a. Apply fault at the HILDRTH8 69.000 (640223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_257 | 3 Phase fault on BASSETT 7115.00 (640580) 115 kV Bus a. Apply fault at the BASSETT 7115.00 (640580) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 7 (640580) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_258 | 3 Phase fault on BASSETT 869.000 (640581) 69 kV Bus a. Apply fault at the BASSETT 869.000 (640581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 8 (640581) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_259 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_260 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_261 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_262 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_263 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_264 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_265 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_266 | 3 Phase fault on GRNBURG3 115.00 (539664) 115 kV Bus a. Apply fault at the GRNBURG3 115.00 (539664) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.3. SUNCITY3 (539697) 115.0 kV to SUNCITY1 (539733) 34.5 kV to SUNCT-T (539937) 2.4 kV Three Winding #1 b.4. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.5. GRNBURG3 (539664) 115.0 kV to GRNBURG1 (539710) 34.5 kV to GRNBUG-T (539910) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_267 | 3 Phase fault on FORD 3 115.00 (539758) 115 kV Bus a. Apply fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.3. FORD 3 (539758) 115.0 kV to FORD 1 (539765) 34.5 kV to FORD T (539968) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_268 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_269 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_270 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_271 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_272 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.2. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.3. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 b.4. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.6. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_273 | 3 Phase fault on DCBEEF3 115.00 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 115.00 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_274 | 3 Phase fault on SPEARVL3 115.00 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 115.00 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_275 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_276 | 3 Phase fault on S-DODGE3 115.00 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 115.00 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115.0 kV to W-DODGE3 (539699) 115.0 kV Transmission Circuit #1 b.2. S-DODGE3 (539688) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.3. S-DODGE3 (539688) 115.0 kV to S-DODGE1 (539727) 34.5 kV to S-DODG-T (539930) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_277 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_278 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_279 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_280 | 3 Phase fault on GRNLEAF3 115.00 (539665) 115 kV Bus a. Apply fault at the GRNLEAF3 115.00 (539665) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.2. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.3. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_281 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_282 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_283 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_284 | 3 Phase fault on GRANTNB_-TS7115.00 (659800) 115 kV Bus a. Apply fault at the GRANTNB_-TS7115.00 (659800) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTNB_-TS7 (659800) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_285 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_286 | 3 Phase fault on SPCREEK_-TS7115.00 (659810) 115 kV Bus a. Apply fault at the SPCREEK_-TS7115.00 (659810) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTNB_-TS7 (659800) 115.0 kV to SPCREEK_-TS7 (659810) 115.0 kV Transmission Circuit #1 b.2. LAMAR___-TS7 (659804) 115.0 kV to SPCREEK_-TS7 (659810) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_287 | 3 Phase fault on CRETE___-TS7115.00 (659813) 115 kV Bus a. Apply fault at the CRETE___-TS7115.00 (659813) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR___-TS7 (659804) 115.0 kV to CRETE___-TS7 (659813) 115.0 kV Transmission Circuit #1 b.2. CRETE___-TS7 (659813) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 b.3. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 b.4. ATHEY 7 (641244) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_288 | 3 Phase fault on BLUECK 7 115.00 (640086) 115 kV Bus a. Apply fault at the BLUECK 7 115.00 (640086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECK 7 (640086) 115.0 kV to W.HORSE_-TS7 (659812) 115.0 kV Transmission Circuit #1 b.2. COLDWATR-TS7 (659802) 115.0 kV to W.HORSE_-TS7 (659812) 115.0 kV Transmission Circuit #1 b.3. B.SPRGS7 (640068) 115.0 kV to BLUECK 7 (640086) 115.0 kV Transmission Circuit #1 b.4. BLUECK 7 (640086) 115.0 kV to BLUECK 9 (640087) 34.5 kV to BLUECREEKT19 (643022) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_289 | 3 Phase fault on BRULE 7 115.00 (640091) 115 kV Bus a. Apply fault at the BRULE 7 115.00 (640091) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 b.2. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.3. BRULE 7 (640091) 115.0 kV to BRULE 9 (640092) 34.5 kV to BRULE T1 9 (643025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_290 | 3 Phase fault on JULSTAP7 115.00 (640246) 115 kV Bus a. Apply fault at the JULSTAP7 115.00 (640246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to JULSTAP7 (640246) 115.0 kV Transmission Circuit #1 b.2. JULSTAP7 (640246) 115.0 kV to CHAPPEL7 (653300) 115.0 kV Transmission Circuit #1 b.3. JULSTAP7 (640246) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 b.4. CHAPPEL7 (653300) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.5. SIDNEY 7 (653572) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_291 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_292 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_293 | 3 Phase fault on GRANTNB_-TS7115.00 (659800) 115 kV Bus a. Apply fault at the GRANTNB_-TS7115.00 (659800) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTNB_-TS7 (659800) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_294 | 3 Phase fault on MARSHAL3 115.00 (533303) 115 kV Bus a. Apply fault at the MARSHAL3 115.00 (533303) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHAL3 (533303) 115.0 kV to KNOB HL3 (533332) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_295 | 3 Phase fault on KNOB HL3 115.00 (533332) 115 kV Bus a. Apply fault at the KNOB HL3 115.00 (533332) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_296 | 3 Phase fault on KNOB HL3 115.00 (533332) 115 kV Bus a. Apply fault at the KNOB HL3 115.00 (533332) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOB HL3 (533332) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_297 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_298 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_299 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_300 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_301 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_302 | 3 Phase fault on KNOB HL3 115.00 (533332) 115 kV Bus a. Apply fault at the KNOB HL3 115.00 (533332) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOB HL3 (533332) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_303 | 3 Phase fault on INTERST_-TS7115.00 (659819) 115 kV Bus a. Apply fault at the INTERST_-TS7115.00 (659819) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to JULSTAP7 (640246) 115.0 kV Transmission Circuit #1 b.2. JULSTAP7 (640246) 115.0 kV to CHAPPEL7 (653300) 115.0 kV Transmission Circuit #1 b.3. JULSTAP7 (640246) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 b.4. CHAPPEL7 (653300) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.5. CHAPPEL7 (653300) 115.0 kV to CHAPPEL9 (653301) 34.5 kV Two Winding #1 b.6. SIDNEY 7 (653572) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.7. JULESBG7 (653302) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 b.8. HIGHLINE (653303) 115.0 kV to INTERST_-TS7 (659819) 115.0 kV Transmission Circuit #1 b.9. INTERST_-TS7 (659819) 115.0 kV to INTERSTW-TS8 (659827) 69.0 kV Two Winding #1 b.10. INTERST_-TS7 (659819) 115.0 kV to INTERSTE-TS8 (659828) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_304 | 3 Phase fault on VETAL_TP-RM7115.00 (659153) 115 kV Bus a. Apply fault at the VETAL_TP-RM7115.00 (659153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.2. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_305 | 3 Phase fault on WITTEN__-RB7115.00 (659166) 115 kV Bus a. Apply fault at the WITTEN__-RB7115.00 (659166) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.2. WINNER 7 (652494) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_306 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_307 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_308 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_309 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_310 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_311 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_312 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 b.2. STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 b.3. STEGALL_-MB9 (659167) 13.8 kV to STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_313 | 3 Phase fault on GRANTNB_-TS7115.00 (659800) 115 kV Bus a. Apply fault at the GRANTNB_-TS7115.00 (659800) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTNB_-TS7 (659800) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_314 | 3 Phase fault on DH_CS_EA-TS4230.00 (659829) 230 kV Bus a. Apply fault at the DH_CS_EA-TS4230.00 (659829) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEYW4 (652584) 230.0 kV to DH_CS.WE-TS4 (659830) 230.0 kV Transmission Circuit #x1 b.2. NB WEST4 (652585) 230.0 kV to DH_CS.WE-TS4 (659830) 230.0 kV Transmission Circuit #x1 b.3. DH_CS.WE-TS4 (659830) 230.0 kV Fixed Shunt Device b.4. DH_CS_EA-TS4 (659829) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_315 | 3 Phase fault on B.SPRGS7 115.00 (640068) 115 kV Bus a. Apply fault at the B.SPRGS7 115.00 (640068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to BLUECK 7 (640086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_316 | 3 Phase fault on BRULE 7 115.00 (640091) 115 kV Bus a. Apply fault at the BRULE 7 115.00 (640091) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 b.2. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.3. BRULE 7 (640091) 115.0 kV to BRULE 9 (640092) 34.5 kV to BRULE T1 9 (643025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_317 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_318 | 3 Phase fault on GRANTNB_-TS7115.00 (659800) 115 kV Bus a. Apply fault at the GRANTNB_-TS7115.00 (659800) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTNB_-TS7 (659800) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_319 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_320 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_321 | 3 Phase fault on OGALALA_-TS7115.00 (659801) 115 kV Bus a. Apply fault at the OGALALA_-TS7115.00 (659801) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA_-TS7 (659801) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_322 | 3 Phase fault on OGALALA_-TS7115.00 (659801) 115 kV Bus a. Apply fault at the OGALALA_-TS7115.00 (659801) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA_-TS7 (659801) 115.0 kV to MCONGHY_-TS7 (659824) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_323 | 3 Phase fault on ROSCOE__-TS7115.00 (659809) 115 kV Bus a. Apply fault at the ROSCOE__-TS7115.00 (659809) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA_-TS7 (659801) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.2. ELSIETP_-TS7 (659807) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_324 | 3 Phase fault on ELSIETP_-TS7115.00 (659807) 115 kV Bus a. Apply fault at the ELSIETP_-TS7115.00 (659807) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA_-TS7 (659801) 115.0 kV to MCONGHY_-TS7 (659824) 115.0 kV Transmission Circuit #1 b.2. MCONGHY_-TS7 (659824) 115.0 kV to ARTHUR__-TS7 (659825) 115.0 kV Transmission Circuit #1 b.3. ELSIETP_-TS7 (659807) 115.0 kV to PAXTON__-TS7 (659808) 115.0 kV Transmission Circuit #1 b.4. ELSIETP_-TS7 (659807) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.5. ELSIETP_-TS7 (659807) 115.0 kV to ELSIE___-TS7 (659822) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_325 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_326 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SD.LS-KS-MB3 (659425) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_327 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z b.2. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.3. SD.LS-LR-MB3 (659426) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_328 | 3 Phase fault on WINNER 7 115.00 (652494) 115 kV Bus a. Apply fault at the WINNER 7 115.00 (652494) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREGORY7 (652478) 115.0 kV to WINNER 7 (652494) 115.0 kV Transmission Circuit #1 b.2. WINNER 7 (652494) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.3. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_329 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_330 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_331 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_332 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_333 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_334 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_335 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_336 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_337 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_338 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_339 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_340 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_341 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_342 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_343 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_344 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_345 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_346 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_347 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_348 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_349 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_350 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_351 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_352 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_353 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_354 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_355 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_356 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_357 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_358 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_359 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_360 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_361 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_362 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_363 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_364 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_365 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_366 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_367 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_368 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_369 | 3 Phase fault on S1234 5 161.00 (646234) 161 kV Bus a. Apply fault at the S1234 5 161.00 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_370 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_371 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_372 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_373 | 3 Phase fault on S1244 5 161.00 (646244) 161 kV Bus a. Apply fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_374 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_375 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_376 | 3 Phase fault on S1297 5 161.00 (646297) 161 kV Bus a. Apply fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.2. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_377 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_378 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_379 | 3 Phase fault on S1254 5 161.00 (646254) 161 kV Bus a. Apply fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_380 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_381 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_382 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_383 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_384 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_385 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_386 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_387 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_388 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_389 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_390 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_391 | 3 Phase fault on S1361 5 161.00 (646361) 161 kV Bus a. Apply fault at the S1361 5 161.00 (646361) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1361 5 (646361) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_392 | 3 Phase fault on PLTSMTH8 69.000 (640320) 69 kV Bus a. Apply fault at the PLTSMTH8 69.000 (640320) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLTSMTH8 (640320) 69.0 kV to S961 8 (647961) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_393 | 3 Phase fault on PLTSMTH8 69.000 (640320) 69 kV Bus a. Apply fault at the PLTSMTH8 69.000 (640320) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLTSMTH8 (640320) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_394 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_395 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_396 | 3 Phase fault on 991TP 8 69.000 (647091) 69 kV Bus a. Apply fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 991TP 8 (647091) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 b.2. 991TP 8 (647091) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.3. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_397 | 3 Phase fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_398 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_399 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S972 8 (647972) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_400 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_401 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_402 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_403 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_404 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_405 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_406 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_407 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_408 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_409 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_410 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_411 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_412 | 3 Phase fault on S917 8 69.000 (647917) 69 kV Bus a. Apply fault at the S917 8 69.000 (647917) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_413 | 3 Phase fault on S918 8 69.000 (647918) 69 kV Bus a. Apply fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_414 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_415 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_416 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_417 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_418 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_419 | 3 Phase fault on S930 8 69.000 (647930) 69 kV Bus a. Apply fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_420 | 3 Phase fault on S972 8 69.000 (647972) 69 kV Bus a. Apply fault at the S972 8 69.000 (647972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S972 8 (647972) 69.0 kV to S982 8 (647982) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_421 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. S991 E 8 (647291) 69.0 kV to S1291 5 (646291) 161.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_422 | 3 Phase fault on ASH GRV8 69.000 (647100) 69 kV Bus a. Apply fault at the ASH GRV8 69.000 (647100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_423 | 3 Phase fault on 990TP 8 69.000 (647090) 69 kV Bus a. Apply fault at the 990TP 8 69.000 (647090) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 990TP 8 (647090) 69.0 kV to S971 8 (647971) 69.0 kV Transmission Circuit #1 b.2. 990TP 8 (647090) 69.0 kV to S982 8 (647982) 69.0 kV Transmission Circuit #1 b.3. 990TP 8 (647090) 69.0 kV to S990 8 (647990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_424 | 3 Phase fault on 979TP 8 69.000 (647079) 69 kV Bus a. Apply fault at the 979TP 8 69.000 (647079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 979TP 8 (647079) 69.0 kV to S979 8 (647979) 69.0 kV Transmission Circuit #1 b.2. 979TP 8 (647079) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.3. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_425 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_426 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_427 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_428 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_429 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_430 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_431 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_432 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_433 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_434 | 3 Phase fault on S3761 3 345.00 (645761) 345 kV Bus a. Apply fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_435 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_436 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_437 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_438 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_439 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_440 | 3 Phase fault on S6866 8 69.000 (647866) 69 kV Bus a. Apply fault at the S6866 8 69.000 (647866) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_441 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_442 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_443 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_444 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_445 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_446 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_447 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_448 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_449 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_450 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_451 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_452 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_453 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_454 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_455 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_456 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_457 | 3 Phase fault on J1620 POI 115.00 (46207) 115 kV Bus a. Apply fault at the J1620 POI 115.00 (46207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1620 POI (46207) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_458 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_459 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_460 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_461 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_462 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_463 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_464 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_465 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_466 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_467 | 3 Phase fault on BEACH 3 115.00 (530557) 115 kV Bus a. Apply fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_468 | 3 Phase fault on WKNNY 3 115.00 (530560) 115 kV Bus a. Apply fault at the WKNNY 3 115.00 (530560) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_469 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_470 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_471 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_472 | 3 Phase fault on N HAYS3 115.00 (530581) 115 kV Bus a. Apply fault at the N HAYS3 115.00 (530581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_473 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G20-070-TAP (765035) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_474 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_475 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_476 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_477 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_478 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_479 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_480 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_481 | 3 Phase fault on MARSHAL3 115.00 (533303) 115 kV Bus a. Apply fault at the MARSHAL3 115.00 (533303) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHAL3 (533303) 115.0 kV to SMITTYV3 (533338) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_482 | 3 Phase fault on NW-DGTP3 115.00 (539628) 115 kV Bus a. Apply fault at the NW-DGTP3 115.00 (539628) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DGTP3 (539628) 115.0 kV to W-DODGE3 (539699) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_483 | 3 Phase fault on DCBEEF3 115.00 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 115.00 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_484 | 3 Phase fault on DCBEEF3 115.00 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 115.00 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_485 | 3 Phase fault on CLIFTON3 115.00 (539656) 115 kV Bus a. Apply fault at the CLIFTON3 115.00 (539656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_486 | 3 Phase fault on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_487 | 3 Phase fault on GRNBURG3 115.00 (539664) 115 kV Bus a. Apply fault at the GRNBURG3 115.00 (539664) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_488 | 3 Phase fault on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_489 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_490 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_491 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_492 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_493 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_494 | 3 Phase fault on FORD 3 115.00 (539758) 115 kV Bus a. Apply fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_495 | 3 Phase fault on FORD 3 115.00 (539758) 115 kV Bus a. Apply fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_496 | 3 Phase fault on SSTARW 3 115.00 (539761) 115 kV Bus a. Apply fault at the SSTARW 3 115.00 (539761) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SSTARW 3 (539761) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_497 | 3 Phase fault on NFTDODG3 115.00 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 115.00 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115.0 kV to GEN-2019-044 (763758) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_498 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_499 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to TRANSFORMER (539813) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_500 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_501 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_502 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_503 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_504 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_505 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_506 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_507 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_508 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_509 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Voltage relay trip at LAKERD1 (541171) due to low voltage following the fault. The issue is only observed in transfer case. | Operational steady state fixes (existing caps/taps/gen set points).
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_510 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Voltage relay trip at LAKERD1 (541171) due to high voltage following the fault. The issue is only observed in transfer case. | Operational steady state fixes (existing caps/taps/gen set points).
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_511 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Voltage relay trip at LAKERD1 (541171) due to low voltage following the fault. The issue is only observed in transfer case. | Operational steady state fixes (existing caps/taps/gen set points).
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_512 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_513 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reduce acceleration factor to 0.1.
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_514 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_515 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_516 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_517 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_518 | 3 Phase fault on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_519 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_520 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_521 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_522 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_523 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_524 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_525 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_526 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_527 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_528 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to G20-070-TAP (765035) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_529 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_530 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_531 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_532 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_533 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_534 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_535 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_536 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REMSEN 3 (635398) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_537 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_538 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to GLACIAL EDGE (637009) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_539 | 3 Phase fault on AINSWND7 115.00 (640050) 115 kV Bus a. Apply fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_540 | 3 Phase fault on AINSWND7 115.00 (640050) 115 kV Bus a. Apply fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_541 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_542 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_543 | 3 Phase fault on ATKINSN7 115.00 (640058) 115 kV Bus a. Apply fault at the ATKINSN7 115.00 (640058) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATKINSN7 (640058) 115.0 kV to EMMET 7 (640165) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_544 | 3 Phase fault on ATKINSN7 115.00 (640058) 115 kV Bus a. Apply fault at the ATKINSN7 115.00 (640058) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATKINSN7 (640058) 115.0 kV to STUART 7 (640367) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_545 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_546 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_547 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_548 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_549 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_550 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_551 | 3 Phase fault on B.SPRGS7 115.00 (640068) 115 kV Bus a. Apply fault at the B.SPRGS7 115.00 (640068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_552 | 3 Phase fault on B.SPRGS7 115.00 (640068) 115 kV Bus a. Apply fault at the B.SPRGS7 115.00 (640068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to JULSTAP7 (640246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_553 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_554 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_555 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_556 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_557 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_558 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_559 | 3 Phase fault on BEEMER 7 115.00 (640078) 115 kV Bus a. Apply fault at the BEEMER 7 115.00 (640078) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_560 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_561 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_562 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_563 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_564 | 3 Phase fault on BLUECK 7 115.00 (640086) 115 kV Bus a. Apply fault at the BLUECK 7 115.00 (640086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECK 7 (640086) 115.0 kV to W.HORSE_-TS7 (659812) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_565 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_566 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_567 | 3 Phase fault on BRULE 7 115.00 (640091) 115 kV Bus a. Apply fault at the BRULE 7 115.00 (640091) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_568 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_569 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_570 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_571 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_572 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_573 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_574 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_575 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_576 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_577 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_578 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_579 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_580 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_581 | 3 Phase fault on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_582 | 3 Phase fault on CODY 7 115.00 (640117) 115 kV Bus a. Apply fault at the CODY 7 115.00 (640117) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CODY 7 (640117) 115.0 kV to G20-069-TAP (764475) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_583 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_584 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_585 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_586 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_587 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_588 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_589 | 3 Phase fault on DAVEY 7 115.00 (640155) 115 kV Bus a. Apply fault at the DAVEY 7 115.00 (640155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVEY 7 (640155) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_590 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_591 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_592 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_593 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_594 | 3 Phase fault on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_595 | 3 Phase fault on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRBRY7 (640169) 115.0 kV to G20-077-TAP (764490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_596 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_597 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_598 | 3 Phase fault on FRIEND 7 115.00 (640174) 115 kV Bus a. Apply fault at the FRIEND 7 115.00 (640174) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_599 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_600 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_601 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_602 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_603 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_604 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_605 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_606 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_607 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_608 | 3 Phase fault on GOSPER 7 115.00 (640194) 115 kV Bus a. Apply fault at the GOSPER 7 115.00 (640194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_609 | 3 Phase fault on GOTHNBG7 115.00 (640196) 115 kV Bus a. Apply fault at the GOTHNBG7 115.00 (640196) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTHNBG7 (640196) 115.0 kV to JEFFREY7 (640238) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_610 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_611 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_612 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_613 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_614 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_615 | 3 Phase fault on HARBINE7 115.00 (640208) 115 kV Bus a. Apply fault at the HARBINE7 115.00 (640208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_616 | 3 Phase fault on HARMONY7 115.00 (640210) 115 kV Bus a. Apply fault at the HARMONY7 115.00 (640210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARMONY7 (640210) 115.0 kV to ST.FRANC (640351) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_617 | 3 Phase fault on HARMONY7 115.00 (640210) 115 kV Bus a. Apply fault at the HARMONY7 115.00 (640210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARMONY7 (640210) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_618 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_619 | 3 Phase fault on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRN N7 (640218) 115.0 kV to HEBRON 7 (640220) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_620 | 3 Phase fault on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRN N7 (640218) 115.0 kV to G20-077-TAP (764490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_621 | 3 Phase fault on HEBRON 7 115.00 (640220) 115 kV Bus a. Apply fault at the HEBRON 7 115.00 (640220) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 7 (640220) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_622 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_623 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_624 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_625 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_626 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_627 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_628 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_629 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_630 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_631 | 3 Phase fault on HUMBOLT7 115.00 (640235) 115 kV Bus a. Apply fault at the HUMBOLT7 115.00 (640235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_632 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to JOHN.1 7 (640240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_633 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_634 | 3 Phase fault on JOHN.1 7 115.00 (640240) 115 kV Bus a. Apply fault at the JOHN.1 7 115.00 (640240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_635 | 3 Phase fault on JOHN.2 7 115.00 (640242) 115 kV Bus a. Apply fault at the JOHN.2 7 115.00 (640242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.2 7 (640242) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_636 | 3 Phase fault on JOHN.2 7 115.00 (640242) 115 kV Bus a. Apply fault at the JOHN.2 7 115.00 (640242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.2 7 (640242) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_637 | 3 Phase fault on JULSTAP7 115.00 (640246) 115 kV Bus a. Apply fault at the JULSTAP7 115.00 (640246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JULSTAP7 (640246) 115.0 kV to CHAPPEL7 (653300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_638 | 3 Phase fault on JULSTAP7 115.00 (640246) 115 kV Bus a. Apply fault at the JULSTAP7 115.00 (640246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JULSTAP7 (640246) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_639 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_640 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_641 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_642 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_643 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_644 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KINGSLY7 (640255) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_645 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_646 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_647 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to PROSSER7 (640321) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_648 | 3 Phase fault on MALONEY7 115.00 (640265) 115 kV Bus a. Apply fault at the MALONEY7 115.00 (640265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_649 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_650 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_651 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_652 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_653 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_654 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_655 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_656 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_657 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_658 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_659 | 3 Phase fault on ORLEANS7 115.00 (640310) 115 kV Bus a. Apply fault at the ORLEANS7 115.00 (640310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS7 (640310) 115.0 kV to G20-013-TAP (764445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_660 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_661 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_662 | 3 Phase fault on REDWILO7 115.00 (640326) 115 kV Bus a. Apply fault at the REDWILO7 115.00 (640326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_663 | 3 Phase fault on RIVERDL7 115.00 (640331) 115 kV Bus a. Apply fault at the RIVERDL7 115.00 (640331) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_664 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_665 | 3 Phase fault on ST.FRANC 115.00 (640351) 115 kV Bus a. Apply fault at the ST.FRANC 115.00 (640351) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_666 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_667 | 3 Phase fault on STUART 7 115.00 (640367) 115 kV Bus a. Apply fault at the STUART 7 115.00 (640367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STUART 7 (640367) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_668 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_669 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_670 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_671 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_673 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_674 | 3 Phase fault on STEELEC7 115.00 (640426) 115 kV Bus a. Apply fault at the STEELEC7 115.00 (640426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEELEC7 (640426) 115.0 kV to S.FLATS.PLT7 (640558) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_675 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_676 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_677 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_678 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_679 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to UPSTREAM.W 7 (643254) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_680 | 3 Phase fault on BOBCAT.C 3345.00 (640529) 345 kV Bus a. Apply fault at the BOBCAT.C 3345.00 (640529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT.C 3 (640529) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_681 | 3 Phase fault on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to RTLSNAKE.W 4 (640561) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_682 | 3 Phase fault on ROSEMONT 7115.00 (640583) 115 kV Bus a. Apply fault at the ROSEMONT 7115.00 (640583) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEMONT 7 (640583) 115.0 kV to COTTONWD 7 (640584) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_683 | 3 Phase fault on TURTLE.CRK 3345.00 (640588) 345 kV Bus a. Apply fault at the TURTLE.CRK 3345.00 (640588) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to PLUMBCR.W 3 (643271) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_684 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_685 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_686 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_687 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_688 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_689 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_690 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_691 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_692 | 3 Phase fault on S1236 5 161.00 (646236) 161 kV Bus a. Apply fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_693 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_694 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_695 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_696 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_697 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_698 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_699 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_700 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_701 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_702 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_703 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_704 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_705 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_706 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_707 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_708 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_709 | 3 Phase fault on 979TP 8 69.000 (647079) 69 kV Bus a. Apply fault at the 979TP 8 69.000 (647079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 979TP 8 (647079) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_710 | 3 Phase fault on 979TP 8 69.000 (647079) 69 kV Bus a. Apply fault at the 979TP 8 69.000 (647079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_711 | 3 Phase fault on 979TP 8 69.000 (647079) 69 kV Bus a. Apply fault at the 979TP 8 69.000 (647079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 979TP 8 (647079) 69.0 kV to S979 8 (647979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_712 | 3 Phase fault on 990TP 8 69.000 (647090) 69 kV Bus a. Apply fault at the 990TP 8 69.000 (647090) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 990TP 8 (647090) 69.0 kV to S982 8 (647982) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_713 | 3 Phase fault on 991TP 8 69.000 (647091) 69 kV Bus a. Apply fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 991TP 8 (647091) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_714 | 3 Phase fault on 991TP 8 69.000 (647091) 69 kV Bus a. Apply fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 991TP 8 (647091) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_715 | 3 Phase fault on 991TP 8 69.000 (647091) 69 kV Bus a. Apply fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_716 | 3 Phase fault on MUD LNG8 69.000 (647104) 69 kV Bus a. Apply fault at the MUD LNG8 69.000 (647104) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_717 | 3 Phase fault on S991 E 8 69.000 (647291) 69 kV Bus a. Apply fault at the S991 E 8 69.000 (647291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_718 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_719 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_720 | 3 Phase fault on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_721 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_722 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_723 | 3 Phase fault on 19&ALVO 7 115.00 (650215) 115 kV Bus a. Apply fault at the 19&ALVO 7 115.00 (650215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_724 | 3 Phase fault on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_725 | 3 Phase fault on 84LEIGHTON7 115.00 (650267) 115 kV Bus a. Apply fault at the 84LEIGHTON7 115.00 (650267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_726 | 3 Phase fault on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_727 | 3 Phase fault on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_728 | 3 Phase fault on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_729 | 3 Phase fault on MISSION7 115.00 (652482) 115 kV Bus a. Apply fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_730 | 3 Phase fault on MISSION7 115.00 (652482) 115 kV Bus a. Apply fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_731 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_732 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_733 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to DEERCREK-BE3 (659286) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_734 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_735 | 3 Phase fault on STEGALL4 230.00 (652573) 230 kV Bus a. Apply fault at the STEGALL4 230.00 (652573) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_736 | 3 Phase fault on CHAPPEL7 115.00 (653300) 115 kV Bus a. Apply fault at the CHAPPEL7 115.00 (653300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPPEL7 (653300) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_737 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_738 | 3 Phase fault on SIDNEY 7 115.00 (653572) 115 kV Bus a. Apply fault at the SIDNEY 7 115.00 (653572) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY 7 (653572) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_739 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_740 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_741 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_742 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_743 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_744 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_745 | 3 Phase fault on GRANTNB_-TS7115.00 (659800) 115 kV Bus a. Apply fault at the GRANTNB_-TS7115.00 (659800) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTNB_-TS7 (659800) 115.0 kV to SPCREEK_-TS7 (659810) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_746 | 3 Phase fault on LAMAR___-TS7115.00 (659804) 115 kV Bus a. Apply fault at the LAMAR___-TS7115.00 (659804) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR___-TS7 (659804) 115.0 kV to SPCREEK_-TS7 (659810) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_747 | 3 Phase fault on ELSIETP_-TS7115.00 (659807) 115 kV Bus a. Apply fault at the ELSIETP_-TS7115.00 (659807) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELSIETP_-TS7 (659807) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_748 | 3 Phase fault on MCONGHY_-TS7115.00 (659824) 115 kV Bus a. Apply fault at the MCONGHY_-TS7115.00 (659824) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCONGHY_-TS7 (659824) 115.0 kV to ARTHUR__-TS7 (659825) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_749 | 3 Phase fault on ARTHUR__-TS7115.00 (659825) 115 kV Bus a. Apply fault at the ARTHUR__-TS7115.00 (659825) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTHUR__-TS7 (659825) 115.0 kV to HYANNIS_-TS7 (659826) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_750 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_751 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_752 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_753 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_754 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_755 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_756 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_757 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_758 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_759 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_760 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_761 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_762 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_763 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT8 (640052) 69.0 kV to AINSWRT7 (640051) 115.0 kV to AINSWORTHT29 (643002) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_764 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_765 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_766 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG8 (640101) 69.0 kV to CAMBRIG7 (640100) 115.0 kV to CAMBRIDGET19 (643028) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_767 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 8 (640145) 69.0 kV to COZAD 7 (640144) 115.0 kV to COZAD T2 9 (643174) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_768 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_769 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK 8 (640162) 69.0 kV to ELMCRK_7 (640161) 115.0 kV to ELMCREEK T19 (643053) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_770 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 8 (640168) 69.0 kV to ENDERS 7 (640167) 115.0 kV to ENDERS T1 9 (643055) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_771 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 8 (640179) 69.0 kV to GENEVA 7 (640178) 115.0 kV to GENEVA T2 9 (643062) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_772 | 3 Phase fault on GOTHNBG7 115.00 (640196) 115 kV Bus a. Apply fault at the GOTHNBG7 115.00 (640196) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTHNBG8 (640197) 69.0 kV to GOTHNBG7 (640196) 115.0 kV to GOTHENBRGT29 (643068) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_773 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R8 (640207) 69.0 kV to GUIDE R7 (640206) 115.0 kV to GUIDEROCKT19 (643073) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_774 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV to HILDRTH7 (640222) 115.0 kV to HILDRETH T19 (643079) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_775 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_776 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.LK8 (640245) 69.0 kV to JOHN.LK7 (640244) 115.0 kV to JOHNSONLKT19 (643089) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_777 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNGTN8 (640257) 69.0 kV to LXNGTN 7 (640256) 115.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_778 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 8 (640262) 69.0 kV to LOWELL 7 (640261) 115.0 kV to LOWELL T1 9 (643096) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_779 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_780 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_781 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 8 (640273) 69.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_782 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT8 (640288) 69.0 kV to N.PLATT7 (640287) 115.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_783 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_784 | 3 Phase fault on ORLEANS7 115.00 (640310) 115 kV Bus a. Apply fault at the ORLEANS7 115.00 (640310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS8 (640311) 69.0 kV to ORLEANS7 (640310) 115.0 kV to ORLEANS T1 9 (643120) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_785 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_786 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to (659608) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_787 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_788 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_789 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 8 (640373) 69.0 kV to SUTTON 7 (640372) 115.0 kV to SUTTON T1 9 (643149) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_790 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT8 (640415) 69.0 kV to CARLJCT7 (640105) 115.0 kV to CARLTNJCTT29 (643031) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_791 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_792 | 3 Phase fault on YORK SW7 115.00 (640413) 115 kV Bus a. Apply fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK.SW T2 8 (640447) 69.0 kV to YORK SW7 (640413) 115.0 kV to YORK.SW T2 9 (643176) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_793 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_794 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to (994010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_795 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_796 | 3 Phase fault on BASSETT 7115.00 (640580) 115 kV Bus a. Apply fault at the BASSETT 7115.00 (640580) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 8 (640581) 69.0 kV to BASSETT 7 (640580) 115.0 kV to BASSETT T1 9 (643180) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_797 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_798 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_799 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_800 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S966 8 (647966) 69.0 kV to STEINER7 (640361) 115.0 kV to STEINER T1 9 (643143) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_801 | 3 Phase fault on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_802 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_803 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_804 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_805 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_806 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_807 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_808 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_809 | 3 Phase fault on MISSION7 115.00 (652482) 115 kV Bus a. Apply fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MISSION7 (652482) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_810 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_811 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_812 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Local_Fault_813 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-LR-MB3 (659426) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_001 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_002 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_003 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_004 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_005 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_006 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_007 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_008 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_009 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_010 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_011 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_012 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_014 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_015 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | G02_P1_Regional_Fault_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1.
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1.
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_017 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_018 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_019 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_020 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_021 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_022 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_023 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_024 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_025 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_026 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_027 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_028 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_029 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_030 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_031 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_032 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_033 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_034 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_035 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_036 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_037 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_038 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_039 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Voltage relay trip at LAKERD1 (541171) due to low voltage following the fault. The issue is only observed in transfer case. | Operational steady state fixes (existing caps/taps/gen set points).
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_040 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Voltage relay trip at LAKERD1 (541171) due to high voltage following the fault. The issue is only observed in transfer case. | Operational steady state fixes (existing caps/taps/gen set points).
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_041 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | Voltage relay trip at LAKERD1 (541171) due to low voltage following the fault. The issue is only observed in transfer case. | Operational steady state fixes (existing caps/taps/gen set points).
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_042 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_043 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_044 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_045 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_046 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_047 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_048 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_049 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_050 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_051 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_052 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_053 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to (659608) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_054 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_055 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_056 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Transfer | G02_P1_Regional_Fault_057 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_001 | Single Phase Fault with Stuck Breaker on LKFLDXL3 345.00 (601029) 345 kV Bus a. Apply Fault at the LKFLDXL3 345.00 (601029) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOBLES 3 (601034) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 b.2. GRE-TRIMWNDW (615100) 0.6 kV to GRE-TRIMWNA9 (615101) 34.5 kV Two Winding #1 b.3. GRE-TRIMWNA9 (615101) 34.5 kV to GRE-TRIMWNB9 (615102) 34.5 kV Transmission Circuit #z b.4. TRIMONT WD 3 (601068) 345.0 kV to GRE-TRIMWNB9 (615102) 34.5 kV Two Winding #1 b.5. GRE-ELMCWNDW (615104) 0.6 kV to GRE-ELMCWNA9 (615105) 34.5 kV Two Winding #1 b.6. GRE-ELMCWNA9 (615105) 34.5 kV to GRE-ELMCWNB9 (615106) 34.5 kV Transmission Circuit #z b.7. TRIMONT WD 3 (601068) 345.0 kV to GRE-ELMCWNB9 (615106) 34.5 kV Two Winding #1 b.8. ELMCREEK2 W8 (606025) 34.5 kV to ECRK2 FDR (606063) 34.5 kV Transmission Circuit #1 b.9. TRIMONT WD 3 (601068) 345.0 kV to ELMCREEK2 W8 (606025) 34.5 kV Two Winding #1 b.10. ECRK2 FDR (606063) 34.5 kV to G514 ECRK2 W (600134) 0.7 kV Two Winding #1 b.11. GRE-LGS 31G (615041) 13.8 kV to GRE-LKFDGEN3 (615040) 345.0 kV to GRE-LGS 32G (615042) 13.8 kV Three Winding #1 b.12. GRE-LGS 32G (615042) 13.8 kV to GRE-LKFDGEN3 (615040) 345.0 kV to GRE-LGS 31G (615041) 13.8 kV Three Winding #1 b.13. GRE-LGS 33G (615043) 13.8 kV to GRE-LKFDGEN3 (615040) 345.0 kV to GRE-LGS 34G (615044) 13.8 kV Three Winding #1 b.14. GRE-LGS 34G (615044) 13.8 kV to GRE-LKFDGEN3 (615040) 345.0 kV to GRE-LGS 33G (615043) 13.8 kV Three Winding #1 b.15. GRE-LGS 35G (615045) 13.8 kV to GRE-LKFDGEN3 (615040) 345.0 kV to GRE-LGS 36G (615046) 13.8 kV Three Winding #1 b.16. GRE-LGS 36G (615046) 13.8 kV to GRE-LKFDGEN3 (615040) 345.0 kV to GRE-LGS 35G (615045) 13.8 kV Three Winding #1 b.17. LKFLDXL3 (601029) 345.0 kV to TRIMONT WD 3 (601068) 345.0 kV Transmission Circuit #1 b.18. LKFLDXL3 (601029) 345.0 kV to CRANDAL 3 (601074) 345.0 kV Transmission Circuit #1 b.19. LKFLDXL3 (601029) 345.0 kV to GRE-LKFDGEN3 (615040) 345.0 kV Transmission Circuit #z b.20. LKFLDXL3 (601029) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_003 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_004 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_005 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_006 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_007 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_008 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_009 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOBLES 3 (601034) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_010 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOBLES 3 (601034) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_011 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_012 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_013 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.4. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_014 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_015 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_016 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_017 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_018 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_019 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_020 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_021 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_022 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_023 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_024 | Single Phase Fault with Stuck Breaker on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply Fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.3. OBRIEN 3 (635368) 345.0 kV to Fixed Shunt Device b.4. LAKEFLD3 (631138) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_025 | Single Phase Fault with Stuck Breaker on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply Fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV to OBRIEN B1 9 (635410) 34.5 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV to OBRIEN B2 9 (635411) 34.5 kV Two Winding #1 b.4. LAKEFLD3 (631138) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_026 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_027 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_028 | Single Phase Fault with Stuck Breaker on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B2 9 (635402) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_029 | Single Phase Fault with Stuck Breaker on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B3 9 (635403) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_030 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_031 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_032 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_033 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_034 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_035 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_036 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_037 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_038 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_039 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_040 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_041 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_042 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_043 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_044 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_045 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_046 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_047 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_048 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_049 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_050 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_051 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_052 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_053 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_054 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_055 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_056 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_057 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_058 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_059 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_060 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_061 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_062 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_063 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_064 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_065 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_066 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_067 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_068 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_069 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_070 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_071 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_072 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_073 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_074 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.2. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_075 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-TERT1 (539743) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV Three Winding #1 b.2. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 b.3. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.4. SVWF1-TX1 (539752) 34.5 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.7. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.9. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_076 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.4. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_077 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.2. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_078 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 b.4. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_079 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_080 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_081 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_082 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.2. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.3. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_083 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_084 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_085 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_086 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_087 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_088 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_089 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_090 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_091 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_092 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_093 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_094 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_095 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 b.4. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.5. HOLCOMB3 (531448) 115.0 kV to # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_096 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_097 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_098 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_099 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_100 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_101 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_102 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_103 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_104 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_105 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_106 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_107 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_108 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_109 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_110 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_111 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_112 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_113 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_114 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_115 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_116 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_117 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_118 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_119 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_120 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_121 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_122 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_123 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_124 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_125 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_126 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_127 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_128 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_129 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_130 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_131 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_132 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_133 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_134 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_135 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_136 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_137 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_138 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_139 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_140 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_141 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_142 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_143 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_144 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_145 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_146 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_147 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_148 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_149 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_150 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_151 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_152 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_153 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_154 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_155 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_156 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_157 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_158 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_159 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_160 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_161 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_162 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_163 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_164 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_165 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_166 | Single Phase Fault with Stuck Breaker on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply Fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_167 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_168 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_169 | Single Phase Fault with Stuck Breaker on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply Fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EGYCNTR7 (641087) 115.0 kV to EGY CTRG (641086) 13.8 kV Two Winding #1 b.2. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_170 | Single Phase Fault with Stuck Breaker on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply Fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EGYCNTR7 (641087) 115.0 kV to EGYCTR2G (641089) 18.0 kV Two Winding #1 b.2. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_171 | Single Phase Fault with Stuck Breaker on S. 281 7 115.00 (641090) 115 kV Bus a. Apply Fault at the S. 281 7 115.00 (641090) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. D.HENRY7 (641083) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 b.3. S. 281 9 (641096) 13.8 kV to S. 281 7 (641090) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_172 | Single Phase Fault with Stuck Breaker on S. 281 7 115.00 (641090) 115 kV Bus a. Apply Fault at the S. 281 7 115.00 (641090) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. D.HENRY7 (641083) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 b.3. S. 281 9 (641096) 13.8 kV to S. 281 7 (641090) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_173 | Single Phase Fault with Stuck Breaker on S. 281 7 115.00 (641090) 115 kV Bus a. Apply Fault at the S. 281 7 115.00 (641090) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. D.HENRY7 (641083) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 b.3. S. 281 9 (641096) 13.8 kV to S. 281 7 (641090) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_174 | Single Phase Fault with Stuck Breaker on BYPASS 7 115.00 (641082) 115 kV Bus a. Apply Fault at the BYPASS 7 115.00 (641082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BYPASS 9 (641091) 13.8 kV to BYPASS 7 (641082) 115.0 kV Two Winding #1 b.2. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_175 | Single Phase Fault with Stuck Breaker on E7THST 7 115.00 (641085) 115 kV Bus a. Apply Fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_176 | Single Phase Fault with Stuck Breaker on E7THST 7 115.00 (641085) 115 kV Bus a. Apply Fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_177 | Single Phase Fault with Stuck Breaker on E7THST 7 115.00 (641085) 115 kV Bus a. Apply Fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_178 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_179 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.5. POSTROCK7 (530583) 345.0 kV to G20-070-TAP (765035) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_180 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.2. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_181 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_182 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_183 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_184 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_185 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_186 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_187 | Single Phase Fault with Stuck Breaker on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply Fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_188 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_189 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_190 | Single Phase Fault with Stuck Breaker on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply Fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.5. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_191 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_192 | Single Phase Fault with Stuck Breaker on OGALATP3 115.00 (530677) 115 kV Bus a. Apply Fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.6. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.7. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_193 | Single Phase Fault with Stuck Breaker on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply Fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_194 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_195 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_196 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_197 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_198 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_199 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_200 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_201 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_202 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_203 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_204 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_205 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_206 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_207 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_208 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_209 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.5. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.6. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_210 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_211 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_212 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_213 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_214 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_215 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_216 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_217 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_218 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_219 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_220 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_221 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_222 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_223 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_224 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_225 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_226 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_227 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_228 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_229 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_230 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_231 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_232 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_233 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_234 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_235 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_236 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_237 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_238 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_239 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_240 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_241 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_242 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_243 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_244 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_245 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_246 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_247 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_248 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_249 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_250 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_251 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 b.5. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_252 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_253 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_254 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_255 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_256 | Single Phase Fault with Stuck Breaker on JULSTAP7 115.00 (640246) 115 kV Bus a. Apply Fault at the JULSTAP7 115.00 (640246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-147 (588220) 115.0 kV to SIDNEY 7 (653572) 115.0 kV Transmission Circuit #1 b.2. SIDNEY 7 (653572) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.3. SIDNEY 7 (653572) 115.0 kV to SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 b.4. B.SPRGS7 (640068) 115.0 kV to JULSTAP7 (640246) 115.0 kV Transmission Circuit #1 b.5. JULSTAP7 (640246) 115.0 kV to CHAPPEL7 (653300) 115.0 kV Transmission Circuit #1 b.6. JULSTAP7 (640246) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_257 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_258 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z b.3. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.4. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 b.5. SIDNEY__-MB9 (659168) 13.8 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_259 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.3. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_260 | Single Phase Fault with Stuck Breaker on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply Fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 b.2. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.3. LRS_1___-MBG (659118) 24.0 kV to LARAMIE_-MB3 (659131) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_261 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_262 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_263 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_264 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_265 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_266 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_267 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_268 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_269 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_270 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_271 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_272 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_273 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_274 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_275 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_276 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_277 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_278 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_279 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_280 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_281 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_282 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_283 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_284 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_285 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_286 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_287 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_288 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_289 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_290 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_291 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_292 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_293 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_294 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_295 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_296 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_297 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_298 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_299 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_300 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_301 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_302 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_303 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_304 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_305 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_306 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_307 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_308 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_309 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_310 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_311 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_312 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_313 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_314 | Single Phase Fault with Stuck Breaker on S1217 5 (646217) 161 kV Bus a. Apply Fault at the S1217 5 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_315 | Single Phase Fault with Stuck Breaker on S1217 5 (646217) 161 kV Bus a. Apply Fault at the S1217 5 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_316 | Single Phase Fault with Stuck Breaker on S1217 5 (646217) 161 kV Bus a. Apply Fault at the S1217 5 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_317 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_318 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_319 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_320 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_321 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_322 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_323 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S1366 5 (646366) 161.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_324 | Single Phase Fault with Stuck Breaker on S1251 5 (646251) 161 kV Bus a. Apply Fault at the S1251 5 (646251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_325 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_326 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_327 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_328 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_329 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_330 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_331 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_332 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_333 | Single Phase Fault with Stuck Breaker on S1366 5 (646366) 161 kV Bus a. Apply Fault at the S1366 5 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.8. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.9. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.10. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_334 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Voltage relay trip at GEN-2020-008 (764981) due to high voltage following the fault. The issue is only observed in transfer case. | Operational steady state fixes (existing caps/taps/gen set points).
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_335 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_336 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_337 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_338 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_339 | Single Phase Fault with Stuck Breaker on PHILL 5 161.00 (541225) 161 kV Bus a. Apply Fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 b.2. DOGWDCT1 (541163) 18.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 b.3. DOGWDCT2 (541164) 18.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 b.4. DOGWDSTG (541162) 18.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_340 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_341 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 b.3. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 b.4. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.6. MULLNCR7 (541197) 345.0 kV to GEN-2018-022 (762581) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_342 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.3. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.4. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_343 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.4. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 b.5. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T12 (543639) 13.8 kV Three Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_344 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.4. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.6. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_345 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 b.3. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 b.4. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.6. MULLNCR7 (541197) 345.0 kV to GEN-2018-022 (762581) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_346 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 b.3. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 b.4. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.6. MULLNCR7 (541197) 345.0 kV to GEN-2018-022 (762581) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_347 | Single Phase Fault with Stuck Breaker on OSBORN7 345.00 (541501) 345 kV Bus a. Apply Fault at the OSBORN7 345.00 (541501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to OSBORN7 (541501) 345.0 kV Transmission Circuit #1 b.2. OSBORN7 (541501) 345.0 kV to OSBORN_B1_1 (541502) 34.5 kV to OSBORN_TER_1 (541505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_348 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.3. HOLT 7 (541510) 345.0 kV to ROCKCK7 (541511) 345.0 kV Transmission Circuit #1 b.4. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.5. HOLT 7 (541510) 345.0 kV to GEN-2017-115 (760746) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_349 | Single Phase Fault with Stuck Breaker on ROCKCK7 345.00 (541511) 345 kV Bus a. Apply Fault at the ROCKCK7 345.00 (541511) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to ROCKCK7 (541511) 345.0 kV Transmission Circuit #1 b.2. ROCKCK7 (541511) 345.0 kV to OUTLAW (541543) 345.0 kV Transmission Circuit #1 b.3. ROCKCK7 (541511) 345.0 kV to ROCKCK_T1_1 (541512) 34.5 kV to ROCKCK_TR1_1 (541508) 13.2 kV Three Winding #1 b.4. ROCKCK7 (541511) 345.0 kV to ROCKCK_T2_1 (541515) 34.5 kV to ROCKCK_TR2_1 (541509) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_350 | Single Phase Fault with Stuck Breaker on OUTLAW 345.00 (541543) 345 kV Bus a. Apply Fault at the OUTLAW 345.00 (541543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROCKCK7 (541511) 345.0 kV to OUTLAW (541543) 345.0 kV Transmission Circuit #1 b.2. OUTLAW (541543) 345.0 kV to OUTLAW_T1_1 (541544) 34.5 kV to OUTLAW_TR1_1 (541551) 13.8 kV Three Winding #1 b.3. OUTLAW (541543) 345.0 kV to OUTLAW_T2_1 (541547) 34.5 kV to OUTLAW_TR2_1 (541552) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_351 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. KETCHEM7 (541500) 345.0 kV to OSBORN7 (541501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_352 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_353 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_354 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.6. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.7. SEWARD 2 (530565) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.8. SEWARD 2 (530565) 69.0 kV to ZOOK 2 (530577) 69.0 kV Transmission Circuit #1 b.10. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.11. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.12. S ELWD 2 (530567) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.13. S ELWD 2 (530567) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_355 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.3. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.4. ALEXND-T (539902) 12.5 kV to ALEXNDR1 (539702) 34.5 kV to ALXNDR 3 (530606) 115.0 kV Three Winding #1 b.6. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.8. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.9. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.10. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.13. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.14. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.15. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_356 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.4. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.5. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.6. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.7. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 b.8. GRTBEND3 (539678) 115.0 kV to GRTBEND1 (539719) 34.5 kV to GRTBENDT (539921) 7.2 kV Three Winding #1 b.10. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.11. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.12. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.13. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.15. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.16. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.17. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.18. 24-FREY3 (539661) 115.0 kV to GEN-2018-116 (763329) 115.0 kV Transmission Circuit #1 b.19. 24-FREY3 (539661) 115.0 kV to 24-FREY1 (539707) 34.5 kV to 24-FREYT (539907) 13.8 kV Three Winding #1 b.20. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.21. 2ND-KS 3 (539689) 115.0 kV to 2ND-KS 1 (539728) 34.5 kV to 2ND-KS T (539931) 13.8 kV Three Winding #1 b.22. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.23. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.24. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.25. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_357 | Single Phase Fault with Stuck Breaker on SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus a. Apply Fault at the SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.2. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.3. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.4. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.7. SPRVILL-EHVB (539117) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV to SVWF3-TERT1 (539744) 13.8 kV Three Winding #1 b.8. SPERVLTT (539935) 13.8 kV to SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV Three Winding #1 b.9. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.11. SPEARVL3 (539694) 115.0 kV to SPEARVL1 (539732) 34.5 kV to SPERVLDT (539936) 13.8 kV Three Winding #1 b.12. SVWF2 1 (539136) 0.6 kV to SVWF2-CLCT1 (539135) 34.5 kV Two Winding #1 b.13. SVWF1 1 (539116) 0.6 kV to SVWF1-CLCT1 (539115) 34.5 kV Two Winding #1 b.14. SVWF3-CLCT1 (539119) 34.5 kV to SVWF3 1 (539120) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_358 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.5. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.6. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (587500) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_359 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to GEN-2018-025 (762603) 345.0 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.5. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 b.6. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 b.7. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.8. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.9. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.10. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.11. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_360 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to GEN-2018-025 (762603) 345.0 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.5. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 b.6. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 b.7. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_361 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.3. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.5. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.6. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.7. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_362 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.3. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.5. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_363 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.4. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.5. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.6. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 b.7. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.8. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.9. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.10. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_364 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.4. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.5. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.6. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_365 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.5. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.6. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.7. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.8. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.9. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.10. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.11. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.13. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.14. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.15. S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.16. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.17. S906 N 8 (647006) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #z1 b.18. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.19. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.20. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.21. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.23. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.24. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.25. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.26. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.27. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_366 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.5. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_367 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.6. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 b.8. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.9. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.10. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 b.11. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_368 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.6. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_369 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.3. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.5. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.6. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.7. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.8. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.9. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.12. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.13. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.14. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.15. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.16. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_370 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.3. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_371 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.3. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.4. S3740 3 (645740) 345.0 kV to GEN-2018-033 (762691) 345.0 kV Transmission Circuit #1 b.5. S3740 3 (645740) 345.0 kV to GEN-2020-036 (764690) 345.0 kV Transmission Circuit #1 b.6. S3740 3 (645740) 345.0 kV to GEN-2020-038 (764705) 345.0 kV Transmission Circuit #1 b.7. S3740 3 (645740) 345.0 kV to CASS 1G (645041) 15.0 kV Two Winding #1 b.8. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_372 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 b.3. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.6. S1361 5 (646361) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_373 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_374 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.3. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.4. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.5. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 b.6. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.7. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.8. S901 8 (647901) 69.0 kV to GEN-2017-198 (760872) 69.0 kV Transmission Circuit #1 b.9. S901 8 (647901) 69.0 kV to JONES 1G (645051) 13.8 kV Two Winding #1 b.10. S901 8 (647901) 69.0 kV to JONES 2G (645052) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_375 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.4. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 b.5. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #2 b.6. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.7. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.8. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.9. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 b.10. S1211 5 (646211) 161.0 kV to S1211T39 (645127) 13.8 kV Two Winding #1 b.11. S1211 5 (646211) 161.0 kV to S1211T49 (645128) 13.8 kV Two Winding #1 b.12. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 b.13. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.14. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.15. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.16. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_376 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 b.4. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.5. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.6. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_377 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.4. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.5. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_378 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.5. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.6. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_379 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.3. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 b.4. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.5. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.6. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_380 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 b.4. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.5. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_381 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.5. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 b.6. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_382 | Single Phase Fault with Stuck Breaker on S1291 5 161.00 (646291) 161 kV Bus a. Apply Fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 b.3. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 b.4. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_383 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_384 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. SD.LS-KS-MB3 (659425) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_385 | Single Phase Fault with Stuck Breaker on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply Fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.LS-LR-MB3 (659426) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #z b.2. SD.LS-LR-MB3 (659426) 345.0 kV to LARAMIE_-MB3 (659131) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_386 | Single Phase Fault with Stuck Breaker on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply Fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to LARAMIE_-MB3 (659131) 345.0 kV Transmission Circuit #1 b.2. STEGALL_-MB3 (659135) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_387 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S1214 5 (646214) 161.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 b.2. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_388 | Single Phase Fault with Stuck Breaker on S983 8 69.000 (647983) 69 kV Bus a. Apply Fault at the S983 8 69.000 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S983 8 (647983) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.2. S983 8 (647983) 69.0 kV to S902 8 (647902) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_389 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_390 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_391 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to AXTELL 7 (640066) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_392 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_393 | Single Phase Fault with Stuck Breaker on S1362 5 161.00 (646362) 161 kV Bus a. Apply Fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 b.2. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_394 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_395 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_396 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_397 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.2. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_398 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_399 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_400 | Single Phase Fault with Stuck Breaker on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply Fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to G20-077-TAP (764490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_401 | Single Phase Fault with Stuck Breaker on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply Fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEBRN N7 (640218) 115.0 kV to CARLJCT7 (640105) 115.0 kV Transmission Circuit #1 b.2. HEBRN N7 (640218) 115.0 kV to HEBRON 7 (640220) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_402 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_403 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_404 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. 103&ROKEBY3 (650189) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_405 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_406 | Single Phase Fault with Stuck Breaker on SD.LS-LR-MB3 (659426) 345 kV Bus a. Apply Fault at the SD.LS-LR-MB3 (659426) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.LS-LR-MB3 (659426) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_407 | Single Phase Fault with Stuck Breaker on STEGALL_-MB3 (659135) 345 kV Bus a. Apply Fault at the STEGALL_-MB3 (659135) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_408 | Single Phase Fault with Stuck Breaker on S914A 8 (647014) 69 kV Bus a. Apply Fault at the S914A 8 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_409 | Single Phase Fault with Stuck Breaker on S983 8 (647983) 69 kV Bus a. Apply Fault at the S983 8 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S983 8 (647983) 69.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_410 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_411 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_413 | Single Phase Fault with Stuck Breaker on ORLEANS7 (640310) 115 kV Bus a. Apply Fault at the ORLEANS7 (640310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORLEANS7 (640310) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_414 | Single Phase Fault with Stuck Breaker on S1281 5 (646281) 161 kV Bus a. Apply Fault at the S1281 5 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_415 | Single Phase Fault with Stuck Breaker on SCS 1X (645071) 15 kV Bus a. Apply Fault at the SCS 1X (645071) 15 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCS 1X (645071) 15.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_416 | Single Phase Fault with Stuck Breaker on SCS 2X (645072) 15 kV Bus a. Apply Fault at the SCS 2X (645072) 15 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCS 2X (645072) 15.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_417 | Single Phase Fault with Stuck Breaker on S1362 5 (646362) 161 kV Bus a. Apply Fault at the S1362 5 (646362) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1362 5 (646362) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_418 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_419 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_420 | Single Phase Fault with Stuck Breaker on CASS 1G (645041) 15 kV Bus a. Apply Fault at the CASS 1G (645041) 15 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CASS 1G (645041) 15.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_421 | Single Phase Fault with Stuck Breaker on CASS 2G (645042) 15 kV Bus a. Apply Fault at the CASS 2G (645042) 15 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CASS 2G (645042) 15.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_422 | Single Phase Fault with Stuck Breaker on S3458 3 (645458) 345 kV Bus a. Apply Fault at the S3458 3 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_423 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_424 | Single Phase Fault with Stuck Breaker on S1252 5 (646252) 161 kV Bus a. Apply Fault at the S1252 5 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1252 5 (646252) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_425 | Single Phase Fault with Stuck Breaker on MIL 1-3X (645081) 13.8 kV Bus a. Apply Fault at the MIL 1-3X (645081) 13.8 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIL 1-3X (645081) 13.8 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_426 | Single Phase Fault with Stuck Breaker on MIL 4-6X (645082) 13.8 kV Bus a. Apply Fault at the MIL 4-6X (645082) 13.8 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIL 4-6X (645082) 13.8 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_427 | Single Phase Fault with Stuck Breaker on MIL 7-9X (645083) 13.8 kV Bus a. Apply Fault at the MIL 7-9X (645083) 13.8 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIL 7-9X (645083) 13.8 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_428 | Single Phase Fault with Stuck Breaker on CODY 7 (640117) 115 kV Bus a. Apply Fault at the CODY 7 (640117) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CODY 7 (640117) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_429 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_430 | Single Phase Fault with Stuck Breaker on FAIRBRY7 (640169) 115 kV Bus a. Apply Fault at the FAIRBRY7 (640169) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRBRY7 (640169) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_431 | Single Phase Fault with Stuck Breaker on HEBRN N7 (640218) 115 kV Bus a. Apply Fault at the HEBRN N7 (640218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEBRN N7 (640218) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_432 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_433 | Single Phase Fault with Stuck Breaker on S1237 5 (646237) 161 kV Bus a. Apply Fault at the S1237 5 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Local_Fault_434 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_001 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_002 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_003 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_004 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_005 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_006 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_007 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_008 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_009 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_010 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_011 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_012 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_013 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_014 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_015 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_016 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_017 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_018 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_019 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_020 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_021 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_023 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_024 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_025 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_026 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_027 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_028 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_029 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_030 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_031 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_032 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_033 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_034 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_035 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_036 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_037 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_038 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_039 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_040 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_041 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_042 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_043 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_044 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_045 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_046 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_047 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_048 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_049 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_050 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_051 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_052 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_053 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | G02_P4_Regional_Fault_054 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.5. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.6. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.7. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.8. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.9. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.10. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.11. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.13. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.14. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.15. S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.16. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.17. S906 N 8 (647006) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #z1 b.18. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.19. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.20. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.21. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.23. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.24. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.25. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.26. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.27. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reduce clearing time to 12 cycles.
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_054 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.5. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.6. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.7. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.8. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.9. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.10. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.11. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.13. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.14. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.15. S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.16. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.17. S906 N 8 (647006) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #z1 b.18. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.19. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.20. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.21. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.23. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.24. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.25. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.26. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.27. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reduce clearing time to 12 cycles.
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_055 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.5. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_056 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.6. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 b.8. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.9. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.10. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 b.11. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25S | Transfer | G02_P4_Regional_Fault_057 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.6. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_001 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_002 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_003 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_004 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_005 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_006 | 3 Phase fault on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_007 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.2. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_008 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_009 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_010 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_011 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_012 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_013 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_014 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_015 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_016 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_017 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_018 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_019 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON4 (603149) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_020 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_021 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_022 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_023 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to PROSE CAP7 (603265) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_024 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_025 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_026 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_027 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_028 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_029 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_030 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_031 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.2. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_032 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_033 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to ROCK CO5 (602039) 161.0 kV Transmission Circuit #1 b.2. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_034 | 3 Phase fault on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_035 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_036 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_037 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_038 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_039 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_040 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_041 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_042 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_043 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_044 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_045 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_046 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_047 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_048 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_050 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_051 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_052 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_053 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_054 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_055 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_056 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_057 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_058 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_059 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_060 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_061 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_062 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_063 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_064 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_065 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_066 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_067 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_068 | 3 Phase fault on BRULE 7 115.00 (640091) 115 kV Bus a. Apply fault at the BRULE 7 115.00 (640091) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 b.2. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.3. BRULE 7 (640091) 115.0 kV to BRULE 9 (640092) 34.5 kV to BRULE T1 9 (643025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_069 | 3 Phase fault on INTERST_-TS7115.00 (659819) 115 kV Bus a. Apply fault at the INTERST_-TS7115.00 (659819) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to JULSTAP7 (640246) 115.0 kV Transmission Circuit #1 b.2. JULSTAP7 (640246) 115.0 kV to CHAPPEL7 (653300) 115.0 kV Transmission Circuit #1 b.3. JULSTAP7 (640246) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 b.4. CHAPPEL7 (653300) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.5. CHAPPEL7 (653300) 115.0 kV to CHAPPEL9 (653301) 34.5 kV Two Winding #1 b.6. SIDNEY 7 (653572) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.7. GEN-2016-147 (588220) 115.0 kV to SIDNEY 7 (653572) 115.0 kV Transmission Circuit #1 b.8. SIDNEY 7 (653572) 115.0 kV to SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 b.9. JULESBG7 (653302) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 b.10. HIGHLINE (653303) 115.0 kV to INTERST_-TS7 (659819) 115.0 kV Transmission Circuit #1 b.11. INTERST_-TS7 (659819) 115.0 kV to INTERSTW-TS8 (659827) 69.0 kV Two Winding #1 b.12. INTERST_-TS7 (659819) 115.0 kV to INTERSTE-TS8 (659828) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_070 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_071 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_072 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_073 | 3 Phase fault on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_074 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT_REACT7 (541517) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_075 | 3 Phase fault on MC REAC1 345.00 (541411) 345 kV Bus a. Apply fault at the MC REAC1 345.00 (541411) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MC REAC1 (541411) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_076 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MC REAC2 (541412) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_077 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MC REAC3 (541413) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_078 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_079 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_080 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_081 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_082 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_083 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_084 | 3 Phase fault on BYPASS 7 115.00 (641082) 115 kV Bus a. Apply fault at the BYPASS 7 115.00 (641082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_085 | 3 Phase fault on E7THST 7 115.00 (641085) 115 kV Bus a. Apply fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_086 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_087 | 3 Phase fault on E7THST 7 115.00 (641085) 115 kV Bus a. Apply fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_088 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_089 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.2. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_090 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_091 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_092 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_093 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_094 | 3 Phase fault on MC REAC1 345.00 (541411) 345 kV Bus a. Apply fault at the MC REAC1 345.00 (541411) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MC REAC1 (541411) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_095 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MC REAC2 (541412) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_096 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MC REAC3 (541413) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_097 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT_REACT7 (541517) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_098 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_099 | 3 Phase fault on NW70FAIRFD7 115.00 (650210) 115 kV Bus a. Apply fault at the NW70FAIRFD7 115.00 (650210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_100 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_101 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.6. 2&N 7 (650230) 115.0 kV Fixed Shunt Device | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_102 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_103 | 3 Phase fault on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.2. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.3. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_104 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_105 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_106 | 3 Phase fault on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_107 | 3 Phase fault on 84LEIGHTON7 115.00 (650267) 115 kV Bus a. Apply fault at the 84LEIGHTON7 115.00 (650267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_108 | 3 Phase fault on DAVEY 7 115.00 (640155) 115 kV Bus a. Apply fault at the DAVEY 7 115.00 (640155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVEY 7 (640155) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_109 | 3 Phase fault on 70&BLUFF 7 115.00 (650269) 115 kV Bus a. Apply fault at the 70&BLUFF 7 115.00 (650269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_110 | 3 Phase fault on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_111 | 3 Phase fault on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_112 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_113 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_114 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_115 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_116 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_117 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_118 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_119 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_120 | 3 Phase fault on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 b.4. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_121 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_122 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_123 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_124 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_125 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_126 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_127 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_128 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_129 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_130 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_131 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_132 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_133 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_134 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_135 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_136 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_137 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_138 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_139 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_140 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_141 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_142 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_143 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_144 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_145 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_146 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_147 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_148 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_149 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_150 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_151 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_152 | 3 Phase fault on WKNNY 3 115.00 (530560) 115 kV Bus a. Apply fault at the WKNNY 3 115.00 (530560) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_153 | 3 Phase fault on ANGUS 3 115.00 (530714) 115 kV Bus a. Apply fault at the ANGUS 3 115.00 (530714) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_154 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_155 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_156 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_157 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_158 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_159 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_160 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_161 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_162 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_163 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_164 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_165 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_166 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_167 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_168 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_169 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_170 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_171 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_172 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_173 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_174 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Large change in the angles of GMECG2 units nos. 8, 9, 10, and 11 (530675) following the event. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_174 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Large change in the angles of GMECG2 units nos. 8, 9, 10, and 11 (530675) following the event. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_174 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Large change in the angles of GMECG2 units nos. 8, 9, 10, and 11 (530675) following the event. The issues is also observed in the base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_175 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_176 | 3 Phase fault on HARMONY7 115.00 (640210) 115 kV Bus a. Apply fault at the HARMONY7 115.00 (640210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARMONY7 (640210) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.2. HARMONY7 (640210) 115.0 kV to ST.FRANC (640351) 115.0 kV Transmission Circuit #1 b.3. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_177 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.2. STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_178 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_179 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.2 7 (640242) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 b.2. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_180 | 3 Phase fault on GOTHNBG7 115.00 (640196) 115 kV Bus a. Apply fault at the GOTHNBG7 115.00 (640196) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTHNBG7 (640196) 115.0 kV to JEFFREY7 (640238) 115.0 kV Transmission Circuit #1 b.2. COZAD 7 (640144) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_181 | 3 Phase fault on WESTMIN7 115.00 (640407) 115 kV Bus a. Apply fault at the WESTMIN7 115.00 (640407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.2 7 (640242) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.2. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_182 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_183 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_184 | 3 Phase fault on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.3. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_185 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_186 | 3 Phase fault on HEBRON 7 115.00 (640220) 115 kV Bus a. Apply fault at the HEBRON 7 115.00 (640220) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 7 (640220) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 b.2. HEBRN N7 (640218) 115.0 kV to HEBRON 7 (640220) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_187 | 3 Phase fault on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRYG (640170) 34.5 kV to FAIRBRY7 (640169) 115.0 kV to FAIRBURY T19 (643056) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_188 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.2. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_189 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_190 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.6. S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_191 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_192 | 3 Phase fault on DAVEY 7 115.00 (640155) 115 kV Bus a. Apply fault at the DAVEY 7 115.00 (640155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVEY 7 (640155) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.2. DAVEY 7 (640155) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_193 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_194 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_195 | 3 Phase fault on W.POINT7 115.00 (640400) 115 kV Bus a. Apply fault at the W.POINT7 115.00 (640400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.2. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_196 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 b.2. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_197 | 3 Phase fault on COLTON__-TS7115.00 (659817) 115 kV Bus a. Apply fault at the COLTON__-TS7115.00 (659817) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY 7 (653572) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.2. CHAPPEL7 (653300) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.3. JULSTAP7 (640246) 115.0 kV to CHAPPEL7 (653300) 115.0 kV Transmission Circuit #1 b.4. B.SPRGS7 (640068) 115.0 kV to JULSTAP7 (640246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_198 | 3 Phase fault on BRULE 7 115.00 (640091) 115 kV Bus a. Apply fault at the BRULE 7 115.00 (640091) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 b.2. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_199 | 3 Phase fault on BLUECK 7 115.00 (640086) 115 kV Bus a. Apply fault at the BLUECK 7 115.00 (640086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECK 7 (640086) 115.0 kV to W.HORSE_-TS7 (659812) 115.0 kV Transmission Circuit #1 b.2. B.SPRGS7 (640068) 115.0 kV to BLUECK 7 (640086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_200 | 3 Phase fault on SPCREEK_-TS7115.00 (659810) 115 kV Bus a. Apply fault at the SPCREEK_-TS7115.00 (659810) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR___-TS7 (659804) 115.0 kV to SPCREEK_-TS7 (659810) 115.0 kV Transmission Circuit #1 b.2. GRANTNB_-TS7 (659800) 115.0 kV to SPCREEK_-TS7 (659810) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_201 | 3 Phase fault on CRETE___-TS7115.00 (659813) 115 kV Bus a. Apply fault at the CRETE___-TS7115.00 (659813) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR___-TS7 (659804) 115.0 kV to CRETE___-TS7 (659813) 115.0 kV Transmission Circuit #1 b.2. CRETE___-TS7 (659813) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 b.3. ATHEY 7 (641244) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 b.4. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_202 | 3 Phase fault on ROSCOE__-TS7115.00 (659809) 115 kV Bus a. Apply fault at the ROSCOE__-TS7115.00 (659809) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA_-TS7 (659801) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.2. ELSIETP_-TS7 (659807) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_203 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_204 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_205 | 3 Phase fault on CANADAY4 230.00 (640102) 230 kV Bus a. Apply fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_206 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_207 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_208 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_209 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_210 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_211 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_212 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_213 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_214 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_215 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_216 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_217 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_218 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_219 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_220 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_221 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_222 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_223 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_224 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_225 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_226 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_227 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_228 | 3 Phase fault on BOBCAT.C 3345.00 (640529) 345 kV Bus a. Apply fault at the BOBCAT.C 3345.00 (640529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT.C 7 (640530) 115.0 kV to BOBCAT.C 3 (640529) 345.0 kV to BOBCAT.C 9 (640531) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_229 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_230 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_231 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_232 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_233 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_234 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_235 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_236 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_237 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 b.4. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_238 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 b.4. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_239 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_240 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_241 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_242 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_243 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_244 | 3 Phase fault on GENEVA 8 69.000 (640179) 69 kV Bus a. Apply fault at the GENEVA 8 69.000 (640179) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 8 (640179) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_245 | 3 Phase fault on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRN N7 (640218) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_246 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_247 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_248 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_249 | 3 Phase fault on MCCOOK 8 69.000 (640270) 69 kV Bus a. Apply fault at the MCCOOK 8 69.000 (640270) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_250 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_251 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_252 | 3 Phase fault on ORLEANS8 69.000 (640311) 69 kV Bus a. Apply fault at the ORLEANS8 69.000 (640311) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS8 (640311) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_253 | 3 Phase fault on SUTTON 8 69.000 (640373) 69 kV Bus a. Apply fault at the SUTTON 8 69.000 (640373) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 8 (640373) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_254 | 3 Phase fault on VALENTN7 115.00 (640392) 115 kV Bus a. Apply fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALENTN7 (640392) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_255 | 3 Phase fault on STEELEC7 115.00 (640426) 115 kV Bus a. Apply fault at the STEELEC7 115.00 (640426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEELEC7 (640426) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_256 | 3 Phase fault on HILDRTH8 69.000 (640223) 69 kV Bus a. Apply fault at the HILDRTH8 69.000 (640223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_257 | 3 Phase fault on BASSETT 7115.00 (640580) 115 kV Bus a. Apply fault at the BASSETT 7115.00 (640580) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 7 (640580) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_258 | 3 Phase fault on BASSETT 869.000 (640581) 69 kV Bus a. Apply fault at the BASSETT 869.000 (640581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 8 (640581) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_259 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_260 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_261 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_262 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_263 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_264 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_265 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_266 | 3 Phase fault on GRNBURG3 115.00 (539664) 115 kV Bus a. Apply fault at the GRNBURG3 115.00 (539664) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.3. SUNCITY3 (539697) 115.0 kV to SUNCITY1 (539733) 34.5 kV to SUNCT-T (539937) 2.4 kV Three Winding #1 b.4. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.5. GRNBURG3 (539664) 115.0 kV to GRNBURG1 (539710) 34.5 kV to GRNBUG-T (539910) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_267 | 3 Phase fault on FORD 3 115.00 (539758) 115 kV Bus a. Apply fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.3. FORD 3 (539758) 115.0 kV to FORD 1 (539765) 34.5 kV to FORD T (539968) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_268 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_269 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_270 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_271 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_272 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.2. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.3. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 b.4. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.6. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_273 | 3 Phase fault on DCBEEF3 115.00 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 115.00 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_274 | 3 Phase fault on SPEARVL3 115.00 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 115.00 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_275 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_276 | 3 Phase fault on S-DODGE3 115.00 (539688) 115 kV Bus a. Apply fault at the S-DODGE3 115.00 (539688) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S-DODGE3 (539688) 115.0 kV to W-DODGE3 (539699) 115.0 kV Transmission Circuit #1 b.2. S-DODGE3 (539688) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.3. S-DODGE3 (539688) 115.0 kV to S-DODGE1 (539727) 34.5 kV to S-DODG-T (539930) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_277 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_278 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_279 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_280 | 3 Phase fault on GRNLEAF3 115.00 (539665) 115 kV Bus a. Apply fault at the GRNLEAF3 115.00 (539665) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.2. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.3. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_281 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_282 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_283 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_284 | 3 Phase fault on GRANTNB_-TS7115.00 (659800) 115 kV Bus a. Apply fault at the GRANTNB_-TS7115.00 (659800) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTNB_-TS7 (659800) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_285 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_286 | 3 Phase fault on SPCREEK_-TS7115.00 (659810) 115 kV Bus a. Apply fault at the SPCREEK_-TS7115.00 (659810) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTNB_-TS7 (659800) 115.0 kV to SPCREEK_-TS7 (659810) 115.0 kV Transmission Circuit #1 b.2. LAMAR___-TS7 (659804) 115.0 kV to SPCREEK_-TS7 (659810) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_287 | 3 Phase fault on CRETE___-TS7115.00 (659813) 115 kV Bus a. Apply fault at the CRETE___-TS7115.00 (659813) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR___-TS7 (659804) 115.0 kV to CRETE___-TS7 (659813) 115.0 kV Transmission Circuit #1 b.2. CRETE___-TS7 (659813) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 b.3. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 b.4. ATHEY 7 (641244) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_288 | 3 Phase fault on BLUECK 7 115.00 (640086) 115 kV Bus a. Apply fault at the BLUECK 7 115.00 (640086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECK 7 (640086) 115.0 kV to W.HORSE_-TS7 (659812) 115.0 kV Transmission Circuit #1 b.2. COLDWATR-TS7 (659802) 115.0 kV to W.HORSE_-TS7 (659812) 115.0 kV Transmission Circuit #1 b.3. B.SPRGS7 (640068) 115.0 kV to BLUECK 7 (640086) 115.0 kV Transmission Circuit #1 b.4. BLUECK 7 (640086) 115.0 kV to BLUECK 9 (640087) 34.5 kV to BLUECREEKT19 (643022) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_289 | 3 Phase fault on BRULE 7 115.00 (640091) 115 kV Bus a. Apply fault at the BRULE 7 115.00 (640091) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 b.2. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.3. BRULE 7 (640091) 115.0 kV to BRULE 9 (640092) 34.5 kV to BRULE T1 9 (643025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_290 | 3 Phase fault on JULSTAP7 115.00 (640246) 115 kV Bus a. Apply fault at the JULSTAP7 115.00 (640246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to JULSTAP7 (640246) 115.0 kV Transmission Circuit #1 b.2. JULSTAP7 (640246) 115.0 kV to CHAPPEL7 (653300) 115.0 kV Transmission Circuit #1 b.3. JULSTAP7 (640246) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 b.4. CHAPPEL7 (653300) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.5. SIDNEY 7 (653572) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_291 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY 7 (653572) 115.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_292 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_293 | 3 Phase fault on GRANTNB_-TS7115.00 (659800) 115 kV Bus a. Apply fault at the GRANTNB_-TS7115.00 (659800) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTNB_-TS7 (659800) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_294 | 3 Phase fault on MARSHAL3 115.00 (533303) 115 kV Bus a. Apply fault at the MARSHAL3 115.00 (533303) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHAL3 (533303) 115.0 kV to KNOB HL3 (533332) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_295 | 3 Phase fault on KNOB HL3 115.00 (533332) 115 kV Bus a. Apply fault at the KNOB HL3 115.00 (533332) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_296 | 3 Phase fault on KNOB HL3 115.00 (533332) 115 kV Bus a. Apply fault at the KNOB HL3 115.00 (533332) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOB HL3 (533332) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_297 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_298 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_299 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_300 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_301 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_302 | 3 Phase fault on KNOB HL3 115.00 (533332) 115 kV Bus a. Apply fault at the KNOB HL3 115.00 (533332) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOB HL3 (533332) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_303 | 3 Phase fault on INTERST_-TS7115.00 (659819) 115 kV Bus a. Apply fault at the INTERST_-TS7115.00 (659819) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to JULSTAP7 (640246) 115.0 kV Transmission Circuit #1 b.2. JULSTAP7 (640246) 115.0 kV to CHAPPEL7 (653300) 115.0 kV Transmission Circuit #1 b.3. JULSTAP7 (640246) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 b.4. CHAPPEL7 (653300) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.5. CHAPPEL7 (653300) 115.0 kV to CHAPPEL9 (653301) 34.5 kV Two Winding #1 b.6. SIDNEY 7 (653572) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.7. JULESBG7 (653302) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 b.8. HIGHLINE (653303) 115.0 kV to INTERST_-TS7 (659819) 115.0 kV Transmission Circuit #1 b.9. INTERST_-TS7 (659819) 115.0 kV to INTERSTW-TS8 (659827) 69.0 kV Two Winding #1 b.10. INTERST_-TS7 (659819) 115.0 kV to INTERSTE-TS8 (659828) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_304 | 3 Phase fault on VETAL_TP-RM7115.00 (659153) 115 kV Bus a. Apply fault at the VETAL_TP-RM7115.00 (659153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.2. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_305 | 3 Phase fault on WITTEN__-RB7115.00 (659166) 115 kV Bus a. Apply fault at the WITTEN__-RB7115.00 (659166) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.2. WINNER 7 (652494) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_306 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_307 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_308 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_309 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_310 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_311 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_312 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 b.2. STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 b.3. STEGALL_-MB9 (659167) 13.8 kV to STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_313 | 3 Phase fault on GRANTNB_-TS7115.00 (659800) 115 kV Bus a. Apply fault at the GRANTNB_-TS7115.00 (659800) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTNB_-TS7 (659800) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_314 | 3 Phase fault on DH_CS_EA-TS4230.00 (659829) 230 kV Bus a. Apply fault at the DH_CS_EA-TS4230.00 (659829) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEYW4 (652584) 230.0 kV to DH_CS.WE-TS4 (659830) 230.0 kV Transmission Circuit #x1 b.2. NB WEST4 (652585) 230.0 kV to DH_CS.WE-TS4 (659830) 230.0 kV Transmission Circuit #x1 b.3. DH_CS.WE-TS4 (659830) 230.0 kV Fixed Shunt Device b.4. DH_CS_EA-TS4 (659829) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_315 | 3 Phase fault on B.SPRGS7 115.00 (640068) 115 kV Bus a. Apply fault at the B.SPRGS7 115.00 (640068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to BLUECK 7 (640086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_316 | 3 Phase fault on BRULE 7 115.00 (640091) 115 kV Bus a. Apply fault at the BRULE 7 115.00 (640091) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 b.2. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 b.3. BRULE 7 (640091) 115.0 kV to BRULE 9 (640092) 34.5 kV to BRULE T1 9 (643025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_317 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_318 | 3 Phase fault on GRANTNB_-TS7115.00 (659800) 115 kV Bus a. Apply fault at the GRANTNB_-TS7115.00 (659800) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTNB_-TS7 (659800) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_319 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_320 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_321 | 3 Phase fault on OGALALA_-TS7115.00 (659801) 115 kV Bus a. Apply fault at the OGALALA_-TS7115.00 (659801) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA_-TS7 (659801) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_322 | 3 Phase fault on OGALALA_-TS7115.00 (659801) 115 kV Bus a. Apply fault at the OGALALA_-TS7115.00 (659801) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA_-TS7 (659801) 115.0 kV to MCONGHY_-TS7 (659824) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_323 | 3 Phase fault on ROSCOE__-TS7115.00 (659809) 115 kV Bus a. Apply fault at the ROSCOE__-TS7115.00 (659809) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA_-TS7 (659801) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.2. ELSIETP_-TS7 (659807) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_324 | 3 Phase fault on ELSIETP_-TS7115.00 (659807) 115 kV Bus a. Apply fault at the ELSIETP_-TS7115.00 (659807) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA_-TS7 (659801) 115.0 kV to MCONGHY_-TS7 (659824) 115.0 kV Transmission Circuit #1 b.2. MCONGHY_-TS7 (659824) 115.0 kV to ARTHUR__-TS7 (659825) 115.0 kV Transmission Circuit #1 b.3. ELSIETP_-TS7 (659807) 115.0 kV to PAXTON__-TS7 (659808) 115.0 kV Transmission Circuit #1 b.4. ELSIETP_-TS7 (659807) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 b.5. ELSIETP_-TS7 (659807) 115.0 kV to ELSIE___-TS7 (659822) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_325 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_326 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SD.LS-KS-MB3 (659425) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_327 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z b.2. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.3. SD.LS-LR-MB3 (659426) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_328 | 3 Phase fault on WINNER 7 115.00 (652494) 115 kV Bus a. Apply fault at the WINNER 7 115.00 (652494) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREGORY7 (652478) 115.0 kV to WINNER 7 (652494) 115.0 kV Transmission Circuit #1 b.2. WINNER 7 (652494) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.3. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_329 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_330 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_331 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_332 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_333 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_334 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_335 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_336 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_337 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_338 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_339 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_340 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_341 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_342 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_343 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_344 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_345 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_346 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_347 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_348 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_349 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_350 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_351 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_352 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_353 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_354 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_355 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_356 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_357 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_358 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_359 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_360 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_361 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_362 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_363 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_364 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_365 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_366 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_367 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_368 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_369 | 3 Phase fault on S1234 5 161.00 (646234) 161 kV Bus a. Apply fault at the S1234 5 161.00 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_370 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_371 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_372 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_373 | 3 Phase fault on S1244 5 161.00 (646244) 161 kV Bus a. Apply fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_374 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_375 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_376 | 3 Phase fault on S1297 5 161.00 (646297) 161 kV Bus a. Apply fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.2. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_377 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_378 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_379 | 3 Phase fault on S1254 5 161.00 (646254) 161 kV Bus a. Apply fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_380 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_381 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_382 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_383 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_384 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_385 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_386 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_387 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_388 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_389 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_390 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_391 | 3 Phase fault on S1361 5 161.00 (646361) 161 kV Bus a. Apply fault at the S1361 5 161.00 (646361) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1361 5 (646361) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_392 | 3 Phase fault on PLTSMTH8 69.000 (640320) 69 kV Bus a. Apply fault at the PLTSMTH8 69.000 (640320) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLTSMTH8 (640320) 69.0 kV to S961 8 (647961) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_393 | 3 Phase fault on PLTSMTH8 69.000 (640320) 69 kV Bus a. Apply fault at the PLTSMTH8 69.000 (640320) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLTSMTH8 (640320) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_394 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_395 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_396 | 3 Phase fault on 991TP 8 69.000 (647091) 69 kV Bus a. Apply fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 991TP 8 (647091) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 b.2. 991TP 8 (647091) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.3. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_397 | 3 Phase fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_398 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_399 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S972 8 (647972) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_400 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_401 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_402 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_403 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_404 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_405 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_406 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_407 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_408 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_409 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_410 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_411 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_412 | 3 Phase fault on S917 8 69.000 (647917) 69 kV Bus a. Apply fault at the S917 8 69.000 (647917) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_413 | 3 Phase fault on S918 8 69.000 (647918) 69 kV Bus a. Apply fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_414 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_415 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_416 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_417 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_418 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_419 | 3 Phase fault on S930 8 69.000 (647930) 69 kV Bus a. Apply fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_420 | 3 Phase fault on S972 8 69.000 (647972) 69 kV Bus a. Apply fault at the S972 8 69.000 (647972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S972 8 (647972) 69.0 kV to S982 8 (647982) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_421 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. S991 E 8 (647291) 69.0 kV to S1291 5 (646291) 161.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_422 | 3 Phase fault on ASH GRV8 69.000 (647100) 69 kV Bus a. Apply fault at the ASH GRV8 69.000 (647100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_423 | 3 Phase fault on 990TP 8 69.000 (647090) 69 kV Bus a. Apply fault at the 990TP 8 69.000 (647090) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 990TP 8 (647090) 69.0 kV to S971 8 (647971) 69.0 kV Transmission Circuit #1 b.2. 990TP 8 (647090) 69.0 kV to S982 8 (647982) 69.0 kV Transmission Circuit #1 b.3. 990TP 8 (647090) 69.0 kV to S990 8 (647990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_424 | 3 Phase fault on 979TP 8 69.000 (647079) 69 kV Bus a. Apply fault at the 979TP 8 69.000 (647079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 979TP 8 (647079) 69.0 kV to S979 8 (647979) 69.0 kV Transmission Circuit #1 b.2. 979TP 8 (647079) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.3. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_425 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_426 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_427 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_428 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_429 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_430 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_431 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_432 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_433 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_434 | 3 Phase fault on S3761 3 345.00 (645761) 345 kV Bus a. Apply fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_435 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_436 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_437 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_438 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_439 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_440 | 3 Phase fault on S6866 8 69.000 (647866) 69 kV Bus a. Apply fault at the S6866 8 69.000 (647866) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_441 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_442 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_443 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_444 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_445 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_446 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_447 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_448 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_449 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_450 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_451 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_452 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_453 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_454 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_455 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_456 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_457 | 3 Phase fault on J1620 POI 115.00 (46207) 115 kV Bus a. Apply fault at the J1620 POI 115.00 (46207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1620 POI (46207) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_458 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_459 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_460 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_461 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_462 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_463 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_464 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_465 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_466 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_467 | 3 Phase fault on BEACH 3 115.00 (530557) 115 kV Bus a. Apply fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_468 | 3 Phase fault on WKNNY 3 115.00 (530560) 115 kV Bus a. Apply fault at the WKNNY 3 115.00 (530560) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_469 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Large change in the angles of GMECG2 units nos. 8, 9, 10, and 11 (530675) following the event. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_469 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Large change in the angles of GMECG2 units nos. 8, 9, 10, and 11 (530675) following the event. The issues is also observed in the base case. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_470 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Large change in the angles of GMECG2 units nos. 8, 9, 10, and 11 (530675) following the event. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_470 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Large change in the angles of GMECG2 units nos. 8, 9, 10, and 11 (530675) following the event. The issues is also observed in the base case. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_471 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Large change in the angles of GMECG2 units nos. 8, 9, 10, and 11 (530675) following the event. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_471 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | Yes | Yes | Yes | Yes | Yes | Yes | Large change in the angles of GMECG2 units nos. 8, 9, 10, and 11 (530675) following the event. The issues is also observed in the base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_472 | 3 Phase fault on N HAYS3 115.00 (530581) 115 kV Bus a. Apply fault at the N HAYS3 115.00 (530581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_473 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G20-070-TAP (765035) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_474 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_475 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_476 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_477 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_478 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_479 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_480 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_481 | 3 Phase fault on MARSHAL3 115.00 (533303) 115 kV Bus a. Apply fault at the MARSHAL3 115.00 (533303) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHAL3 (533303) 115.0 kV to SMITTYV3 (533338) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_482 | 3 Phase fault on NW-DGTP3 115.00 (539628) 115 kV Bus a. Apply fault at the NW-DGTP3 115.00 (539628) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DGTP3 (539628) 115.0 kV to W-DODGE3 (539699) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_483 | 3 Phase fault on DCBEEF3 115.00 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 115.00 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_484 | 3 Phase fault on DCBEEF3 115.00 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 115.00 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_485 | 3 Phase fault on CLIFTON3 115.00 (539656) 115 kV Bus a. Apply fault at the CLIFTON3 115.00 (539656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_486 | 3 Phase fault on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_487 | 3 Phase fault on GRNBURG3 115.00 (539664) 115 kV Bus a. Apply fault at the GRNBURG3 115.00 (539664) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_488 | 3 Phase fault on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_489 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_490 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_491 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_492 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_493 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_494 | 3 Phase fault on FORD 3 115.00 (539758) 115 kV Bus a. Apply fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_495 | 3 Phase fault on FORD 3 115.00 (539758) 115 kV Bus a. Apply fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_496 | 3 Phase fault on SSTARW 3 115.00 (539761) 115 kV Bus a. Apply fault at the SSTARW 3 115.00 (539761) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SSTARW 3 (539761) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_497 | 3 Phase fault on NFTDODG3 115.00 (539771) 115 kV Bus a. Apply fault at the NFTDODG3 115.00 (539771) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NFTDODG3 (539771) 115.0 kV to GEN-2019-044 (763758) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_498 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_499 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to TRANSFORMER (539813) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_500 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_501 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_502 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_503 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_504 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_505 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_506 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_507 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_508 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_509 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_510 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_511 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_512 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_513 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_514 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_515 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_516 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_517 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_518 | 3 Phase fault on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_519 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_520 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_521 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_522 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_523 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_524 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_525 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_526 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_527 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_528 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to G20-070-TAP (765035) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_529 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_530 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_531 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_532 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_533 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_534 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_535 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_536 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REMSEN 3 (635398) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_537 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_538 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to GLACIAL EDGE (637009) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_539 | 3 Phase fault on AINSWND7 115.00 (640050) 115 kV Bus a. Apply fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_540 | 3 Phase fault on AINSWND7 115.00 (640050) 115 kV Bus a. Apply fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_541 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_542 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_543 | 3 Phase fault on ATKINSN7 115.00 (640058) 115 kV Bus a. Apply fault at the ATKINSN7 115.00 (640058) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATKINSN7 (640058) 115.0 kV to EMMET 7 (640165) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_544 | 3 Phase fault on ATKINSN7 115.00 (640058) 115 kV Bus a. Apply fault at the ATKINSN7 115.00 (640058) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATKINSN7 (640058) 115.0 kV to STUART 7 (640367) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_545 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_546 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_547 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_548 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_549 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_550 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_551 | 3 Phase fault on B.SPRGS7 115.00 (640068) 115 kV Bus a. Apply fault at the B.SPRGS7 115.00 (640068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to BRULE 7 (640091) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_552 | 3 Phase fault on B.SPRGS7 115.00 (640068) 115 kV Bus a. Apply fault at the B.SPRGS7 115.00 (640068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.SPRGS7 (640068) 115.0 kV to JULSTAP7 (640246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_553 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_554 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_555 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_556 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_557 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_558 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_559 | 3 Phase fault on BEEMER 7 115.00 (640078) 115 kV Bus a. Apply fault at the BEEMER 7 115.00 (640078) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_560 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_561 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_562 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_563 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_564 | 3 Phase fault on BLUECK 7 115.00 (640086) 115 kV Bus a. Apply fault at the BLUECK 7 115.00 (640086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECK 7 (640086) 115.0 kV to W.HORSE_-TS7 (659812) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_565 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_566 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_567 | 3 Phase fault on BRULE 7 115.00 (640091) 115 kV Bus a. Apply fault at the BRULE 7 115.00 (640091) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRULE 7 (640091) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_568 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_569 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_570 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_571 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_572 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_573 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_574 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_575 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_576 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_577 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_578 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_579 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_580 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_581 | 3 Phase fault on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_582 | 3 Phase fault on CODY 7 115.00 (640117) 115 kV Bus a. Apply fault at the CODY 7 115.00 (640117) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CODY 7 (640117) 115.0 kV to G20-069-TAP (764475) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_583 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_584 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_585 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_586 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_587 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_588 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_589 | 3 Phase fault on DAVEY 7 115.00 (640155) 115 kV Bus a. Apply fault at the DAVEY 7 115.00 (640155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVEY 7 (640155) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_590 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_591 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_592 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_593 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_594 | 3 Phase fault on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_595 | 3 Phase fault on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRBRY7 (640169) 115.0 kV to G20-077-TAP (764490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_596 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_597 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_598 | 3 Phase fault on FRIEND 7 115.00 (640174) 115 kV Bus a. Apply fault at the FRIEND 7 115.00 (640174) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_599 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_600 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_601 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_602 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_603 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_604 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_605 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_606 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_607 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_608 | 3 Phase fault on GOSPER 7 115.00 (640194) 115 kV Bus a. Apply fault at the GOSPER 7 115.00 (640194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_609 | 3 Phase fault on GOTHNBG7 115.00 (640196) 115 kV Bus a. Apply fault at the GOTHNBG7 115.00 (640196) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTHNBG7 (640196) 115.0 kV to JEFFREY7 (640238) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_610 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_611 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_612 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_613 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_614 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_615 | 3 Phase fault on HARBINE7 115.00 (640208) 115 kV Bus a. Apply fault at the HARBINE7 115.00 (640208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARBINE7 (640208) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_616 | 3 Phase fault on HARMONY7 115.00 (640210) 115 kV Bus a. Apply fault at the HARMONY7 115.00 (640210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARMONY7 (640210) 115.0 kV to ST.FRANC (640351) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_617 | 3 Phase fault on HARMONY7 115.00 (640210) 115 kV Bus a. Apply fault at the HARMONY7 115.00 (640210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARMONY7 (640210) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_618 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_619 | 3 Phase fault on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRN N7 (640218) 115.0 kV to HEBRON 7 (640220) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_620 | 3 Phase fault on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRN N7 (640218) 115.0 kV to G20-077-TAP (764490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_621 | 3 Phase fault on HEBRON 7 115.00 (640220) 115 kV Bus a. Apply fault at the HEBRON 7 115.00 (640220) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEBRON 7 (640220) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_622 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_623 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_624 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_625 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_626 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_627 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_628 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_629 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_630 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_631 | 3 Phase fault on HUMBOLT7 115.00 (640235) 115 kV Bus a. Apply fault at the HUMBOLT7 115.00 (640235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_632 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to JOHN.1 7 (640240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_633 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_634 | 3 Phase fault on JOHN.1 7 115.00 (640240) 115 kV Bus a. Apply fault at the JOHN.1 7 115.00 (640240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_635 | 3 Phase fault on JOHN.2 7 115.00 (640242) 115 kV Bus a. Apply fault at the JOHN.2 7 115.00 (640242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.2 7 (640242) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_636 | 3 Phase fault on JOHN.2 7 115.00 (640242) 115 kV Bus a. Apply fault at the JOHN.2 7 115.00 (640242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.2 7 (640242) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_637 | 3 Phase fault on JULSTAP7 115.00 (640246) 115 kV Bus a. Apply fault at the JULSTAP7 115.00 (640246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JULSTAP7 (640246) 115.0 kV to CHAPPEL7 (653300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_638 | 3 Phase fault on JULSTAP7 115.00 (640246) 115 kV Bus a. Apply fault at the JULSTAP7 115.00 (640246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JULSTAP7 (640246) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_639 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_640 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_641 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_642 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_643 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_644 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KINGSLY7 (640255) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_645 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_646 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_647 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to PROSSER7 (640321) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_648 | 3 Phase fault on MALONEY7 115.00 (640265) 115 kV Bus a. Apply fault at the MALONEY7 115.00 (640265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_649 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_650 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_651 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_652 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_653 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_654 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_655 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_656 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_657 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_658 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_659 | 3 Phase fault on ORLEANS7 115.00 (640310) 115 kV Bus a. Apply fault at the ORLEANS7 115.00 (640310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS7 (640310) 115.0 kV to G20-013-TAP (764445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_660 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_661 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_662 | 3 Phase fault on REDWILO7 115.00 (640326) 115 kV Bus a. Apply fault at the REDWILO7 115.00 (640326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_663 | 3 Phase fault on RIVERDL7 115.00 (640331) 115 kV Bus a. Apply fault at the RIVERDL7 115.00 (640331) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_664 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_665 | 3 Phase fault on ST.FRANC 115.00 (640351) 115 kV Bus a. Apply fault at the ST.FRANC 115.00 (640351) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_666 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_667 | 3 Phase fault on STUART 7 115.00 (640367) 115 kV Bus a. Apply fault at the STUART 7 115.00 (640367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STUART 7 (640367) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_668 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_669 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_670 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_671 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_673 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_674 | 3 Phase fault on STEELEC7 115.00 (640426) 115 kV Bus a. Apply fault at the STEELEC7 115.00 (640426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEELEC7 (640426) 115.0 kV to S.FLATS.PLT7 (640558) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_675 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_676 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_677 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_678 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_679 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to UPSTREAM.W 7 (643254) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_680 | 3 Phase fault on BOBCAT.C 3345.00 (640529) 345 kV Bus a. Apply fault at the BOBCAT.C 3345.00 (640529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT.C 3 (640529) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_681 | 3 Phase fault on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to RTLSNAKE.W 4 (640561) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_682 | 3 Phase fault on ROSEMONT 7115.00 (640583) 115 kV Bus a. Apply fault at the ROSEMONT 7115.00 (640583) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEMONT 7 (640583) 115.0 kV to COTTONWD 7 (640584) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_683 | 3 Phase fault on TURTLE.CRK 3345.00 (640588) 345 kV Bus a. Apply fault at the TURTLE.CRK 3345.00 (640588) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to PLUMBCR.W 3 (643271) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_684 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_685 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_686 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_687 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_688 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_689 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_690 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_691 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_692 | 3 Phase fault on S1236 5 161.00 (646236) 161 kV Bus a. Apply fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_693 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_694 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_695 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_696 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_697 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_698 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_699 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_700 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_701 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_702 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_703 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_704 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_705 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_706 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_707 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_708 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_709 | 3 Phase fault on 979TP 8 69.000 (647079) 69 kV Bus a. Apply fault at the 979TP 8 69.000 (647079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 979TP 8 (647079) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_710 | 3 Phase fault on 979TP 8 69.000 (647079) 69 kV Bus a. Apply fault at the 979TP 8 69.000 (647079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_711 | 3 Phase fault on 979TP 8 69.000 (647079) 69 kV Bus a. Apply fault at the 979TP 8 69.000 (647079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 979TP 8 (647079) 69.0 kV to S979 8 (647979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_712 | 3 Phase fault on 990TP 8 69.000 (647090) 69 kV Bus a. Apply fault at the 990TP 8 69.000 (647090) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 990TP 8 (647090) 69.0 kV to S982 8 (647982) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_713 | 3 Phase fault on 991TP 8 69.000 (647091) 69 kV Bus a. Apply fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 991TP 8 (647091) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_714 | 3 Phase fault on 991TP 8 69.000 (647091) 69 kV Bus a. Apply fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 991TP 8 (647091) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_715 | 3 Phase fault on 991TP 8 69.000 (647091) 69 kV Bus a. Apply fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_716 | 3 Phase fault on MUD LNG8 69.000 (647104) 69 kV Bus a. Apply fault at the MUD LNG8 69.000 (647104) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_717 | 3 Phase fault on S991 E 8 69.000 (647291) 69 kV Bus a. Apply fault at the S991 E 8 69.000 (647291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_718 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_719 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_720 | 3 Phase fault on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_721 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_722 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_723 | 3 Phase fault on 19&ALVO 7 115.00 (650215) 115 kV Bus a. Apply fault at the 19&ALVO 7 115.00 (650215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_724 | 3 Phase fault on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_725 | 3 Phase fault on 84LEIGHTON7 115.00 (650267) 115 kV Bus a. Apply fault at the 84LEIGHTON7 115.00 (650267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_726 | 3 Phase fault on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_727 | 3 Phase fault on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_728 | 3 Phase fault on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_729 | 3 Phase fault on MISSION7 115.00 (652482) 115 kV Bus a. Apply fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_730 | 3 Phase fault on MISSION7 115.00 (652482) 115 kV Bus a. Apply fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_731 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_732 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_733 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to DEERCREK-BE3 (659286) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_734 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_735 | 3 Phase fault on STEGALL4 230.00 (652573) 230 kV Bus a. Apply fault at the STEGALL4 230.00 (652573) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STEGALL4 (652573) 230.0 kV to STEGALL_-MB4 (659206) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_736 | 3 Phase fault on CHAPPEL7 115.00 (653300) 115 kV Bus a. Apply fault at the CHAPPEL7 115.00 (653300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPPEL7 (653300) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_737 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_738 | 3 Phase fault on SIDNEY 7 115.00 (653572) 115 kV Bus a. Apply fault at the SIDNEY 7 115.00 (653572) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY 7 (653572) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_739 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_740 | 3 Phase fault on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_741 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_742 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_743 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_744 | 3 Phase fault on SIDNEY___TS4230.00 (659134) 230 kV Bus a. Apply fault at the SIDNEY___TS4230.00 (659134) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_745 | 3 Phase fault on GRANTNB_-TS7115.00 (659800) 115 kV Bus a. Apply fault at the GRANTNB_-TS7115.00 (659800) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTNB_-TS7 (659800) 115.0 kV to SPCREEK_-TS7 (659810) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_746 | 3 Phase fault on LAMAR___-TS7115.00 (659804) 115 kV Bus a. Apply fault at the LAMAR___-TS7115.00 (659804) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMAR___-TS7 (659804) 115.0 kV to SPCREEK_-TS7 (659810) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_747 | 3 Phase fault on ELSIETP_-TS7115.00 (659807) 115 kV Bus a. Apply fault at the ELSIETP_-TS7115.00 (659807) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELSIETP_-TS7 (659807) 115.0 kV to ROSCOE__-TS7 (659809) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_748 | 3 Phase fault on MCONGHY_-TS7115.00 (659824) 115 kV Bus a. Apply fault at the MCONGHY_-TS7115.00 (659824) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCONGHY_-TS7 (659824) 115.0 kV to ARTHUR__-TS7 (659825) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_749 | 3 Phase fault on ARTHUR__-TS7115.00 (659825) 115 kV Bus a. Apply fault at the ARTHUR__-TS7115.00 (659825) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTHUR__-TS7 (659825) 115.0 kV to HYANNIS_-TS7 (659826) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_750 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_751 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_752 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_753 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_754 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_755 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_756 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_757 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_758 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_759 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_760 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_761 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_762 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_763 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT8 (640052) 69.0 kV to AINSWRT7 (640051) 115.0 kV to AINSWORTHT29 (643002) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_764 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_765 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_766 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG8 (640101) 69.0 kV to CAMBRIG7 (640100) 115.0 kV to CAMBRIDGET19 (643028) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_767 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 8 (640145) 69.0 kV to COZAD 7 (640144) 115.0 kV to COZAD T2 9 (643174) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_768 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_769 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK 8 (640162) 69.0 kV to ELMCRK_7 (640161) 115.0 kV to ELMCREEK T19 (643053) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_770 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 8 (640168) 69.0 kV to ENDERS 7 (640167) 115.0 kV to ENDERS T1 9 (643055) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_771 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 8 (640179) 69.0 kV to GENEVA 7 (640178) 115.0 kV to GENEVA T2 9 (643062) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_772 | 3 Phase fault on GOTHNBG7 115.00 (640196) 115 kV Bus a. Apply fault at the GOTHNBG7 115.00 (640196) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTHNBG8 (640197) 69.0 kV to GOTHNBG7 (640196) 115.0 kV to GOTHENBRGT29 (643068) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_773 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R8 (640207) 69.0 kV to GUIDE R7 (640206) 115.0 kV to GUIDEROCKT19 (643073) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_774 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV to HILDRTH7 (640222) 115.0 kV to HILDRETH T19 (643079) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_775 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_776 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.LK8 (640245) 69.0 kV to JOHN.LK7 (640244) 115.0 kV to JOHNSONLKT19 (643089) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_777 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNGTN8 (640257) 69.0 kV to LXNGTN 7 (640256) 115.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_778 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 8 (640262) 69.0 kV to LOWELL 7 (640261) 115.0 kV to LOWELL T1 9 (643096) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_779 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_780 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_781 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 8 (640273) 69.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_782 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT8 (640288) 69.0 kV to N.PLATT7 (640287) 115.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_783 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_784 | 3 Phase fault on ORLEANS7 115.00 (640310) 115 kV Bus a. Apply fault at the ORLEANS7 115.00 (640310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS8 (640311) 69.0 kV to ORLEANS7 (640310) 115.0 kV to ORLEANS T1 9 (643120) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_785 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_786 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to (659608) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_787 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_788 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_789 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 8 (640373) 69.0 kV to SUTTON 7 (640372) 115.0 kV to SUTTON T1 9 (643149) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_790 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT8 (640415) 69.0 kV to CARLJCT7 (640105) 115.0 kV to CARLTNJCTT29 (643031) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_791 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_792 | 3 Phase fault on YORK SW7 115.00 (640413) 115 kV Bus a. Apply fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK.SW T2 8 (640447) 69.0 kV to YORK SW7 (640413) 115.0 kV to YORK.SW T2 9 (643176) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_793 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_794 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to (994010) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_795 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_796 | 3 Phase fault on BASSETT 7115.00 (640580) 115 kV Bus a. Apply fault at the BASSETT 7115.00 (640580) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 8 (640581) 69.0 kV to BASSETT 7 (640580) 115.0 kV to BASSETT T1 9 (643180) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_797 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_798 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_799 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_800 | 3 Phase fault on STEINER7 115.00 (640361) 115 kV Bus a. Apply fault at the STEINER7 115.00 (640361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S966 8 (647966) 69.0 kV to STEINER7 (640361) 115.0 kV to STEINER T1 9 (643143) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_801 | 3 Phase fault on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_802 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_803 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_804 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_805 | 3 Phase fault on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_806 | 3 Phase fault on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to STEGALL_-MB4 (659206) 230.0 kV to STEGALL_-MB9 (659167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_807 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_808 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_809 | 3 Phase fault on MISSION7 115.00 (652482) 115 kV Bus a. Apply fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MISSION7 (652482) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_810 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_811 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_812 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Local_Fault_813 | 3 Phase fault on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SD.LS-LR-MB3 (659426) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_001 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_002 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_003 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_004 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_005 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_006 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_007 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_008 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_009 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_010 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | Reclosing removed.
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_011 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_012 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_014 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_015 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_017 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_018 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_019 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_020 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_021 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_022 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_023 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_024 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_025 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_026 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_027 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_028 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_029 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_030 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_031 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_032 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_033 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_034 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_035 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_036 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_037 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_038 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_039 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_040 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_041 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_042 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_043 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_044 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_045 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_046 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_047 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_048 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_049 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_050 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_051 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_052 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_053 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to (659608) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_054 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_055 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_056 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue is also observed in Base case. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Transfer | G02_P1_Regional_Fault_057 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_001 | Single Phase Fault with Stuck Breaker on LKFLDXL3 345.00 (601029) 345 kV Bus a. Apply Fault at the LKFLDXL3 345.00 (601029) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOBLES 3 (601034) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 b.2. GRE-TRIMWNDW (615100) 0.6 kV to GRE-TRIMWNA9 (615101) 34.5 kV Two Winding #1 b.3. GRE-TRIMWNA9 (615101) 34.5 kV to GRE-TRIMWNB9 (615102) 34.5 kV Transmission Circuit #z b.4. TRIMONT WD 3 (601068) 345.0 kV to GRE-TRIMWNB9 (615102) 34.5 kV Two Winding #1 b.5. GRE-ELMCWNDW (615104) 0.6 kV to GRE-ELMCWNA9 (615105) 34.5 kV Two Winding #1 b.6. GRE-ELMCWNA9 (615105) 34.5 kV to GRE-ELMCWNB9 (615106) 34.5 kV Transmission Circuit #z b.7. TRIMONT WD 3 (601068) 345.0 kV to GRE-ELMCWNB9 (615106) 34.5 kV Two Winding #1 b.8. ELMCREEK2 W8 (606025) 34.5 kV to ECRK2 FDR (606063) 34.5 kV Transmission Circuit #1 b.9. TRIMONT WD 3 (601068) 345.0 kV to ELMCREEK2 W8 (606025) 34.5 kV Two Winding #1 b.10. ECRK2 FDR (606063) 34.5 kV to G514 ECRK2 W (600134) 0.7 kV Two Winding #1 b.11. GRE-LGS 31G (615041) 13.8 kV to GRE-LKFDGEN3 (615040) 345.0 kV to GRE-LGS 32G (615042) 13.8 kV Three Winding #1 b.12. GRE-LGS 32G (615042) 13.8 kV to GRE-LKFDGEN3 (615040) 345.0 kV to GRE-LGS 31G (615041) 13.8 kV Three Winding #1 b.13. GRE-LGS 33G (615043) 13.8 kV to GRE-LKFDGEN3 (615040) 345.0 kV to GRE-LGS 34G (615044) 13.8 kV Three Winding #1 b.14. GRE-LGS 34G (615044) 13.8 kV to GRE-LKFDGEN3 (615040) 345.0 kV to GRE-LGS 33G (615043) 13.8 kV Three Winding #1 b.15. GRE-LGS 35G (615045) 13.8 kV to GRE-LKFDGEN3 (615040) 345.0 kV to GRE-LGS 36G (615046) 13.8 kV Three Winding #1 b.16. GRE-LGS 36G (615046) 13.8 kV to GRE-LKFDGEN3 (615040) 345.0 kV to GRE-LGS 35G (615045) 13.8 kV Three Winding #1 b.17. LKFLDXL3 (601029) 345.0 kV to TRIMONT WD 3 (601068) 345.0 kV Transmission Circuit #1 b.18. LKFLDXL3 (601029) 345.0 kV to CRANDAL 3 (601074) 345.0 kV Transmission Circuit #1 b.19. LKFLDXL3 (601029) 345.0 kV to GRE-LKFDGEN3 (615040) 345.0 kV Transmission Circuit #z b.20. LKFLDXL3 (601029) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_003 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_004 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_005 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_006 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_007 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_008 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_009 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOBLES 3 (601034) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_010 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOBLES 3 (601034) 345.0 kV to LAKEFLD3 (631138) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_011 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_012 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_013 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.4. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_014 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_015 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_016 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_017 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_018 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_019 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_020 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_021 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_022 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_023 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_024 | Single Phase Fault with Stuck Breaker on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply Fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.3. OBRIEN 3 (635368) 345.0 kV to Fixed Shunt Device b.4. LAKEFLD3 (631138) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_025 | Single Phase Fault with Stuck Breaker on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply Fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV to OBRIEN B1 9 (635410) 34.5 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV to OBRIEN B2 9 (635411) 34.5 kV Two Winding #1 b.4. LAKEFLD3 (631138) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_026 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_027 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_028 | Single Phase Fault with Stuck Breaker on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B2 9 (635402) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_029 | Single Phase Fault with Stuck Breaker on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply Fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B3 9 (635403) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 b.3. OBRIEN 3 (635368) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_030 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_031 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_032 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_033 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_034 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_035 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_036 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_037 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_038 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_039 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_040 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_041 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_042 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_043 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_044 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_045 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_046 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_047 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_048 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_049 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_050 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_051 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_052 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_053 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_054 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_055 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_056 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_057 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_058 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_059 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_060 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_061 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_062 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_063 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_064 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_065 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_066 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_067 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_068 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_069 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_070 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_071 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_072 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_073 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_074 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.2. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_075 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-TERT1 (539743) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV Three Winding #1 b.2. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 b.3. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.4. SVWF1-TX1 (539752) 34.5 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.7. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.9. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_076 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.4. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_077 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.2. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_078 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 b.4. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_079 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_080 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_081 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_082 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.2. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.3. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_083 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_084 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_085 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_086 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_087 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_088 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_089 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_090 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_091 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_092 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_093 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_094 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_095 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 b.4. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.5. HOLCOMB3 (531448) 115.0 kV to # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_096 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_097 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_098 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_099 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_100 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_101 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_102 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_103 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_104 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_105 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_106 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_107 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_108 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_109 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_110 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_111 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_112 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_113 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_114 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_115 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_116 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_117 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_118 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_119 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_120 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_121 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_122 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_123 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_124 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_125 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_126 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_127 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_128 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_129 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_130 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_131 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_132 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_133 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_134 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_135 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_136 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_137 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_138 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_139 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_140 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_141 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_142 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_143 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_144 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_145 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_146 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_147 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_148 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_149 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_150 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_151 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_152 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_153 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_154 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_155 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_156 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_157 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_158 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_159 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_160 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_161 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_162 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_163 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_164 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_165 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_166 | Single Phase Fault with Stuck Breaker on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply Fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_167 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_168 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_169 | Single Phase Fault with Stuck Breaker on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply Fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EGYCNTR7 (641087) 115.0 kV to EGY CTRG (641086) 13.8 kV Two Winding #1 b.2. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_170 | Single Phase Fault with Stuck Breaker on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply Fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EGYCNTR7 (641087) 115.0 kV to EGYCTR2G (641089) 18.0 kV Two Winding #1 b.2. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_171 | Single Phase Fault with Stuck Breaker on S. 281 7 115.00 (641090) 115 kV Bus a. Apply Fault at the S. 281 7 115.00 (641090) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. D.HENRY7 (641083) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 b.3. S. 281 9 (641096) 13.8 kV to S. 281 7 (641090) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_172 | Single Phase Fault with Stuck Breaker on S. 281 7 115.00 (641090) 115 kV Bus a. Apply Fault at the S. 281 7 115.00 (641090) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. D.HENRY7 (641083) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 b.3. S. 281 9 (641096) 13.8 kV to S. 281 7 (641090) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_173 | Single Phase Fault with Stuck Breaker on S. 281 7 115.00 (641090) 115 kV Bus a. Apply Fault at the S. 281 7 115.00 (641090) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. D.HENRY7 (641083) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 b.3. S. 281 9 (641096) 13.8 kV to S. 281 7 (641090) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_174 | Single Phase Fault with Stuck Breaker on BYPASS 7 115.00 (641082) 115 kV Bus a. Apply Fault at the BYPASS 7 115.00 (641082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BYPASS 9 (641091) 13.8 kV to BYPASS 7 (641082) 115.0 kV Two Winding #1 b.2. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_175 | Single Phase Fault with Stuck Breaker on E7THST 7 115.00 (641085) 115 kV Bus a. Apply Fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_176 | Single Phase Fault with Stuck Breaker on E7THST 7 115.00 (641085) 115 kV Bus a. Apply Fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_177 | Single Phase Fault with Stuck Breaker on E7THST 7 115.00 (641085) 115 kV Bus a. Apply Fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_178 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_179 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.5. POSTROCK7 (530583) 345.0 kV to G20-070-TAP (765035) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_180 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.2. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_181 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_182 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_183 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_184 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_185 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_186 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_187 | Single Phase Fault with Stuck Breaker on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply Fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_188 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_189 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_190 | Single Phase Fault with Stuck Breaker on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply Fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.5. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_191 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_192 | Single Phase Fault with Stuck Breaker on OGALATP3 115.00 (530677) 115 kV Bus a. Apply Fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.6. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.7. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_193 | Single Phase Fault with Stuck Breaker on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply Fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_194 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_195 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_196 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_197 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_198 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_199 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_200 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_201 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_202 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_203 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_204 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_205 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_206 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_207 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_208 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_209 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.5. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.6. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_210 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_211 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_212 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_213 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_214 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_215 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_216 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_217 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_218 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_219 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_220 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_221 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_222 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_223 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_224 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_225 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_226 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_227 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_228 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_229 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_230 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_231 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_232 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_233 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_234 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_235 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_236 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_237 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_238 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_239 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_240 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_241 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_242 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_243 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_244 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_245 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_246 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_247 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_248 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_249 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_250 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_251 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 b.5. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_252 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_253 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_254 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_255 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_256 | Single Phase Fault with Stuck Breaker on JULSTAP7 115.00 (640246) 115 kV Bus a. Apply Fault at the JULSTAP7 115.00 (640246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-147 (588220) 115.0 kV to SIDNEY 7 (653572) 115.0 kV Transmission Circuit #1 b.2. SIDNEY 7 (653572) 115.0 kV to COLTON__-TS7 (659817) 115.0 kV Transmission Circuit #1 b.3. SIDNEY 7 (653572) 115.0 kV to SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-TS8 (659803) 13.8 kV Three Winding #1 b.4. B.SPRGS7 (640068) 115.0 kV to JULSTAP7 (640246) 115.0 kV Transmission Circuit #1 b.5. JULSTAP7 (640246) 115.0 kV to CHAPPEL7 (653300) 115.0 kV Transmission Circuit #1 b.6. JULSTAP7 (640246) 115.0 kV to HIGHLINE (653303) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_257 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_258 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #z b.3. SIDNEY___TS4 (659134) 230.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Transmission Circuit #1 b.4. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 b.5. SIDNEY__-MB9 (659168) 13.8 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB4 (659210) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_259 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.3. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_260 | Single Phase Fault with Stuck Breaker on LARAMIE_-MB3345.00 (659131) 345 kV Bus a. Apply Fault at the LARAMIE_-MB3345.00 (659131) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LARAMIE_-MB3 (659131) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 b.2. LARAMIE_-MB3 (659131) 345.0 kV to SD.LS-LR-MB3 (659426) 345.0 kV Transmission Circuit #1 b.3. LRS_1___-MBG (659118) 24.0 kV to LARAMIE_-MB3 (659131) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_261 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_262 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_263 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_264 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_265 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_266 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_267 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_268 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_269 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_270 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_271 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_272 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_273 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_274 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_275 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_276 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_277 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_278 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_279 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_280 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_281 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_282 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_283 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_284 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_285 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_286 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_287 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_288 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_289 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_290 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_291 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_292 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_293 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_294 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_295 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_296 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_297 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_298 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_299 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_300 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_301 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_302 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_303 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_304 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_305 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_306 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_307 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_308 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_309 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_310 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_311 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_312 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_313 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_314 | Single Phase Fault with Stuck Breaker on S1217 5 (646217) 161 kV Bus a. Apply Fault at the S1217 5 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_315 | Single Phase Fault with Stuck Breaker on S1217 5 (646217) 161 kV Bus a. Apply Fault at the S1217 5 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_316 | Single Phase Fault with Stuck Breaker on S1217 5 (646217) 161 kV Bus a. Apply Fault at the S1217 5 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_317 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_318 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_319 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_320 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_321 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_322 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_323 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S1366 5 (646366) 161.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_324 | Single Phase Fault with Stuck Breaker on S1251 5 (646251) 161 kV Bus a. Apply Fault at the S1251 5 (646251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_325 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_326 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_327 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_328 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_329 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_330 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_331 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_332 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_333 | Single Phase Fault with Stuck Breaker on S1366 5 (646366) 161 kV Bus a. Apply Fault at the S1366 5 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.8. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.9. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.10. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_334 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_335 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_336 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_337 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_338 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_339 | Single Phase Fault with Stuck Breaker on PHILL 5 161.00 (541225) 161 kV Bus a. Apply Fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 b.2. DOGWDCT1 (541163) 18.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 b.3. DOGWDCT2 (541164) 18.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 b.4. DOGWDSTG (541162) 18.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_340 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_341 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 b.3. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 b.4. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.6. MULLNCR7 (541197) 345.0 kV to GEN-2018-022 (762581) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_342 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.3. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.4. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_343 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.4. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 b.5. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T12 (543639) 13.8 kV Three Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_344 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.4. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.6. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_345 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 b.3. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 b.4. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.6. MULLNCR7 (541197) 345.0 kV to GEN-2018-022 (762581) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_346 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 b.3. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 b.4. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.6. MULLNCR7 (541197) 345.0 kV to GEN-2018-022 (762581) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_347 | Single Phase Fault with Stuck Breaker on OSBORN7 345.00 (541501) 345 kV Bus a. Apply Fault at the OSBORN7 345.00 (541501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to OSBORN7 (541501) 345.0 kV Transmission Circuit #1 b.2. OSBORN7 (541501) 345.0 kV to OSBORN_B1_1 (541502) 34.5 kV to OSBORN_TER_1 (541505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_348 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.3. HOLT 7 (541510) 345.0 kV to ROCKCK7 (541511) 345.0 kV Transmission Circuit #1 b.4. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.5. HOLT 7 (541510) 345.0 kV to GEN-2017-115 (760746) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_349 | Single Phase Fault with Stuck Breaker on ROCKCK7 345.00 (541511) 345 kV Bus a. Apply Fault at the ROCKCK7 345.00 (541511) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to ROCKCK7 (541511) 345.0 kV Transmission Circuit #1 b.2. ROCKCK7 (541511) 345.0 kV to OUTLAW (541543) 345.0 kV Transmission Circuit #1 b.3. ROCKCK7 (541511) 345.0 kV to ROCKCK_T1_1 (541512) 34.5 kV to ROCKCK_TR1_1 (541508) 13.2 kV Three Winding #1 b.4. ROCKCK7 (541511) 345.0 kV to ROCKCK_T2_1 (541515) 34.5 kV to ROCKCK_TR2_1 (541509) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_350 | Single Phase Fault with Stuck Breaker on OUTLAW 345.00 (541543) 345 kV Bus a. Apply Fault at the OUTLAW 345.00 (541543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROCKCK7 (541511) 345.0 kV to OUTLAW (541543) 345.0 kV Transmission Circuit #1 b.2. OUTLAW (541543) 345.0 kV to OUTLAW_T1_1 (541544) 34.5 kV to OUTLAW_TR1_1 (541551) 13.8 kV Three Winding #1 b.3. OUTLAW (541543) 345.0 kV to OUTLAW_T2_1 (541547) 34.5 kV to OUTLAW_TR2_1 (541552) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_351 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. KETCHEM7 (541500) 345.0 kV to OSBORN7 (541501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_352 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_353 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_354 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.6. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.7. SEWARD 2 (530565) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.8. SEWARD 2 (530565) 69.0 kV to ZOOK 2 (530577) 69.0 kV Transmission Circuit #1 b.10. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.11. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.12. S ELWD 2 (530567) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.13. S ELWD 2 (530567) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_355 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.3. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.4. ALEXND-T (539902) 12.5 kV to ALEXNDR1 (539702) 34.5 kV to ALXNDR 3 (530606) 115.0 kV Three Winding #1 b.6. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.8. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.9. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.10. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.13. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.14. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.15. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_356 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.4. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.5. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.6. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.7. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 b.8. GRTBEND3 (539678) 115.0 kV to GRTBEND1 (539719) 34.5 kV to GRTBENDT (539921) 7.2 kV Three Winding #1 b.10. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.11. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.12. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.13. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.15. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.16. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.17. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.18. 24-FREY3 (539661) 115.0 kV to GEN-2018-116 (763329) 115.0 kV Transmission Circuit #1 b.19. 24-FREY3 (539661) 115.0 kV to 24-FREY1 (539707) 34.5 kV to 24-FREYT (539907) 13.8 kV Three Winding #1 b.20. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.21. 2ND-KS 3 (539689) 115.0 kV to 2ND-KS 1 (539728) 34.5 kV to 2ND-KS T (539931) 13.8 kV Three Winding #1 b.22. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.23. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.24. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.25. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_357 | Single Phase Fault with Stuck Breaker on SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus a. Apply Fault at the SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.2. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.3. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.4. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.7. SPRVILL-EHVB (539117) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV to SVWF3-TERT1 (539744) 13.8 kV Three Winding #1 b.8. SPERVLTT (539935) 13.8 kV to SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV Three Winding #1 b.9. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.11. SPEARVL3 (539694) 115.0 kV to SPEARVL1 (539732) 34.5 kV to SPERVLDT (539936) 13.8 kV Three Winding #1 b.12. SVWF2 1 (539136) 0.6 kV to SVWF2-CLCT1 (539135) 34.5 kV Two Winding #1 b.13. SVWF1 1 (539116) 0.6 kV to SVWF1-CLCT1 (539115) 34.5 kV Two Winding #1 b.14. SVWF3-CLCT1 (539119) 34.5 kV to SVWF3 1 (539120) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_358 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.5. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.6. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (587500) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_359 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to GEN-2018-025 (762603) 345.0 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.5. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 b.6. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 b.7. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.8. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.9. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.10. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.11. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_360 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to GEN-2018-025 (762603) 345.0 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.5. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 b.6. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 b.7. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_361 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.3. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.5. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.6. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.7. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_362 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.3. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.5. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_363 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.4. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.5. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.6. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 b.7. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.8. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.9. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.10. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_364 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.4. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.5. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.6. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_365 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.5. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.6. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.7. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.8. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.9. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.10. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.11. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.13. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.14. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.15. S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.16. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.17. S906 N 8 (647006) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #z1 b.18. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.19. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.20. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.21. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.23. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.24. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.25. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.26. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.27. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_366 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.5. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_367 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.6. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 b.8. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.9. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.10. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 b.11. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_368 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.6. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_369 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.3. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.5. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.6. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.7. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.8. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.9. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.12. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.13. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.14. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.15. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.16. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_370 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.3. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_371 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.3. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.4. S3740 3 (645740) 345.0 kV to GEN-2018-033 (762691) 345.0 kV Transmission Circuit #1 b.5. S3740 3 (645740) 345.0 kV to GEN-2020-036 (764690) 345.0 kV Transmission Circuit #1 b.6. S3740 3 (645740) 345.0 kV to GEN-2020-038 (764705) 345.0 kV Transmission Circuit #1 b.7. S3740 3 (645740) 345.0 kV to CASS 1G (645041) 15.0 kV Two Winding #1 b.8. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_372 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 b.3. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.6. S1361 5 (646361) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_373 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_374 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.3. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.4. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.5. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 b.6. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.7. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.8. S901 8 (647901) 69.0 kV to GEN-2017-198 (760872) 69.0 kV Transmission Circuit #1 b.9. S901 8 (647901) 69.0 kV to JONES 1G (645051) 13.8 kV Two Winding #1 b.10. S901 8 (647901) 69.0 kV to JONES 2G (645052) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_375 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.4. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 b.5. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #2 b.6. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.7. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.8. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.9. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 b.10. S1211 5 (646211) 161.0 kV to S1211T39 (645127) 13.8 kV Two Winding #1 b.11. S1211 5 (646211) 161.0 kV to S1211T49 (645128) 13.8 kV Two Winding #1 b.12. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 b.13. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.14. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.15. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.16. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_376 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 b.4. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.5. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.6. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_377 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.4. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.5. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_378 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.5. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.6. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_379 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.3. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 b.4. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.5. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.6. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_380 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 b.4. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.5. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_381 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.5. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 b.6. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_382 | Single Phase Fault with Stuck Breaker on S1291 5 161.00 (646291) 161 kV Bus a. Apply Fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 b.3. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 b.4. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_383 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_384 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. SD.LS-KS-MB3 (659425) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_385 | Single Phase Fault with Stuck Breaker on SD.LS-LR-MB3345.00 (659426) 345 kV Bus a. Apply Fault at the SD.LS-LR-MB3345.00 (659426) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.LS-LR-MB3 (659426) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #z b.2. SD.LS-LR-MB3 (659426) 345.0 kV to LARAMIE_-MB3 (659131) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_386 | Single Phase Fault with Stuck Breaker on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply Fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to LARAMIE_-MB3 (659131) 345.0 kV Transmission Circuit #1 b.2. STEGALL_-MB3 (659135) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_387 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S1214 5 (646214) 161.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 b.2. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_388 | Single Phase Fault with Stuck Breaker on S983 8 69.000 (647983) 69 kV Bus a. Apply Fault at the S983 8 69.000 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S983 8 (647983) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.2. S983 8 (647983) 69.0 kV to S902 8 (647902) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_389 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_390 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_391 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to AXTELL 7 (640066) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_392 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_393 | Single Phase Fault with Stuck Breaker on S1362 5 161.00 (646362) 161 kV Bus a. Apply Fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 b.2. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_394 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_395 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_396 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_397 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.2. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_398 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_399 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_400 | Single Phase Fault with Stuck Breaker on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply Fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to G20-077-TAP (764490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_401 | Single Phase Fault with Stuck Breaker on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply Fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEBRN N7 (640218) 115.0 kV to CARLJCT7 (640105) 115.0 kV Transmission Circuit #1 b.2. HEBRN N7 (640218) 115.0 kV to HEBRON 7 (640220) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_402 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_403 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_404 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. 103&ROKEBY3 (650189) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_405 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.LS-KS-MB3 (659425) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_406 | Single Phase Fault with Stuck Breaker on SD.LS-LR-MB3 (659426) 345 kV Bus a. Apply Fault at the SD.LS-LR-MB3 (659426) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.LS-LR-MB3 (659426) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_407 | Single Phase Fault with Stuck Breaker on STEGALL_-MB3 (659135) 345 kV Bus a. Apply Fault at the STEGALL_-MB3 (659135) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_408 | Single Phase Fault with Stuck Breaker on S914A 8 (647014) 69 kV Bus a. Apply Fault at the S914A 8 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_409 | Single Phase Fault with Stuck Breaker on S983 8 (647983) 69 kV Bus a. Apply Fault at the S983 8 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S983 8 (647983) 69.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_410 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_411 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_413 | Single Phase Fault with Stuck Breaker on ORLEANS7 (640310) 115 kV Bus a. Apply Fault at the ORLEANS7 (640310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORLEANS7 (640310) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_414 | Single Phase Fault with Stuck Breaker on S1281 5 (646281) 161 kV Bus a. Apply Fault at the S1281 5 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_415 | Single Phase Fault with Stuck Breaker on SCS 1X (645071) 15 kV Bus a. Apply Fault at the SCS 1X (645071) 15 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCS 1X (645071) 15.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_416 | Single Phase Fault with Stuck Breaker on SCS 2X (645072) 15 kV Bus a. Apply Fault at the SCS 2X (645072) 15 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCS 2X (645072) 15.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_417 | Single Phase Fault with Stuck Breaker on S1362 5 (646362) 161 kV Bus a. Apply Fault at the S1362 5 (646362) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1362 5 (646362) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_418 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_419 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_420 | Single Phase Fault with Stuck Breaker on CASS 1G (645041) 15 kV Bus a. Apply Fault at the CASS 1G (645041) 15 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CASS 1G (645041) 15.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_421 | Single Phase Fault with Stuck Breaker on CASS 2G (645042) 15 kV Bus a. Apply Fault at the CASS 2G (645042) 15 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CASS 2G (645042) 15.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_422 | Single Phase Fault with Stuck Breaker on S3458 3 (645458) 345 kV Bus a. Apply Fault at the S3458 3 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_423 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_424 | Single Phase Fault with Stuck Breaker on S1252 5 (646252) 161 kV Bus a. Apply Fault at the S1252 5 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1252 5 (646252) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_425 | Single Phase Fault with Stuck Breaker on MIL 1-3X (645081) 13.8 kV Bus a. Apply Fault at the MIL 1-3X (645081) 13.8 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIL 1-3X (645081) 13.8 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_426 | Single Phase Fault with Stuck Breaker on MIL 4-6X (645082) 13.8 kV Bus a. Apply Fault at the MIL 4-6X (645082) 13.8 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIL 4-6X (645082) 13.8 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_427 | Single Phase Fault with Stuck Breaker on MIL 7-9X (645083) 13.8 kV Bus a. Apply Fault at the MIL 7-9X (645083) 13.8 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIL 7-9X (645083) 13.8 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_428 | Single Phase Fault with Stuck Breaker on CODY 7 (640117) 115 kV Bus a. Apply Fault at the CODY 7 (640117) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CODY 7 (640117) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_429 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_430 | Single Phase Fault with Stuck Breaker on FAIRBRY7 (640169) 115 kV Bus a. Apply Fault at the FAIRBRY7 (640169) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRBRY7 (640169) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_431 | Single Phase Fault with Stuck Breaker on HEBRN N7 (640218) 115 kV Bus a. Apply Fault at the HEBRN N7 (640218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEBRN N7 (640218) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_432 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_433 | Single Phase Fault with Stuck Breaker on S1237 5 (646237) 161 kV Bus a. Apply Fault at the S1237 5 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Local_Fault_434 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_001 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_002 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_003 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_004 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_005 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_006 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_007 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_008 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_009 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_010 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_011 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_012 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_013 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_014 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_015 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_016 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_017 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_018 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_019 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_020 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_021 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_023 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_024 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_025 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_026 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_027 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_028 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_029 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_030 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_031 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_032 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_033 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_034 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_035 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_036 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_037 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_038 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_039 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_040 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_041 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_042 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_043 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_044 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_045 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_046 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_047 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_048 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_049 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_050 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_051 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_052 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_053 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_054 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.5. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.6. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.7. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.8. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.9. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.10. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.11. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.13. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.14. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.15. S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.16. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.17. S906 N 8 (647006) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #z1 b.18. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.19. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.20. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.21. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.23. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.24. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.25. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.26. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.27. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_055 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.5. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_056 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.6. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 b.8. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.9. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.10. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 b.11. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25W | Transfer | G02_P4_Regional_Fault_057 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.6. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). The issue is not observed in base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_005 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_006 | 3 Phase fault on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_034 | 3 Phase fault on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_036 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_044 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_046 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_051 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_052 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_053 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_059 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_002 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_005 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_007 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_010 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Reclosing removed.
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_005 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_009 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_034 | 3 Phase fault on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_050 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_059 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_067 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_458 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_459 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_530 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_531 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_536 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REMSEN 3 (635398) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_538 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to GLACIAL EDGE (637009) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Local_Fault_807 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Regional_Fault_010 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Regional_Fault_011 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Regional_Fault_036 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Regional_Fault_043 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Regional_Fault_044 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25S | Base | G02_P1_Regional_Fault_056 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_009 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_035 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_047 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_050 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_063 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_458 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_530 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_531 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_532 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_533 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_535 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_537 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_538 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to GLACIAL EDGE (637009) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Local_Fault_807 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_001 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_008 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_011 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_036 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_043 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_044 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_045 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
02 - Nebraska | 25W | Base | G02_P1_Regional_Fault_056 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | 1. Reduce clearing time to 3.5 cycles. 2. Reduce acceleration factor to 0.1. 3. Remove reclosing
03 - Central | 25S | Transfer | G03_P1_Local_Fault_001 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_002 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_003 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_004 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_005 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_006 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.2. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_007 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_008 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_009 | 3 Phase fault on 5COMPTN 161.00 (300719) 161 kV Bus a. Apply fault at the 5COMPTN 161.00 (300719) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_010 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.3. BUFORD 5 (504440) 161.0 kV to NORFORK5 (505448) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_011 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.4. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_012 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_013 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_014 | 3 Phase fault on CHAMSPR7 345.00 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 345.00 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_015 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_016 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_017 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_018 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_019 | 3 Phase fault on 5GRANDVIEW% 161.00 (338099) 161 kV Bus a. Apply fault at the 5GRANDVIEW% 161.00 (338099) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_020 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). This issue is also observed in the Base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_021 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_022 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_023 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_024 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_025 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_026 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_027 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_028 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_029 | 3 Phase fault on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_030 | 3 Phase fault on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_031 | 3 Phase fault on RGAFBTP2 69.000 (541322) 69 kV Bus a. Apply fault at the RGAFBTP2 69.000 (541322) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.2. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.3. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.6. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_032 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 b.2. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_033 | 3 Phase fault on APCITY 2 69.000 (541306) 69 kV Bus a. Apply fault at the APCITY 2 69.000 (541306) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to URICHTP2 (541304) 69.0 kV Transmission Circuit #1 b.2. URICHTP2 (541304) 69.0 kV to URICH 2 (541305) 69.0 kV Transmission Circuit #1 b.3. URICHTP2 (541304) 69.0 kV to APCITY 2 (541306) 69.0 kV Transmission Circuit #1 b.4. APCITY 2 (541306) 69.0 kV to NEVADA 2 (541308) 69.0 kV Transmission Circuit #1 b.5. APCITY 2 (541306) 69.0 kV to ASGI-2018-00 (762361) 69.0 kV Transmission Circuit #1 b.6. APCITY 2 (541306) 69.0 kV to APCITY1 (541325) 34.5 kV to APCITY_TER1 (541326) 2.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_034 | 3 Phase fault on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 b.2. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 b.3. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.4. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.5. FREEMAN2 (541291) 69.0 kV to FREEMAN_SP2 (541540) 69.0 kV Transmission Circuit #1 b.6. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_035 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_036 | 3 Phase fault on HLDENTP2 69.000 (541386) 69 kV Bus a. Apply fault at the HLDENTP2 69.000 (541386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to CNTRVIEW2 (541385) 69.0 kV Transmission Circuit #1 b.2. CNTRVIEW2 (541385) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.3. HOLDEN 2 (541278) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.4. HLDENTP2 (541386) 69.0 kV to KNGSVIL 2 (541387) 69.0 kV Transmission Circuit #1 b.5. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 b.6. RGREEN 2 (541279) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_037 | 3 Phase fault on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.3. POSTOAK2 (541300) 69.0 kV to POSTOAK1 (541373) 34.5 kV to POSTOAK_TER1 (541374) 2.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_038 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_039 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_040 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_041 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_042 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_043 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_044 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_045 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_046 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_047 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_048 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_049 | 3 Phase fault on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 b.2. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_050 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_051 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_052 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_053 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_054 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.2. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_055 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_056 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_057 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_058 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_059 | 3 Phase fault on NORTON 5 161.00 (543064) 161 kV Bus a. Apply fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.2. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 b.3. NORTON 5 (543064) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_060 | 3 Phase fault on OSAWTM_CAP5 161.00 (543135) 161 kV Bus a. Apply fault at the OSAWTM_CAP5 161.00 (543135) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLA 5 (543069) 161.0 kV to OSAWAT 5 (543112) 161.0 kV Transmission Circuit #1 b.2. OSAWTM_CAP5 (543135) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_061 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_062 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_063 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_064 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_065 | 3 Phase fault on SWAVCAP2 69.000 (543012) 69 kV Bus a. Apply fault at the SWAVCAP2 69.000 (543012) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.2. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.3. SWAVCAP2 (543012) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_066 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_067 | 3 Phase fault on WINJT S5 161.00 (543010) 161 kV Bus a. Apply fault at the WINJT S5 161.00 (543010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_068 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_069 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_070 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_071 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_072 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). This issue is also observed in the Base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_073 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_074 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_075 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_076 | 3 Phase fault on RGAFBTP2 69.000 (541322) 69 kV Bus a. Apply fault at the RGAFBTP2 69.000 (541322) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.2. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.3. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.4. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.5. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.6. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_077 | 3 Phase fault on HLDENTP2 69.000 (541386) 69 kV Bus a. Apply fault at the HLDENTP2 69.000 (541386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIEW2 (541385) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.2. HOLDEN 2 (541278) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.3. HLDENTP2 (541386) 69.0 kV to KNGSVIL 2 (541387) 69.0 kV Transmission Circuit #1 b.4. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 b.5. RGREEN 2 (541279) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_078 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 b.2. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_079 | 3 Phase fault on APCITY 2 69.000 (541306) 69 kV Bus a. Apply fault at the APCITY 2 69.000 (541306) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. APCITY 2 (541306) 69.0 kV to NEVADA 2 (541308) 69.0 kV Transmission Circuit #1 b.2. URICHTP2 (541304) 69.0 kV to APCITY 2 (541306) 69.0 kV Transmission Circuit #1 b.3. APCITY 2 (541306) 69.0 kV to ASGI-2018-00 (762361) 69.0 kV Transmission Circuit #1 b.4. APCITY 2 (541306) 69.0 kV to APCITY1 (541325) 34.5 kV to APCITY_TER1 (541326) 2.4 kV Three Winding #11 b.5. CLNTPLT2 (541301) 69.0 kV to URICHTP2 (541304) 69.0 kV Transmission Circuit #1 b.6. URICHTP2 (541304) 69.0 kV to URICH 2 (541305) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_080 | 3 Phase fault on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.3. FREEMAN2 (541291) 69.0 kV to FREEMAN_SP2 (541540) 69.0 kV Transmission Circuit #1 b.4. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 b.5. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 b.6. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_081 | 3 Phase fault on RAYTAP 69.000 (541348) 69 kV Bus a. Apply fault at the RAYTAP 69.000 (541348) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.2. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_082 | 3 Phase fault on HLDENTP2 69.000 (541386) 69 kV Bus a. Apply fault at the HLDENTP2 69.000 (541386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIEW2 (541385) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.2. WBURGP 2 (541268) 69.0 kV to CNTRVIEW2 (541385) 69.0 kV Transmission Circuit #1 b.3. HOLDEN 2 (541278) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.4. HLDENTP2 (541386) 69.0 kV to KNGSVIL 2 (541387) 69.0 kV Transmission Circuit #1 b.5. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 b.6. RGREEN 2 (541279) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_083 | 3 Phase fault on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. WBURGP 2 (541268) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 b.3. POSTOAK2 (541300) 69.0 kV to POSTOAK1 (541373) 34.5 kV to POSTOAK_TER1 (541374) 2.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_084 | 3 Phase fault on CORDERTP2 69.000 (543657) 69 kV Bus a. Apply fault at the CORDERTP2 69.000 (543657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORDER 2 (543097) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.2. CORDER 2 (543097) 69.0 kV to CORDER1 (543150) 12.5 kV to CORDER_TER1 (543151) 7.2 kV Three Winding #1 b.3. CORDERTP2 (543657) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.4. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.5. DOVER2 (543101) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.6. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Transient overvoltage rising above 1.2 p.u at SWAVRLY2 69.0 kV (543094) for 2 cycles | Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25S | Transfer | G03_P1_Local_Fault_085 | 3 Phase fault on WHGNSVL2 69.000 (543102) 69 kV Bus a. Apply fault at the WHGNSVL2 69.000 (543102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYVWTP2 (543096) 69.0 kV to AMOCOPL2 (543100) 69.0 kV Transmission Circuit #1 b.2. HIGNSVL2 (543099) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 b.3. CTY HIG2 (543098) 69.0 kV to HIGNSVL2 (543099) 69.0 kV Transmission Circuit #1 b.4. HIGNSVL2 (543099) 69.0 kV to HGNSVL1 (543152) 12.5 kV to HGNSVL_TER1 (543153) 2.4 kV Three Winding #1 b.5. LEXNTON2 (541265) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.6. 13&40 2 (541266) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.7. AMOCOPL2 (543100) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 b.8. WHGNSVL2 (543102) 69.0 kV to WHGNSVL1 (543154) 12.5 kV to WHGNSVL_TER1 (543155) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_086 | 3 Phase fault on SWAVCAP2 69.000 (543012) 69 kV Bus a. Apply fault at the SWAVCAP2 69.000 (543012) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.2. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.3. SWAVCAP2 (543012) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_087 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_088 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_089 | 3 Phase fault on NORTON 5 161.00 (543064) 161 kV Bus a. Apply fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (543064) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_090 | 3 Phase fault on OSAWTM_CAP5 161.00 (543135) 161 kV Bus a. Apply fault at the OSAWTM_CAP5 161.00 (543135) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWTM_CAP5 (543135) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_091 | 3 Phase fault on SWAVCAP5 161.00 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 161.00 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_092 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_093 | 3 Phase fault on SWAVCAP2 69.000 (543012) 69 kV Bus a. Apply fault at the SWAVCAP2 69.000 (543012) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP2 (543012) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_094 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_095 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_096 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.6. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_097 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_098 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_099 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_100 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_101 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_102 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_103 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_104 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_105 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_106 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_107 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_108 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_109 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_110 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_111 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_112 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_113 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_114 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_115 | 3 Phase fault on ELMCREK6 230.00 (539639) 230 kV Bus a. Apply fault at the ELMCREK6 230.00 (539639) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_116 | 3 Phase fault on NMANHT6 230.00 (532865) 230 kV Bus a. Apply fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_117 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_118 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.2. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.3. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_119 | 3 Phase fault on SETAB 3 115.00 (531464) 115 kV Bus a. Apply fault at the SETAB 3 115.00 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_120 | 3 Phase fault on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_121 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_122 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_123 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_124 | 3 Phase fault on PIONEER3 115.00 (531391) 115 kV Bus a. Apply fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to ULYSPLT3 (531490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_125 | 3 Phase fault on GRANTTP3 115.00 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 115.00 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_126 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_127 | 3 Phase fault on HICKOCK3 115.00 (531378) 115 kV Bus a. Apply fault at the HICKOCK3 115.00 (531378) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HICKOCK3 (531378) 115.0 kV to PIONEER3 (531391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_128 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_129 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_130 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_131 | 3 Phase fault on SAT-TAP3 115.00 (531442) 115 kV Bus a. Apply fault at the SAT-TAP3 115.00 (531442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASKELL3 (531374) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.2. PIONTAP3 (531392) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.3. SAT-TAP3 (531442) 115.0 kV to SATMKEC3 (539691) 115.0 kV Transmission Circuit #1 b.4. HASKELL3 (531374) 115.0 kV to SEWARD-3 (531467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_132 | 3 Phase fault on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_133 | 3 Phase fault on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEOTI 3 (531428) 115.0 kV to SELKIRK3 (531434) 115.0 kV Transmission Circuit #1 b.2. SELKIRK3 (531434) 115.0 kV to TRIB SW3 (531438) 115.0 kV Transmission Circuit #1 b.3. LEOTI 3 (531428) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_134 | 3 Phase fault on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.3. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_135 | 3 Phase fault on PILE 3 115.00 (531432) 115 kV Bus a. Apply fault at the PILE 3 115.00 (531432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_136 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_137 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_138 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.2. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.3. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 b.4. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.6. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_139 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_140 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_141 | 3 Phase fault on NATBEEF3 115.00 (539751) 115 kV Bus a. Apply fault at the NATBEEF3 115.00 (539751) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 b.2. NLIB 3 (539737) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_142 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_143 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_144 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_145 | 3 Phase fault on COVERT 3 115.00 (539644) 115 kV Bus a. Apply fault at the COVERT 3 115.00 (539644) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.2. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 b.4. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_146 | 3 Phase fault on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.2. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding #1 b.4. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_147 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_148 | 3 Phase fault on PHLBURG3 115.00 (539685) 115 kV Bus a. Apply fault at the PHLBURG3 115.00 (539685) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_149 | 3 Phase fault on GLENELD3 115.00 (539663) 115 kV Bus a. Apply fault at the GLENELD3 115.00 (539663) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.2. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_150 | 3 Phase fault on JEWELL 3 115.00 (539669) 115 kV Bus a. Apply fault at the JEWELL 3 115.00 (539669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.2. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_151 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_152 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_153 | 3 Phase fault on PIONEER3 115.00 (531391) 115 kV Bus a. Apply fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_154 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_155 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_156 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_157 | 3 Phase fault on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL3 (539701) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_158 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.3. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_159 | 3 Phase fault on 5LOGAN 161.00 (301161) 161 kV Bus a. Apply fault at the 5LOGAN 161.00 (301161) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. 5MANSFDMN (300095) 161.0 kV to 5LOGAN (301161) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_160 | 3 Phase fault on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.3. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_161 | 3 Phase fault on 27CROCO3 115.00 (533187) 115 kV Bus a. Apply fault at the 27CROCO3 115.00 (533187) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_162 | 3 Phase fault on QUINTON3 115.00 (533172) 115 kV Bus a. Apply fault at the QUINTON3 115.00 (533172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_163 | 3 Phase fault on 6 GOLDN3 115.00 (533177) 115 kV Bus a. Apply fault at the 6 GOLDN3 115.00 (533177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_164 | 3 Phase fault on FMC 3 115.00 (533241) 115 kV Bus a. Apply fault at the FMC 3 115.00 (533241) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.2. FMC 3 (533241) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_165 | 3 Phase fault on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_166 | 3 Phase fault on WAVERLY3 115.00 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 115.00 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.2. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_167 | 3 Phase fault on MNTCLLO3 115.00 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 115.00 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.2. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_168 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_169 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_170 | 3 Phase fault on SHERWOD3 115.00 (533194) 115 kV Bus a. Apply fault at the SHERWOD3 115.00 (533194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.2. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_171 | 3 Phase fault on KEENE 3 115.00 (533167) 115 kV Bus a. Apply fault at the KEENE 3 115.00 (533167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to KEENE 3 (533167) 115.0 kV Transmission Circuit #1 b.2. KEENE 3 (533167) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_172 | 3 Phase fault on SOUTHTN3 115.00 (533265) 115 kV Bus a. Apply fault at the SOUTHTN3 115.00 (533265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONITA 3 (533262) 115.0 kV to SOUTHTN3 (533265) 115.0 kV Transmission Circuit #1 b.2. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_173 | 3 Phase fault on GEARY 3 115.00 (533336) 115 kV Bus a. Apply fault at the GEARY 3 115.00 (533336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_174 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_175 | 3 Phase fault on 54&MERI3 115.00 (533156) 115 kV Bus a. Apply fault at the 54&MERI3 115.00 (533156) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.2. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_176 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_177 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_178 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_179 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_180 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_181 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_182 | 3 Phase fault on EMANHAT3 115.00 (533326) 115 kV Bus a. Apply fault at the EMANHAT3 115.00 (533326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT3 (533326) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_183 | 3 Phase fault on BISMARK3 115.00 (533234) 115 kV Bus a. Apply fault at the BISMARK3 115.00 (533234) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK3 (533234) 115.0 kV to FAIRGDS3 (533236) 115.0 kV Transmission Circuit #1 b.2. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_184 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_185 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_186 | 3 Phase fault on SHAWNEE3 115.00 (533176) 115 kV Bus a. Apply fault at the SHAWNEE3 115.00 (533176) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_187 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_188 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_189 | 3 Phase fault on TONGATP3 115.00 (533219) 115 kV Bus a. Apply fault at the TONGATP3 115.00 (533219) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_190 | 3 Phase fault on 166TH 3 115.00 (533233) 115 kV Bus a. Apply fault at the 166TH 3 115.00 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.3. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_191 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_192 | 3 Phase fault on HALLMRK3 115.00 (533242) 115 kV Bus a. Apply fault at the HALLMRK3 115.00 (533242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALLMRK3 (533242) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.2. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.3. HALLMRK3 (533242) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_193 | 3 Phase fault on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_194 | 3 Phase fault on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_195 | 3 Phase fault on LEC U4 3 115.00 (533249) 115 kV Bus a. Apply fault at the LEC U4 3 115.00 (533249) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_196 | 3 Phase fault on BALDCRK3 115.00 (533232) 115 kV Bus a. Apply fault at the BALDCRK3 115.00 (533232) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_197 | 3 Phase fault on MOCKBRD3 115.00 (533253) 115 kV Bus a. Apply fault at the MOCKBRD3 115.00 (533253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.2. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.4. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.5. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_198 | 3 Phase fault on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_199 | 3 Phase fault on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_200 | 3 Phase fault on STAGGHL3 115.00 (533341) 115 kV Bus a. Apply fault at the STAGGHL3 115.00 (533341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to STAGGHL3 (533341) 115.0 kV Transmission Circuit #1 b.2. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_201 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_202 | 3 Phase fault on MIDLADN3 115.00 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 115.00 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_203 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_204 | 3 Phase fault on MOONLIT3 115.00 (533254) 115 kV Bus a. Apply fault at the MOONLIT3 115.00 (533254) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_205 | 3 Phase fault on MORRIS 3 115.00 (533305) 115 kV Bus a. Apply fault at the MORRIS 3 115.00 (533305) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_206 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_207 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_208 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_209 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_210 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.2. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_211 | 3 Phase fault on UNIONRG3 115.00 (533359) 115 kV Bus a. Apply fault at the UNIONRG3 115.00 (533359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG3 (533359) 115.0 kV to TCHOPE 3 (533360) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_212 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_213 | 3 Phase fault on 29TH 4 138.00 (533024) 138 kV Bus a. Apply fault at the 29TH 4 138.00 (533024) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_214 | 3 Phase fault on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_215 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_216 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_217 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_218 | 3 Phase fault on BELAIRE4 138.00 (532988) 138 kV Bus a. Apply fault at the BELAIRE4 138.00 (532988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_219 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_220 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_221 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_222 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_223 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_224 | 3 Phase fault on TALLGRS4 138.00 (532993) 138 kV Bus a. Apply fault at the TALLGRS4 138.00 (532993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_225 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_226 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_227 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_228 | 3 Phase fault on MIDLTNT4 138.00 (514804) 138 kV Bus a. Apply fault at the MIDLTNT4 138.00 (514804) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_229 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to SLATECRK4 (533070) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_230 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_231 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_232 | 3 Phase fault on COFFEYT4 138.00 (510422) 138 kV Bus a. Apply fault at the COFFEYT4 138.00 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.6. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_233 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_234 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_235 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_236 | 3 Phase fault on FARBER 4 138.00 (533042) 138 kV Bus a. Apply fault at the FARBER 4 138.00 (533042) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_237 | 3 Phase fault on BU11PON4 138.00 (533032) 138 kV Bus a. Apply fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_238 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_239 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.3. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_240 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_241 | 3 Phase fault on BEECHTP4 138.00 (533028) 138 kV Bus a. Apply fault at the BEECHTP4 138.00 (533028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEECH 4 (533027) 138.0 kV to BEECHTP4 (533028) 138.0 kV Transmission Circuit #1 b.2. BEECHTP4 (533028) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 b.3. BEECHTP4 (533028) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_242 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_243 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_244 | 3 Phase fault on ANDOVER4 138.00 (533026) 138 kV Bus a. Apply fault at the ANDOVER4 138.00 (533026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_245 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_246 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_247 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_248 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_249 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_250 | 3 Phase fault on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_251 | 3 Phase fault on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_252 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_253 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_254 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_255 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_256 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_257 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_258 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_259 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_260 | 3 Phase fault on JEC 6 230.00 (532852) 230 kV Bus a. Apply fault at the JEC 6 230.00 (532852) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_261 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_262 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_263 | 3 Phase fault on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_264 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_265 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_266 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_267 | 3 Phase fault on NMANHT6 230.00 (532865) 230 kV Bus a. Apply fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_268 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_269 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_270 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_271 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_272 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_273 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_274 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_275 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_276 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_277 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_278 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_279 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_280 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_281 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_282 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_283 | 3 Phase fault on FR2EAST7 345.00 (532792) 345 kV Bus a. Apply fault at the FR2EAST7 345.00 (532792) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2EAST7 (532792) 345.0 kV to FR2WEST7 (532795) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_284 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_285 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_286 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_287 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_288 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_289 | 3 Phase fault on KINGMAN7 345.00 (532783) 345 kV Bus a. Apply fault at the KINGMAN7 345.00 (532783) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGMAN7 (532783) 345.0 kV to NINN1WF7 (532784) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_290 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_291 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_292 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_293 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_294 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_295 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_296 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_297 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_298 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_299 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to RA5HIPR2 (533706) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_300 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_301 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_302 | 3 Phase fault on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.3. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_303 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_304 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 b.2. SC3MILL2 (533552) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 b.3. SC3MILL2 (533552) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 b.4. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_305 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC7CRES2 (533555) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_306 | 3 Phase fault on FRONTEN2 69.000 (533775) 69 kV Bus a. Apply fault at the FRONTEN2 69.000 (533775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.2. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_307 | 3 Phase fault on WARE 2 69.000 (533652) 69 kV Bus a. Apply fault at the WARE 2 69.000 (533652) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.2. SHEFFLD2 (533774) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.3. WARE 2 (533652) 69.0 kV to SHEFFLD2 (533774) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_308 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.2. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_309 | 3 Phase fault on MULBERY2 69.000 (533767) 69 kV Bus a. Apply fault at the MULBERY2 69.000 (533767) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.2. MULBERY2 (533767) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.3. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_310 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_311 | 3 Phase fault on LITCH S2 69.000 (533766) 69 kV Bus a. Apply fault at the LITCH S2 69.000 (533766) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_312 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_313 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_314 | 3 Phase fault on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_315 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_316 | 3 Phase fault on HUDSON-2 69.000 (533763) 69 kV Bus a. Apply fault at the HUDSON-2 69.000 (533763) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON-2 (533763) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_317 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_318 | 3 Phase fault on STROTHR2 69.000 (533556) 69 kV Bus a. Apply fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_319 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_320 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_321 | 3 Phase fault on CC2SHAR2 69.000 (533629) 69 kV Bus a. Apply fault at the CC2SHAR2 69.000 (533629) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CC2SHAR2 (533629) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_322 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 b.3. EMANHAT6 (532861) 230.0 kV to EMANHAT3 (533326) 115.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_323 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.2. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.3. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_324 | 3 Phase fault on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.3. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.4. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_325 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.4. MONTGOM1 (533091) 13.2 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_326 | 3 Phase fault on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_327 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_328 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_329 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_330 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_331 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAUGHN 3 (533308) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_332 | 3 Phase fault on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_333 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_334 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_335 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_336 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_337 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_338 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_339 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_340 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_341 | 3 Phase fault on PARSONS2 69.000 (533704) 69 kV Bus a. Apply fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_342 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_343 | 3 Phase fault on UDALL 2 69.000 (533559) 69 kV Bus a. Apply fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UDALL 2 (533559) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_344 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_345 | 3 Phase fault on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_346 | 3 Phase fault on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_347 | 3 Phase fault on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.4. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.5. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_348 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_349 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.3. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_350 | 3 Phase fault on SKIATOK4 138.00 (509884) 138 kV Bus a. Apply fault at the SKIATOK4 138.00 (509884) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKIATOK4 (509884) 138.0 kV to BARNSAL4 (510388) 138.0 kV Transmission Circuit #1 b.2. T.NO.--4 (509817) 138.0 kV to SKIATOK4 (509884) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_351 | 3 Phase fault on MAYO--S4 138.00 (509780) 138 kV Bus a. Apply fault at the MAYO--S4 138.00 (509780) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--S4 (509780) 138.0 kV to BANNTAP4 (509785) 138.0 kV Transmission Circuit #1 b.2. BANNTAP4 (509785) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 b.3. MINGO-S4 (509761) 138.0 kV to T.S.E.-4 (509811) 138.0 kV Transmission Circuit #1 b.4. MINGO-S4 (509761) 138.0 kV to MAYO--S4 (509780) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_352 | 3 Phase fault on LLANETP4 138.00 (509804) 138 kV Bus a. Apply fault at the LLANETP4 138.00 (509804) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 b.2. CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 b.3. BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 b.4. LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 b.5. LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit #1 b.6. DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit #1 b.7. DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_353 | 3 Phase fault on ALWUETP4 138.00 (510429) 138 kV Bus a. Apply fault at the ALWUETP4 138.00 (510429) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 b.2. N.E.S.-4 (510396) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.3. CHELSA4 (510410) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.4. CHELSA4 (510410) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_354 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_355 | 3 Phase fault on GROVE 5 161.00 (510411) 161 kV Bus a. Apply fault at the GROVE 5 161.00 (510411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 5 (510411) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_356 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_357 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_358 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_359 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_360 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_361 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_362 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_363 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_364 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_365 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_366 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_367 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_368 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_369 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_370 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_371 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_372 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_373 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_374 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_375 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_376 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_377 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_378 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_379 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_380 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_381 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 (510418) 69.0 kV to VINTAJC4 (510417) 138.0 kV to VINJT1-1 (510367) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_382 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_383 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_384 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_385 | 3 Phase fault on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_386 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_387 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_388 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_389 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_390 | 3 Phase fault on 5KETONVL 161.00 (300997) 161 kV Bus a. Apply fault at the 5KETONVL 161.00 (300997) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 b.2. 5KETONVL (300997) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_391 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_392 | 3 Phase fault on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_393 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_394 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_395 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_396 | 3 Phase fault on PENSA 5 161.00 (512654) 161 kV Bus a. Apply fault at the PENSA 5 161.00 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_397 | 3 Phase fault on LOCSTGVKM 5 161.00 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 161.00 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_398 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_399 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_400 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_401 | 3 Phase fault on WMAIN ST5 161.00 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 161.00 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_402 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_403 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_404 | 3 Phase fault on 2NEWPORT 69.000 (301467) 69 kV Bus a. Apply fault at the 2NEWPORT 69.000 (301467) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEWPORT (301467) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 b.2. 2MONKEY (301465) 69.0 kV to 2NEWPORT (301467) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_405 | 3 Phase fault on SAILBOA2 69.000 (510409) 69 kV Bus a. Apply fault at the SAILBOA2 69.000 (510409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAILBOA2 (510409) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_406 | 3 Phase fault on CLEORTP2 69.000 (512692) 69 kV Bus a. Apply fault at the CLEORTP2 69.000 (512692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 2 (512633) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 b.2. PENSA 2 (512628) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 b.3. 2CLEORA (301460) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_407 | 3 Phase fault on MIAMI3 2 69.000 (513024) 69 kV Bus a. Apply fault at the MIAMI3 2 69.000 (513024) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI3 2 (513024) 69.0 kV Transmission Circuit #1 b.2. MIAMI3 2 (513024) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 b.3. MIAMI4 2 (513022) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_408 | 3 Phase fault on ESH TP 2 69.000 (512680) 69 kV Bus a. Apply fault at the ESH TP 2 69.000 (512680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ESHOSP (301468) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.2. 2VINITAHQ (300983) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.3. VINITA-2 (510404) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.4. VINEOTP2 (512673) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.5. 2VIN NEO (301478) 69.0 kV to VINEOTP2 (512673) 69.0 kV Transmission Circuit #1 b.6. 2J6 (300829) 69.0 kV to VINEOTP2 (512673) 69.0 kV Transmission Circuit #1 b.7. 2J6 (300829) 69.0 kV to AFTP TP2 (512620) 69.0 kV Transmission Circuit #1 b.8. AFTP TP2 (512620) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.9. AFTONTP2 (510415) 69.0 kV to AFTN-EX2 (510428) 69.0 kV Transmission Circuit #1 b.10. AFTONTP2 (510415) 69.0 kV to A-CONT 2 (510427) 69.0 kV Transmission Circuit #1 b.11. AFTONTP2 (510415) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.12. AFTON 2 (512633) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_409 | 3 Phase fault on FAIRTAP2 69.000 (512708) 69 kV Bus a. Apply fault at the FAIRTAP2 69.000 (512708) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to FAIRNEO2 (512691) 69.0 kV Transmission Circuit #1 b.2. FAIRNEO2 (512691) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 b.3. AFTON 2 (512633) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 b.4. FAIRTAP2 (512708) 69.0 kV to FRL363 2 (547583) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_410 | 3 Phase fault on MAIDTP2 69.000 (512625) 69 kV Bus a. Apply fault at the MAIDTP2 69.000 (512625) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIDTP2 (512625) 69.0 kV to GRDA1 2 (512727) 69.0 kV Transmission Circuit #1 b.2. MAIDTP2 (512625) 69.0 kV to HUNT 2 (512671) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_411 | 3 Phase fault on MIAMI 2 69.000 (512630) 69 kV Bus a. Apply fault at the MIAMI 2 69.000 (512630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI3 2 (513024) 69.0 kV Transmission Circuit #1 b.2. MIAMI3 2 (513024) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 b.3. MIAMI4 2 (513022) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 b.4. MIAMI1 2 (513020) 69.0 kV to MIAMI4 2 (513022) 69.0 kV Transmission Circuit #1 b.5. MIAMI 2 (512630) 69.0 kV to MIAMI1 2 (513020) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_412 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_413 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_414 | 3 Phase fault on 2WLKRTP 69.000 (300760) 69 kV Bus a. Apply fault at the 2WLKRTP 69.000 (300760) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MIAETP (300852) 69.0 kV to MIAMI 2 (512630) 69.0 kV Transmission Circuit #1 b.2. 2SENECA (300830) 69.0 kV to 2MIAETP (300852) 69.0 kV Transmission Circuit #1 b.3. 2WLKRTP (300760) 69.0 kV to 2SENECA (300830) 69.0 kV Transmission Circuit #1 b.4. 2WLKRTP (300760) 69.0 kV to 2WLKRVL (300761) 69.0 kV Transmission Circuit #1 b.5. 2NEOSHO (300750) 69.0 kV to 2WLKRTP (300760) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_415 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_416 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_417 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_418 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_419 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_420 | 3 Phase fault on TONECE7 345.00 (512750) 345 kV Bus a. Apply fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_421 | 3 Phase fault on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to CLARMR 4 (512707) 138.0 kV to CLARMR4 (512813) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_422 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_423 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_424 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.4. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_425 | 3 Phase fault on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.2. LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_426 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_427 | 3 Phase fault on EAST_PLANT 6230.00 (524163) 230 kV Bus a. Apply fault at the EAST_PLANT 6230.00 (524163) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV to EPLANT_TR3 1 (524160) 13.2 kV Three Winding #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_428 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 b.4. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_429 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to XIT_INTG 3 (523220) 115.0 kV to XIT_INTG TR1 (523219) 13.2 kV Three Winding #1 b.4. XIT_INTG 6 (523221) 230.0 kV to CHAN+TASCOS6 (523869) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_430 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_431 | 3 Phase fault on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_432 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_433 | 3 Phase fault on FAIN 3115.00 (523339) 115 kV Bus a. Apply fault at the FAIN 3115.00 (523339) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK3 (523322) 115.0 kV to FAIN 3 (523339) 115.0 kV Transmission Circuit #1 b.2. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_434 | 3 Phase fault on EXELL_TP 3115.00 (523332) 115 kV Bus a. Apply fault at the EXELL_TP 3115.00 (523332) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUMAS_19ST 3 (523318) 115.0 kV to EXELL_TP 3 (523332) 115.0 kV Transmission Circuit #1 b.2. MCDWL_CREEK3 (523322) 115.0 kV to EXELL_TP 3 (523332) 115.0 kV Transmission Circuit #1 b.3. EXELL 3 (523325) 115.0 kV to EXELL_TP 3 (523332) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_435 | 3 Phase fault on Q_RYTON_TP 3115.00 (523478) 115 kV Bus a. Apply fault at the Q_RYTON_TP 3115.00 (523478) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_E 3 (523346) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_436 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_437 | 3 Phase fault on MULSHVLY_TP3115.00 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3115.00 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 (525019) 115.0 kV to BAILEYCO 3 (525028) 115.0 kV Transmission Circuit #1 b.2. MULESHVALLY3 (525018) 115.0 kV to MULSHVLY_TP3 (525019) 115.0 kV Transmission Circuit #1 b.3. MULSHVLY_TP3 (525019) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_438 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_439 | 3 Phase fault on BC-EARTH 3115.00 (525056) 115 kV Bus a. Apply fault at the BC-EARTH 3115.00 (525056) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-KELLEY +3 (525050) 115.0 kV to BC-EARTH 3 (525056) 115.0 kV Transmission Circuit #1 b.2. BC-EARTH 3 (525056) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_440 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_441 | 3 Phase fault on HART_INDUST3115.00 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3115.00 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 (525124) 115.0 kV to LAMTON 3 (525414) 115.0 kV Transmission Circuit #1 b.2. HART_INDUST3 (525124) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_442 | 3 Phase fault on OUTPOST 3115.00 (524243) 115 kV Bus a. Apply fault at the OUTPOST 3115.00 (524243) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUTPOST 3 (524243) 115.0 kV to BUSHLAND 3 (524266) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_443 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_444 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_445 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_446 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.7. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.8. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.9. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.10. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.11. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_447 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_448 | 3 Phase fault on REDCLFT4 138.00 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 138.00 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.2. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit #1 b.3. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.4. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_449 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_450 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_451 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_452 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_453 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_454 | 3 Phase fault on WWDPST 4 138.00 (515425) 138 kV Bus a. Apply fault at the WWDPST 4 138.00 (515425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_455 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to KEENAN 4 (515394) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_456 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_457 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_458 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_459 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_460 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_461 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_462 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_463 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_464 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_465 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_466 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_467 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_468 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_469 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_470 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_471 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_472 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_473 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_474 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_475 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_476 | 3 Phase fault on RDS295 5 161.00 (547473) 161 kV Bus a. Apply fault at the RDS295 5 161.00 (547473) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_477 | 3 Phase fault on BOL431 5 161.00 (547493) 161 kV Bus a. Apply fault at the BOL431 5 161.00 (547493) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_478 | 3 Phase fault on JOP391 5 161.00 (547593) 161 kV Bus a. Apply fault at the JOP391 5 161.00 (547593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.2. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_479 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_480 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_481 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_482 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_483 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_484 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_485 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_486 | 3 Phase fault on 5MCBAIN T 161.00 (345071) 161 kV Bus a. Apply fault at the 5MCBAIN T 161.00 (345071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_487 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_488 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_489 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_490 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_491 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_492 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_493 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MPLTAP (300036) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 b.3. 5MPLTAP (300036) 161.0 kV to 5LATHROP (344923) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_494 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_495 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_496 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_497 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_498 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_499 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKS (300041) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_500 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_501 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_502 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to VSC2_3 (992003) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_503 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_504 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_505 | 3 Phase fault on 5CAMDEN 161.00 (300064) 161 kV Bus a. Apply fault at the 5CAMDEN 161.00 (300064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CAMDEN (300064) 161.0 kV to 5WHISPR (301077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_506 | 3 Phase fault on 5HIGBEEB1 161.00 (300066) 161 kV Bus a. Apply fault at the 5HIGBEEB1 161.00 (300066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_507 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_508 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_509 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_510 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_511 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_512 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_513 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_514 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_515 | 3 Phase fault on 5COFFMN 161.00 (300072) 161 kV Bus a. Apply fault at the 5COFFMN 161.00 (300072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COFFMN (300072) 161.0 kV to 5HUBEN (300088) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_516 | 3 Phase fault on 5COFFMN 161.00 (300072) 161 kV Bus a. Apply fault at the 5COFFMN 161.00 (300072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COFFMN (300072) 161.0 kV to 5LEBANN (300092) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_517 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_518 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_519 | 3 Phase fault on 5HUBEN 161.00 (300088) 161 kV Bus a. Apply fault at the 5HUBEN 161.00 (300088) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 5MRSHFL (300102) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_520 | 3 Phase fault on 5HUBEN 161.00 (300088) 161 kV Bus a. Apply fault at the 5HUBEN 161.00 (300088) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 5PHLIPS (300109) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_521 | 3 Phase fault on 5HUBEN 161.00 (300088) 161 kV Bus a. Apply fault at the 5HUBEN 161.00 (300088) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 5WHISPR (301077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_522 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5BTLFD (300348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_523 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_524 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5RIVRDL (300726) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_525 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_526 | 3 Phase fault on 5MANSFDMN 161.00 (300095) 161 kV Bus a. Apply fault at the 5MANSFDMN 161.00 (300095) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MANSFDMN (300095) 161.0 kV to 5LOGAN (301161) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_527 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_528 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to 5MORGANXF2 (301622) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_529 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_530 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_531 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_532 | 3 Phase fault on 5MRSHFL 161.00 (300102) 161 kV Bus a. Apply fault at the 5MRSHFL 161.00 (300102) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MRSHFL (300102) 161.0 kV to 5HOLMAN (301159) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_533 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_534 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_535 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_536 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_537 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_538 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_539 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_540 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_541 | 3 Phase fault on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STKAEC (300118) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_542 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_543 | 3 Phase fault on 2KNOXVL 69.000 (300204) 69 kV Bus a. Apply fault at the 2KNOXVL 69.000 (300204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KNOXVL (300204) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_544 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2MOCITY (300304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_545 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2SMRSET (300311) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_546 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_547 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_548 | 3 Phase fault on 2SMITHV 69.000 (300310) 69 kV Bus a. Apply fault at the 2SMITHV 69.000 (300310) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMITHV (300310) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_549 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2MAGNOL (300328) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_550 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2ROSEHL (300334) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_551 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_552 | 3 Phase fault on 2RT Z 69.000 (300325) 69 kV Bus a. Apply fault at the 2RT Z 69.000 (300325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2RT Z (300325) 69.0 kV to 2ELM (300327) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_553 | 3 Phase fault on 2ELM 69.000 (300327) 69 kV Bus a. Apply fault at the 2ELM 69.000 (300327) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELM (300327) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_554 | 3 Phase fault on 5BTLFD 161.00 (300348) 161 kV Bus a. Apply fault at the 5BTLFD 161.00 (300348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_555 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_556 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_557 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_558 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_559 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_560 | 3 Phase fault on 2BELLAMY 69.000 (300646) 69 kV Bus a. Apply fault at the 2BELLAMY 69.000 (300646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BELLAMY (300646) 69.0 kV to 2BLLMYTP (300647) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_561 | 3 Phase fault on 2BLLMYTP 69.000 (300647) 69 kV Bus a. Apply fault at the 2BLLMYTP 69.000 (300647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLLMYTP (300647) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_562 | 3 Phase fault on 2BLLMYTP 69.000 (300647) 69 kV Bus a. Apply fault at the 2BLLMYTP 69.000 (300647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLLMYTP (300647) 69.0 kV to 2MILO (300654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_563 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_564 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2MEDOC (300653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_565 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_566 | 3 Phase fault on 2KENOMA 69.000 (300650) 69 kV Bus a. Apply fault at the 2KENOMA 69.000 (300650) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KENOMA (300650) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_567 | 3 Phase fault on 2LAMR 69.000 (300651) 69 kV Bus a. Apply fault at the 2LAMR 69.000 (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_568 | 3 Phase fault on 2LAMR 69.000 (300651) 69 kV Bus a. Apply fault at the 2LAMR 69.000 (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2LAMARPT (300685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_569 | 3 Phase fault on 2LAMRCTS 69.000 (300652) 69 kV Bus a. Apply fault at the 2LAMRCTS 69.000 (300652) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMRCTS (300652) 69.0 kV to 2LAMARPT (300685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_570 | 3 Phase fault on 2LAMRCTN 69.000 (300655) 69 kV Bus a. Apply fault at the 2LAMRCTN 69.000 (300655) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMRCTN (300655) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_571 | 3 Phase fault on 2CRANE 69.000 (300667) 69 kV Bus a. Apply fault at the 2CRANE 69.000 (300667) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CRANE (300667) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_572 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2GRNFLD (300672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_573 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_574 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2BONA (300800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_575 | 3 Phase fault on 2ELWOOD 69.000 (300669) 69 kV Bus a. Apply fault at the 2ELWOOD 69.000 (300669) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_576 | 3 Phase fault on 5NIXA-1 161.00 (300678) 161 kV Bus a. Apply fault at the 5NIXA-1 161.00 (300678) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_577 | 3 Phase fault on 2PRDYTP 69.000 (300679) 69 kV Bus a. Apply fault at the 2PRDYTP 69.000 (300679) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PRDYTP (300679) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_578 | 3 Phase fault on 2VERONA 69.000 (300680) 69 kV Bus a. Apply fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_579 | 3 Phase fault on 2AUSTIN 69.000 (300688) 69 kV Bus a. Apply fault at the 2AUSTIN 69.000 (300688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AUSTIN (300688) 69.0 kV to 2ELYNTP (300699) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_580 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_581 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_582 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_583 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_584 | 3 Phase fault on 2ELYNNE 69.000 (300698) 69 kV Bus a. Apply fault at the 2ELYNNE 69.000 (300698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELYNNE (300698) 69.0 kV to 2SHARSNV (300709) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_585 | 3 Phase fault on 2ELYNTP 69.000 (300699) 69 kV Bus a. Apply fault at the 2ELYNTP 69.000 (300699) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELYNTP (300699) 69.0 kV to 2PECULR (300705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_586 | 3 Phase fault on 2ELYNTP 69.000 (300699) 69 kV Bus a. Apply fault at the 2ELYNTP 69.000 (300699) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELYNTP (300699) 69.0 kV to 2SHARSNV (300709) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_587 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_588 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_589 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_590 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_591 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_592 | 3 Phase fault on 2NEOSAC 69.000 (300748) 69 kV Bus a. Apply fault at the 2NEOSAC 69.000 (300748) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to 2NEOSHO (300750) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_593 | 3 Phase fault on 2NEOSAC 69.000 (300748) 69 kV Bus a. Apply fault at the 2NEOSAC 69.000 (300748) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to 2SWTWT (300758) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_594 | 3 Phase fault on 2REEDS 69.000 (300751) 69 kV Bus a. Apply fault at the 2REEDS 69.000 (300751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_595 | 3 Phase fault on 2ELKTON 69.000 (300773) 69 kV Bus a. Apply fault at the 2ELKTON 69.000 (300773) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELKTON (300773) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_596 | 3 Phase fault on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2EUDORA (300774) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_597 | 3 Phase fault on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2EUDORA (300774) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_598 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_599 | 3 Phase fault on 2DAMSCUS 69.000 (300804) 69 kV Bus a. Apply fault at the 2DAMSCUS 69.000 (300804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DAMSCUS (300804) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_600 | 3 Phase fault on 2ICONTP 69.000 (300809) 69 kV Bus a. Apply fault at the 2ICONTP 69.000 (300809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ICONTP (300809) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_601 | 3 Phase fault on 2OSCEOL 69.000 (300811) 69 kV Bus a. Apply fault at the 2OSCEOL 69.000 (300811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_602 | 3 Phase fault on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_603 | 3 Phase fault on 2MIAETP 69.000 (300852) 69 kV Bus a. Apply fault at the 2MIAETP 69.000 (300852) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MIAETP (300852) 69.0 kV to MIAMI 2 (512630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_604 | 3 Phase fault on 5KETONVL 161.00 (300997) 161 kV Bus a. Apply fault at the 5KETONVL 161.00 (300997) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_605 | 3 Phase fault on 5LOGAN 161.00 (301161) 161 kV Bus a. Apply fault at the 5LOGAN 161.00 (301161) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_606 | 3 Phase fault on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_607 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_608 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_609 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_610 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_611 | 3 Phase fault on 2NEWPORT 69.000 (301467) 69 kV Bus a. Apply fault at the 2NEWPORT 69.000 (301467) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEWPORT (301467) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_612 | 3 Phase fault on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOKC (301522) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_613 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_614 | 3 Phase fault on 5REEDSP 161.00 (301521) 161 kV Bus a. Apply fault at the 5REEDSP 161.00 (301521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_615 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_616 | 3 Phase fault on 5MCBAIN T 161.00 (345071) 161 kV Bus a. Apply fault at the 5MCBAIN T 161.00 (345071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_617 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_618 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_619 | 3 Phase fault on BEAVER 5 161.00 (505480) 161 kV Bus a. Apply fault at the BEAVER 5 161.00 (505480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_620 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_621 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_622 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_623 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_624 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_625 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_626 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_627 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_628 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_629 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_630 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_631 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_632 | 3 Phase fault on NIXA 2 69.000 (505501) 69 kV Bus a. Apply fault at the NIXA 2 69.000 (505501) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_633 | 3 Phase fault on NIXA DT2 69.000 (505541) 69 kV Bus a. Apply fault at the NIXA DT2 69.000 (505541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA DT2 (505541) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_634 | 3 Phase fault on NX ESPY2 69.000 (505543) 69 kV Bus a. Apply fault at the NX ESPY2 69.000 (505543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NX ESPY2 (505543) 69.0 kV to NIX_SLR_U1_2 (505545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_635 | 3 Phase fault on BA.NO-S4 138.00 (509721) 138 kV Bus a. Apply fault at the BA.NO-S4 138.00 (509721) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.NO-S4 (509721) 138.0 kV to BA.N-ST4 (509786) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_636 | 3 Phase fault on BA101 S4 138.00 (509737) 138 kV Bus a. Apply fault at the BA101 S4 138.00 (509737) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101 S4 (509737) 138.0 kV to BA101ST4 (509768) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_637 | 3 Phase fault on DENVTAP4 138.00 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 138.00 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 (509746) 138.0 kV to T.NO.--4 (509817) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_638 | 3 Phase fault on BA81---4 138.00 (509747) 138 kV Bus a. Apply fault at the BA81---4 138.00 (509747) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA81---4 (509747) 138.0 kV to BA101-N4 (509769) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_639 | 3 Phase fault on B111---4 138.00 (509767) 138 kV Bus a. Apply fault at the B111---4 138.00 (509767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 (509767) 138.0 kV to BA101ST4 (509768) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_640 | 3 Phase fault on BA101ST4 138.00 (509768) 138 kV Bus a. Apply fault at the BA101ST4 138.00 (509768) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 (509768) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_641 | 3 Phase fault on BA101-N4 138.00 (509769) 138 kV Bus a. Apply fault at the BA101-N4 138.00 (509769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 (509769) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_642 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to G16133G16146 (588039) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_643 | 3 Phase fault on BANNTAP4 138.00 (509785) 138 kV Bus a. Apply fault at the BANNTAP4 138.00 (509785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANNTAP4 (509785) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_644 | 3 Phase fault on BA.N-ST4 138.00 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 138.00 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_645 | 3 Phase fault on BA.N-ST4 138.00 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 138.00 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_646 | 3 Phase fault on ONETA--4 138.00 (509806) 138 kV Bus a. Apply fault at the ONETA--4 138.00 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to 121LYNN4 (509869) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_647 | 3 Phase fault on ONETA--4 138.00 (509806) 138 kV Bus a. Apply fault at the ONETA--4 138.00 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_648 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-ET 4 (509839) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_649 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_650 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to OWASOTP4 (509844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_651 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_652 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to SKIATOK4 (509884) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_653 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to T.NO.2-4 (509895) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_654 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to 46ST-TP-4 (509900) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_655 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_656 | 3 Phase fault on 121LYNN4 138.00 (509869) 138 kV Bus a. Apply fault at the 121LYNN4 138.00 (509869) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 121LYNN4 (509869) 138.0 kV to E_121ST4 (509889) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_657 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_658 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_659 | 3 Phase fault on DELWARE4 138.00 (510379) 138 kV Bus a. Apply fault at the DELWARE4 138.00 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_660 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_661 | 3 Phase fault on NBVILLE4 138.00 (510386) 138 kV Bus a. Apply fault at the NBVILLE4 138.00 (510386) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_662 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_663 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_664 | 3 Phase fault on COFFEYT4 138.00 (510422) 138 kV Bus a. Apply fault at the COFFEYT4 138.00 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_665 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_666 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_667 | 3 Phase fault on MAIDTP2 69.000 (512625) 69 kV Bus a. Apply fault at the MAIDTP2 69.000 (512625) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIDTP2 (512625) 69.0 kV to GRDA1 2 (512727) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_668 | 3 Phase fault on MIAMI 2 69.000 (512630) 69 kV Bus a. Apply fault at the MIAMI 2 69.000 (512630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to FAIRNEO2 (512691) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_669 | 3 Phase fault on MIAMI 2 69.000 (512630) 69 kV Bus a. Apply fault at the MIAMI 2 69.000 (512630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI1 2 (513020) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_670 | 3 Phase fault on MIAMI 2 69.000 (512630) 69 kV Bus a. Apply fault at the MIAMI 2 69.000 (512630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI3 2 (513024) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_671 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_672 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_673 | 3 Phase fault on AFTON 2 69.000 (512633) 69 kV Bus a. Apply fault at the AFTON 2 69.000 (512633) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 2 (512633) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_674 | 3 Phase fault on AFTON 2 69.000 (512633) 69 kV Bus a. Apply fault at the AFTON 2 69.000 (512633) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 2 (512633) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_675 | 3 Phase fault on AFTON 2 69.000 (512633) 69 kV Bus a. Apply fault at the AFTON 2 69.000 (512633) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 2 (512633) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_676 | 3 Phase fault on OKAYGR 5 161.00 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 161.00 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_677 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_678 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_679 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_680 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_681 | 3 Phase fault on IODINE-4 138.00 (514796) 138 kV Bus a. Apply fault at the IODINE-4 138.00 (514796) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_682 | 3 Phase fault on IODINE-4 138.00 (514796) 138 kV Bus a. Apply fault at the IODINE-4 138.00 (514796) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_683 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_684 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_685 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_686 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_687 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_688 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_689 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071_TAP (763069) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_690 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_691 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_692 | 3 Phase fault on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_693 | 3 Phase fault on 25MILE 7 345.00 (516146) 345 kV Bus a. Apply fault at the 25MILE 7 345.00 (516146) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 25MILE 7 (516146) 345.0 kV to 25MILZ 7 (516159) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_694 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_695 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_696 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 7 (523101) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_697 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOVUS1 7 (523112) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_698 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_699 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_700 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_701 | 3 Phase fault on NOBLE_WND 3115.00 (523103) 115 kV Bus a. Apply fault at the NOBLE_WND 3115.00 (523103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_702 | 3 Phase fault on BUFF_DUNES 7345.00 (523118) 345 kV Bus a. Apply fault at the BUFF_DUNES 7345.00 (523118) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFF_DUNES 7 (523118) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_703 | 3 Phase fault on GRPLNS-HV4-3115.00 (523130) 115 kV Bus a. Apply fault at the GRPLNS-HV4-3115.00 (523130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_704 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to CHAN+TASCOS6 (523869) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_705 | 3 Phase fault on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_706 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_707 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_708 | 3 Phase fault on MCDWL_CREEK3115.00 (523322) 115 kV Bus a. Apply fault at the MCDWL_CREEK3115.00 (523322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK3 (523322) 115.0 kV to EXELL_TP 3 (523332) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_709 | 3 Phase fault on MCDWL_CREEK3115.00 (523322) 115 kV Bus a. Apply fault at the MCDWL_CREEK3115.00 (523322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK3 (523322) 115.0 kV to FAIN 3 (523339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_710 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_711 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_712 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_713 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_714 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_715 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_716 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_717 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_718 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_719 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_720 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_721 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_722 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_723 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_724 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_725 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_726 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_727 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_728 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_729 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV to DEAFSMITH 6 (524623) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_730 | 3 Phase fault on SPNSPUR_WND7345.00 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7345.00 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_731 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_732 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_733 | 3 Phase fault on DEAFSMITH 6230.00 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6230.00 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 (524623) 230.0 kV to G17-146-TAP (760498) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_734 | 3 Phase fault on CASTRO_CNTY3115.00 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3115.00 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 (524746) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_735 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_736 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_737 | 3 Phase fault on MULSHVLY_TP3115.00 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3115.00 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 (525019) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_738 | 3 Phase fault on BC-EARTH 3115.00 (525056) 115 kV Bus a. Apply fault at the BC-EARTH 3115.00 (525056) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-EARTH 3 (525056) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_739 | 3 Phase fault on HART_INDUST3115.00 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3115.00 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 (525124) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_740 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_741 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_742 | 3 Phase fault on RKYFORD_TP 3115.00 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3115.00 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKYFORD_TP 3 (525446) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_743 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to PLANT_X 6 (525481) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_744 | 3 Phase fault on PLANT_X 3115.00 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3115.00 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_745 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_746 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_747 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to SUNDOWN 6 (526435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_748 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to G17-146-TAP (760498) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_749 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_750 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_751 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_752 | 3 Phase fault on SUNDOWN 6230.00 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6230.00 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 (526435) 230.0 kV to AMOCO_SS 6 (526460) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_753 | 3 Phase fault on SUNDOWN 6230.00 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6230.00 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 (526435) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_754 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_755 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_756 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_757 | 3 Phase fault on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_758 | 3 Phase fault on HASKELL3 115.00 (531374) 115 kV Bus a. Apply fault at the HASKELL3 115.00 (531374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASKELL3 (531374) 115.0 kV to SEWARD-3 (531467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_759 | 3 Phase fault on JONES3 115.00 (531379) 115 kV Bus a. Apply fault at the JONES3 115.00 (531379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_760 | 3 Phase fault on HUGOTON2 69.000 (531380) 69 kV Bus a. Apply fault at the HUGOTON2 69.000 (531380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to CHUGTON2 (531479) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_761 | 3 Phase fault on MOSCOW 2 69.000 (531384) 69 kV Bus a. Apply fault at the MOSCOW 2 69.000 (531384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOW 2 (531384) 69.0 kV to MOSCOWT2 (531385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_762 | 3 Phase fault on MOSCOWT2 69.000 (531385) 69 kV Bus a. Apply fault at the MOSCOWT2 69.000 (531385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOWT2 (531385) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_763 | 3 Phase fault on NORTH6 2 69.000 (531388) 69 kV Bus a. Apply fault at the NORTH6 2 69.000 (531388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6 2 (531388) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_764 | 3 Phase fault on NORTH6T2 69.000 (531389) 69 kV Bus a. Apply fault at the NORTH6T2 69.000 (531389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6T2 (531389) 69.0 kV to WALKMYR2 (531404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_765 | 3 Phase fault on PIONEER3 115.00 (531391) 115 kV Bus a. Apply fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_766 | 3 Phase fault on PIONEER3 115.00 (531391) 115 kV Bus a. Apply fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_767 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_768 | 3 Phase fault on ROLLA 2 115.00 (531395) 115 kV Bus a. Apply fault at the ROLLA 2 115.00 (531395) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLA 2 (531395) 115.0 kV to ABBK 2 (531494) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_769 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WOODS 2 (531406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_770 | 3 Phase fault on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEOTI 3 (531428) 115.0 kV to SELKIRK3 (531434) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_771 | 3 Phase fault on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEOTI 3 (531428) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_772 | 3 Phase fault on PILE 3 115.00 (531432) 115 kV Bus a. Apply fault at the PILE 3 115.00 (531432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_773 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_774 | 3 Phase fault on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_775 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_776 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_777 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_778 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON3 (531481) 115.0 kV to ABBK 2 (531494) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_779 | 3 Phase fault on GRANTTP3 115.00 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 115.00 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_780 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_781 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to READWF 7 (532776) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_782 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_783 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_784 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_785 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_786 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to G20-076-TAP (765155) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_787 | 3 Phase fault on FR2EAST7 345.00 (532792) 345 kV Bus a. Apply fault at the FR2EAST7 345.00 (532792) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2EAST7 (532792) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_788 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_789 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_790 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_791 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_792 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_793 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G20-076-TAP (765155) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_794 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_795 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_796 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_797 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_798 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to LEC U5 6 (532854) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_799 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_800 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_801 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to G20-071-TAP (765140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_802 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to G20-071-TAP (765140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_803 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_804 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_805 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_806 | 3 Phase fault on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_807 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_808 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_809 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_810 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_811 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_812 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_813 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_814 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_815 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_816 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to TCBURNS4 (532994) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_817 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_818 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_819 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_820 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_821 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_822 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_823 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_824 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_825 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_826 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_827 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_828 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_829 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_830 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_831 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_832 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_833 | 3 Phase fault on EVANS S4 138.00 (533041) 138 kV Bus a. Apply fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_834 | 3 Phase fault on EVANS S4 138.00 (533041) 138 kV Bus a. Apply fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_835 | 3 Phase fault on FARBER 4 138.00 (533042) 138 kV Bus a. Apply fault at the FARBER 4 138.00 (533042) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_836 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to CROOKED3 (533155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_837 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to KEENE 3 (533167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_838 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_839 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_840 | 3 Phase fault on 41CALIF3 115.00 (533160) 115 kV Bus a. Apply fault at the 41CALIF3 115.00 (533160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_841 | 3 Phase fault on SHAWNEE3 115.00 (533176) 115 kV Bus a. Apply fault at the SHAWNEE3 115.00 (533176) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_842 | 3 Phase fault on SHAWNEE3 115.00 (533176) 115 kV Bus a. Apply fault at the SHAWNEE3 115.00 (533176) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_843 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to TEC E 3 (533203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_844 | 3 Phase fault on TECHILE3 115.00 (533182) 115 kV Bus a. Apply fault at the TECHILE3 115.00 (533182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_845 | 3 Phase fault on TECHILE3 115.00 (533182) 115 kV Bus a. Apply fault at the TECHILE3 115.00 (533182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_846 | 3 Phase fault on TONGATP3 115.00 (533219) 115 kV Bus a. Apply fault at the TONGATP3 115.00 (533219) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_847 | 3 Phase fault on TONGATP3 115.00 (533219) 115 kV Bus a. Apply fault at the TONGATP3 115.00 (533219) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_848 | 3 Phase fault on BALDCRK3 115.00 (533232) 115 kV Bus a. Apply fault at the BALDCRK3 115.00 (533232) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_849 | 3 Phase fault on BALDCRK3 115.00 (533232) 115 kV Bus a. Apply fault at the BALDCRK3 115.00 (533232) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_850 | 3 Phase fault on 166TH 3 115.00 (533233) 115 kV Bus a. Apply fault at the 166TH 3 115.00 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_851 | 3 Phase fault on BISMARK3 115.00 (533234) 115 kV Bus a. Apply fault at the BISMARK3 115.00 (533234) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_852 | 3 Phase fault on FAIRGDS3 115.00 (533236) 115 kV Bus a. Apply fault at the FAIRGDS3 115.00 (533236) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to EUDORA 3 (533240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_853 | 3 Phase fault on EUDORA 3 115.00 (533240) 115 kV Bus a. Apply fault at the EUDORA 3 115.00 (533240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_854 | 3 Phase fault on FMC 3 115.00 (533241) 115 kV Bus a. Apply fault at the FMC 3 115.00 (533241) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FMC 3 (533241) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_855 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_856 | 3 Phase fault on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_857 | 3 Phase fault on MOCKBRD3 115.00 (533253) 115 kV Bus a. Apply fault at the MOCKBRD3 115.00 (533253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_858 | 3 Phase fault on MOCKBRD3 115.00 (533253) 115 kV Bus a. Apply fault at the MOCKBRD3 115.00 (533253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_859 | 3 Phase fault on MOONLIT3 115.00 (533254) 115 kV Bus a. Apply fault at the MOONLIT3 115.00 (533254) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_860 | 3 Phase fault on FREESTATE3 115.00 (533257) 115 kV Bus a. Apply fault at the FREESTATE3 115.00 (533257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREESTATE3 (533257) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_861 | 3 Phase fault on PENTAGN3 115.00 (533261) 115 kV Bus a. Apply fault at the PENTAGN3 115.00 (533261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_862 | 3 Phase fault on SOUTHTN3 115.00 (533265) 115 kV Bus a. Apply fault at the SOUTHTN3 115.00 (533265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_863 | 3 Phase fault on STULL 3 115.00 (533269) 115 kV Bus a. Apply fault at the STULL 3 115.00 (533269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_864 | 3 Phase fault on WAVERLY3 115.00 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 115.00 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_865 | 3 Phase fault on MNTCLLO3 115.00 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 115.00 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_866 | 3 Phase fault on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_867 | 3 Phase fault on LANG 3 115.00 (533304) 115 kV Bus a. Apply fault at the LANG 3 115.00 (533304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_868 | 3 Phase fault on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_869 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_870 | 3 Phase fault on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_871 | 3 Phase fault on WMBROS 3 115.00 (533310) 115 kV Bus a. Apply fault at the WMBROS 3 115.00 (533310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_872 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_873 | 3 Phase fault on MCDOWEL3 115.00 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 115.00 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_874 | 3 Phase fault on MCDOWEL3 115.00 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 115.00 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_875 | 3 Phase fault on MCDOWEL3 115.00 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 115.00 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to STAGGHL3 (533341) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_876 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_877 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_878 | 3 Phase fault on ARKCTYE2 69.000 (533542) 69 kV Bus a. Apply fault at the ARKCTYE2 69.000 (533542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_879 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_880 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_881 | 3 Phase fault on FLORAL 2 69.000 (533545) 69 kV Bus a. Apply fault at the FLORAL 2 69.000 (533545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORAL 2 (533545) 69.0 kV to FLORALJ2 (533546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_882 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_883 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to TIMBER 2 (533557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_884 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_885 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_886 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_887 | 3 Phase fault on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_888 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_889 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_890 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_891 | 3 Phase fault on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_892 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_893 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_894 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_895 | 3 Phase fault on PRAIRIE2 69.000 (533562) 69 kV Bus a. Apply fault at the PRAIRIE2 69.000 (533562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAIRIE2 (533562) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_896 | 3 Phase fault on WEAVER 2 69.000 (533604) 69 kV Bus a. Apply fault at the WEAVER 2 69.000 (533604) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_897 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to BURLIND2 (533625) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_898 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to BURLJCT2 (533626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_899 | 3 Phase fault on BURLJCT2 69.000 (533626) 69 kV Bus a. Apply fault at the BURLJCT2 69.000 (533626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_900 | 3 Phase fault on BURLJCT2 69.000 (533626) 69 kV Bus a. Apply fault at the BURLJCT2 69.000 (533626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_901 | 3 Phase fault on CC3WEST2 69.000 (533630) 69 kV Bus a. Apply fault at the CC3WEST2 69.000 (533630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_902 | 3 Phase fault on MARMATN2 69.000 (533639) 69 kV Bus a. Apply fault at the MARMATN2 69.000 (533639) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_903 | 3 Phase fault on MARMATN2 69.000 (533639) 69 kV Bus a. Apply fault at the MARMATN2 69.000 (533639) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_904 | 3 Phase fault on MCKEE 2 69.000 (533640) 69 kV Bus a. Apply fault at the MCKEE 2 69.000 (533640) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_905 | 3 Phase fault on UN1ELSM2 69.000 (533647) 69 kV Bus a. Apply fault at the UN1ELSM2 69.000 (533647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_906 | 3 Phase fault on ALTAMNT2 69.000 (533671) 69 kV Bus a. Apply fault at the ALTAMNT2 69.000 (533671) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_907 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_908 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_909 | 3 Phase fault on LABETTE2 69.000 (533695) 69 kV Bus a. Apply fault at the LABETTE2 69.000 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_910 | 3 Phase fault on LABETTS2 69.000 (533696) 69 kV Bus a. Apply fault at the LABETTS2 69.000 (533696) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_911 | 3 Phase fault on ORDNCE 2 69.000 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 69.000 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_912 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_913 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_914 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_915 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_916 | 3 Phase fault on GIR JCT2 69.000 (533762) 69 kV Bus a. Apply fault at the GIR JCT2 69.000 (533762) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_917 | 3 Phase fault on GIR JCT2 69.000 (533762) 69 kV Bus a. Apply fault at the GIR JCT2 69.000 (533762) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_918 | 3 Phase fault on MULBERY2 69.000 (533767) 69 kV Bus a. Apply fault at the MULBERY2 69.000 (533767) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_919 | 3 Phase fault on SHEFFLD2 69.000 (533774) 69 kV Bus a. Apply fault at the SHEFFLD2 69.000 (533774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEFFLD2 (533774) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_920 | 3 Phase fault on FRONTEN2 69.000 (533775) 69 kV Bus a. Apply fault at the FRONTEN2 69.000 (533775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_921 | 3 Phase fault on ROSEHIL2 69.000 (533836) 69 kV Bus a. Apply fault at the ROSEHIL2 69.000 (533836) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL2 (533836) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_922 | 3 Phase fault on EAST SUB 2 69.000 (533990) 69 kV Bus a. Apply fault at the EAST SUB 2 69.000 (533990) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_923 | 3 Phase fault on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_924 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_925 | 3 Phase fault on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_926 | 3 Phase fault on COVERT 3 115.00 (539644) 115 kV Bus a. Apply fault at the COVERT 3 115.00 (539644) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_927 | 3 Phase fault on COVERT 3 115.00 (539644) 115 kV Bus a. Apply fault at the COVERT 3 115.00 (539644) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_928 | 3 Phase fault on KISMET 3 115.00 (539646) 115 kV Bus a. Apply fault at the KISMET 3 115.00 (539646) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_929 | 3 Phase fault on KISMET 3 115.00 (539646) 115 kV Bus a. Apply fault at the KISMET 3 115.00 (539646) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_930 | 3 Phase fault on IONIA 3 115.00 (539647) 115 kV Bus a. Apply fault at the IONIA 3 115.00 (539647) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_931 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_932 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_933 | 3 Phase fault on CIM-PLT3 115.00 (539654) 115 kV Bus a. Apply fault at the CIM-PLT3 115.00 (539654) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_934 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_935 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_936 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_937 | 3 Phase fault on GLENELD3 115.00 (539663) 115 kV Bus a. Apply fault at the GLENELD3 115.00 (539663) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_938 | 3 Phase fault on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_939 | 3 Phase fault on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_940 | 3 Phase fault on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_941 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to E-PINE 3 (539690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_942 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_943 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_944 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_945 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_946 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_947 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_948 | 3 Phase fault on WALDO 3 115.00 (539698) 115 kV Bus a. Apply fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_949 | 3 Phase fault on W-LIBER3 115.00 (539700) 115 kV Bus a. Apply fault at the W-LIBER3 115.00 (539700) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W-LIBER3 (539700) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_950 | 3 Phase fault on NLIB 3 115.00 (539737) 115 kV Bus a. Apply fault at the NLIB 3 115.00 (539737) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NLIB 3 (539737) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_951 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_952 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_953 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_954 | 3 Phase fault on CLNTPLT_CAP269.000 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP269.000 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_955 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_956 | 3 Phase fault on WBURGE_CAP5 161.00 (541148) 161 kV Bus a. Apply fault at the WBURGE_CAP5 161.00 (541148) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE_CAP5 (541148) 161.0 kV to WBURGE 5 (541228) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_957 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_958 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_959 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_960 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_961 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_962 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_963 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_964 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_965 | 3 Phase fault on PRALEE 5 161.00 (541206) 161 kV Bus a. Apply fault at the PRALEE 5 161.00 (541206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_966 | 3 Phase fault on PRALEE 5 161.00 (541206) 161 kV Bus a. Apply fault at the PRALEE 5 161.00 (541206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_967 | 3 Phase fault on PRALEE 5 161.00 (541206) 161 kV Bus a. Apply fault at the PRALEE 5 161.00 (541206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_968 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_969 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_970 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_971 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_972 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_973 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_974 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_975 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_976 | 3 Phase fault on GRNWD 5 161.00 (541218) 161 kV Bus a. Apply fault at the GRNWD 5 161.00 (541218) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_977 | 3 Phase fault on GRNWD 5 161.00 (541218) 161 kV Bus a. Apply fault at the GRNWD 5 161.00 (541218) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_978 | 3 Phase fault on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_979 | 3 Phase fault on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_980 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_981 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_982 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_983 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_984 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_985 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_986 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_987 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_988 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_989 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_990 | 3 Phase fault on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_991 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_992 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_993 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_994 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_995 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_996 | 3 Phase fault on SEDS 2 69.000 (541272) 69 kV Bus a. Apply fault at the SEDS 2 69.000 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_997 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_998 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to HSNVLN 2 (541297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_999 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1000 | 3 Phase fault on PHILL 2 69.000 (541280) 69 kV Bus a. Apply fault at the PHILL 2 69.000 (541280) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1001 | 3 Phase fault on BELTON 2 69.000 (541289) 69 kV Bus a. Apply fault at the BELTON 2 69.000 (541289) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1002 | 3 Phase fault on BELTON 2 69.000 (541289) 69 kV Bus a. Apply fault at the BELTON 2 69.000 (541289) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1003 | 3 Phase fault on BELTONS2 69.000 (541290) 69 kV Bus a. Apply fault at the BELTONS2 69.000 (541290) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1004 | 3 Phase fault on HSNVLS 2 69.000 (541294) 69 kV Bus a. Apply fault at the HSNVLS 2 69.000 (541294) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1005 | 3 Phase fault on HSNVL 2 69.000 (541295) 69 kV Bus a. Apply fault at the HSNVL 2 69.000 (541295) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVLSW2 (541296) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1006 | 3 Phase fault on HSNVLSW2 69.000 (541296) 69 kV Bus a. Apply fault at the HSNVLSW2 69.000 (541296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLSW2 (541296) 69.0 kV to HSNVLN 2 (541297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1007 | 3 Phase fault on HSNVLSW2 69.000 (541296) 69 kV Bus a. Apply fault at the HSNVLSW2 69.000 (541296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLSW2 (541296) 69.0 kV to GRDNCTY2 (541298) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1008 | 3 Phase fault on GRDNCTY2 69.000 (541298) 69 kV Bus a. Apply fault at the GRDNCTY2 69.000 (541298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY2 (541298) 69.0 kV to GUNNPS2 (541299) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1009 | 3 Phase fault on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1010 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1011 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to URICHTP2 (541304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1012 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1013 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1014 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBW5 (541336) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1015 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1016 | 3 Phase fault on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161.0 kV to WAFBE5 (541338) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1017 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1018 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1019 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1020 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1021 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1022 | 3 Phase fault on HLDENTP2 69.000 (541386) 69 kV Bus a. Apply fault at the HLDENTP2 69.000 (541386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLDENTP2 (541386) 69.0 kV to KNGSVIL 2 (541387) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1023 | 3 Phase fault on KNGSVIL 2 69.000 (541387) 69 kV Bus a. Apply fault at the KNGSVIL 2 69.000 (541387) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1024 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1025 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1026 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1027 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1028 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1029 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1030 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1031 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1032 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1033 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BULLCRK5 (543105) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1034 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1035 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1036 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1037 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1038 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1039 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1040 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1041 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1042 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1043 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1044 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1045 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1046 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1047 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1048 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1049 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1050 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1051 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1052 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1053 | 3 Phase fault on PFLUMM 5 161.00 (542979) 161 kV Bus a. Apply fault at the PFLUMM 5 161.00 (542979) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1054 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1055 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1056 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1057 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1058 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1059 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1060 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1061 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1062 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1063 | 3 Phase fault on LEEDS 5 161.00 (542997) 161 kV Bus a. Apply fault at the LEEDS 5 161.00 (542997) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1064 | 3 Phase fault on LEEDS 5 161.00 (542997) 161 kV Bus a. Apply fault at the LEEDS 5 161.00 (542997) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1065 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1066 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1067 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1068 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1069 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1070 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1071 | 3 Phase fault on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1072 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1073 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1074 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1075 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1076 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1077 | 3 Phase fault on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1078 | 3 Phase fault on BRKRIDG5 161.00 (543033) 161 kV Bus a. Apply fault at the BRKRIDG5 161.00 (543033) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKRIDG5 (543033) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1079 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1080 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1081 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1082 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1083 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1084 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1085 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1086 | 3 Phase fault on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LENEXA 5 (543038) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1087 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to GARDNER5 (543056) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1088 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1089 | 3 Phase fault on OXFORD 5 161.00 (543046) 161 kV Bus a. Apply fault at the OXFORD 5 161.00 (543046) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 5 (543046) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1090 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1091 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to NEASTOTTW5 (543166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1092 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1093 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1094 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1095 | 3 Phase fault on MALTABN5 161.00 (543059) 161 kV Bus a. Apply fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1096 | 3 Phase fault on MALTABN5 161.00 (543059) 161 kV Bus a. Apply fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1097 | 3 Phase fault on CAROLTN5 161.00 (543060) 161 kV Bus a. Apply fault at the CAROLTN5 161.00 (543060) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1098 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1099 | 3 Phase fault on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1100 | 3 Phase fault on NORTON 5 161.00 (543064) 161 kV Bus a. Apply fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (543064) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1101 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1102 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1103 | 3 Phase fault on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.OTTWA5 (543066) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1104 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1105 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1106 | 3 Phase fault on PAOLA 5 161.00 (543069) 161 kV Bus a. Apply fault at the PAOLA 5 161.00 (543069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLA 5 (543069) 161.0 kV to OSAWAT 5 (543112) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1107 | 3 Phase fault on S EAST 5 161.00 (543071) 161 kV Bus a. Apply fault at the S EAST 5 161.00 (543071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S EAST 5 (543071) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1108 | 3 Phase fault on MRSHLJT5 161.00 (543072) 161 kV Bus a. Apply fault at the MRSHLJT5 161.00 (543072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRSHLJT5 (543072) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1109 | 3 Phase fault on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSTVAL5 (543077) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1110 | 3 Phase fault on SWAVRLY2 69.000 (543094) 69 kV Bus a. Apply fault at the SWAVRLY2 69.000 (543094) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1111 | 3 Phase fault on MAYVWTP2 69.000 (543096) 69 kV Bus a. Apply fault at the MAYVWTP2 69.000 (543096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYVWTP2 (543096) 69.0 kV to AMOCOPL2 (543100) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1112 | 3 Phase fault on CORDER 2 69.000 (543097) 69 kV Bus a. Apply fault at the CORDER 2 69.000 (543097) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORDER 2 (543097) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1113 | 3 Phase fault on CTY HIG2 69.000 (543098) 69 kV Bus a. Apply fault at the CTY HIG2 69.000 (543098) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTY HIG2 (543098) 69.0 kV to HIGNSVL2 (543099) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1114 | 3 Phase fault on CTY HIG2 69.000 (543098) 69 kV Bus a. Apply fault at the CTY HIG2 69.000 (543098) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTY HIG2 (543098) 69.0 kV to HGNSCTYW2 (543144) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1115 | 3 Phase fault on CTY HIG2 69.000 (543098) 69 kV Bus a. Apply fault at the CTY HIG2 69.000 (543098) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTY HIG2 (543098) 69.0 kV to HGNSCTYPLNT2 (543146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1117 | 3 Phase fault on HIGNSVL2 69.000 (543099) 69 kV Bus a. Apply fault at the HIGNSVL2 69.000 (543099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGNSVL2 (543099) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1118 | 3 Phase fault on AMOCOPL2 69.000 (543100) 69 kV Bus a. Apply fault at the AMOCOPL2 69.000 (543100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOPL2 (543100) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1119 | 3 Phase fault on DOVER2 69.000 (543101) 69 kV Bus a. Apply fault at the DOVER2 69.000 (543101) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER2 (543101) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1120 | 3 Phase fault on OSAWAT 5 161.00 (543112) 161 kV Bus a. Apply fault at the OSAWAT 5 161.00 (543112) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWAT 5 (543112) 161.0 kV to OSAWTM_CAP5 (543135) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1121 | 3 Phase fault on DAKOTA_5 161.00 (543650) 161 kV Bus a. Apply fault at the DAKOTA_5 161.00 (543650) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAKOTA_5 (543650) 161.0 kV to PRQN_WIND5 (543651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1122 | 3 Phase fault on CORDERTP2 69.000 (543657) 69 kV Bus a. Apply fault at the CORDERTP2 69.000 (543657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORDERTP2 (543657) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1123 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON416J2 (547402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1124 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1125 | 3 Phase fault on MON376 2 69.000 (547401) 69 kV Bus a. Apply fault at the MON376 2 69.000 (547401) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376 2 (547401) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1126 | 3 Phase fault on MON416J2 69.000 (547402) 69 kV Bus a. Apply fault at the MON416J2 69.000 (547402) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON416J2 (547402) 69.0 kV to MON416 2 (547403) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1127 | 3 Phase fault on MON416J2 69.000 (547402) 69 kV Bus a. Apply fault at the MON416J2 69.000 (547402) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON416J2 (547402) 69.0 kV to PUR390 2 (547404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1128 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON352 2 (547406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1129 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1130 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1131 | 3 Phase fault on MON311J2 69.000 (547407) 69 kV Bus a. Apply fault at the MON311J2 69.000 (547407) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON311J2 (547407) 69.0 kV to MON311 2 (547408) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1132 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1133 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1134 | 3 Phase fault on SEN375 2 69.000 (547426) 69 kV Bus a. Apply fault at the SEN375 2 69.000 (547426) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEN375 2 (547426) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1135 | 3 Phase fault on WEB105 2 69.000 (547431) 69 kV Bus a. Apply fault at the WEB105 2 69.000 (547431) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB105 2 (547431) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1136 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to EXP4492 (547439) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1137 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1138 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1139 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1140 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1141 | 3 Phase fault on JAS344T2 69.000 (547450) 69 kV Bus a. Apply fault at the JAS344T2 69.000 (547450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAS344T2 (547450) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1142 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1143 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1144 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1145 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1146 | 3 Phase fault on KOD471 2 69.000 (547463) 69 kV Bus a. Apply fault at the KOD471 2 69.000 (547463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOD471 2 (547463) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1147 | 3 Phase fault on ATL109 5 161.00 (547466) 161 kV Bus a. Apply fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1148 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1149 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1150 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1151 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1152 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1153 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1154 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1155 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1156 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1157 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1158 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1159 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1160 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1161 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1162 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1163 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1164 | 3 Phase fault on RDS295 5 161.00 (547473) 161 kV Bus a. Apply fault at the RDS295 5 161.00 (547473) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1165 | 3 Phase fault on ASB349 5 161.00 (547476) 161 kV Bus a. Apply fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1166 | 3 Phase fault on ASB349 5 161.00 (547476) 161 kV Bus a. Apply fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1167 | 3 Phase fault on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1168 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1169 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1170 | 3 Phase fault on LAR382 5 161.00 (547479) 161 kV Bus a. Apply fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1171 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1172 | 3 Phase fault on DEC392 5 161.00 (547484) 161 kV Bus a. Apply fault at the DEC392 5 161.00 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 (547484) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1173 | 3 Phase fault on CAR395 5 161.00 (547485) 161 kV Bus a. Apply fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1174 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1175 | 3 Phase fault on RNM393 5 161.00 (547500) 161 kV Bus a. Apply fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1176 | 3 Phase fault on RIV453 5 161.00 (547501) 161 kV Bus a. Apply fault at the RIV453 5 161.00 (547501) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1177 | 3 Phase fault on RIV167 5 161.00 (547502) 161 kV Bus a. Apply fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1178 | 3 Phase fault on NEO 56 2 69.000 (547524) 69 kV Bus a. Apply fault at the NEO 56 2 69.000 (547524) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO 56 2 (547524) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1179 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1180 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1181 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1182 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1183 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1184 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1185 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1186 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1187 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1188 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1189 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1190 | 3 Phase fault on CAR108 2 69.000 (547532) 69 kV Bus a. Apply fault at the CAR108 2 69.000 (547532) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAR108 2 (547532) 69.0 kV to ATL109 2 (547533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1191 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1192 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to JOP360 2 (547581) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1193 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1194 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1195 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1196 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MON152 2 (547540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1197 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1198 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1199 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1200 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1201 | 3 Phase fault on MON152 2 69.000 (547540) 69 kV Bus a. Apply fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1202 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1203 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1204 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to ROC296 2 (547560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1205 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to LIN314 2 (547563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1206 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to AND322 2 (547566) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1207 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1208 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1209 | 3 Phase fault on GAL278 2 69.000 (547555) 69 kV Bus a. Apply fault at the GAL278 2 69.000 (547555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAL278 2 (547555) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1210 | 3 Phase fault on TIP292 2 69.000 (547559) 69 kV Bus a. Apply fault at the TIP292 2 69.000 (547559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 2 (547559) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1211 | 3 Phase fault on JOP360 2 69.000 (547581) 69 kV Bus a. Apply fault at the JOP360 2 69.000 (547581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP360 2 (547581) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1212 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1213 | 3 Phase fault on JOP389 2 69.000 (547592) 69 kV Bus a. Apply fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1214 | 3 Phase fault on JOP391 5 161.00 (547593) 161 kV Bus a. Apply fault at the JOP391 5 161.00 (547593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1215 | 3 Phase fault on RNM393 2 69.000 (547595) 69 kV Bus a. Apply fault at the RNM393 2 69.000 (547595) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 2 (547595) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1216 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1217 | 3 Phase fault on COX 269.000 (549910) 69 kV Bus a. Apply fault at the COX 269.000 (549910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1218 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to LAUREL 2 (549924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1219 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1220 | 3 Phase fault on DAYTON 269.000 (549913) 69 kV Bus a. Apply fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 2 (549913) 69.0 kV to FORT 2 (549914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1221 | 3 Phase fault on DAYTON 269.000 (549913) 69 kV Bus a. Apply fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1222 | 3 Phase fault on CHAD 269.000 (549919) 69 kV Bus a. Apply fault at the CHAD 269.000 (549919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAD 2 (549919) 69.0 kV to HARGISS 2 (549920) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1223 | 3 Phase fault on HARGISS 269.000 (549920) 69 kV Bus a. Apply fault at the HARGISS 269.000 (549920) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARGISS 2 (549920) 69.0 kV to MAIN STREET2 (549921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1224 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to GRAND 2 (549922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1225 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1226 | 3 Phase fault on GRAND 269.000 (549922) 69 kV Bus a. Apply fault at the GRAND 269.000 (549922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 2 (549922) 69.0 kV to MONROE 2 (549923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1227 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1228 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1229 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1230 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1231 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1232 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1233 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1234 | 3 Phase fault on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1235 | 3 Phase fault on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1236 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1237 | 3 Phase fault on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1238 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1239 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1240 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1241 | 3 Phase fault on MENTOR 5161.00 (549963) 161 kV Bus a. Apply fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1242 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G18-030-TAP (762662) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1243 | 3 Phase fault on LAMAR 6 345.00 (599951) 345 kV Bus a. Apply fault at the LAMAR 6 345.00 (599951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR 6 (599951) 345.0 kV to PNM-DC7 (599956) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1244 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 7HUBEN (300042) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1245 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1246 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLARK (300802) 69.0 kV to 5CLARK (300070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1247 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1248 | 3 Phase fault on 5COFFMN 161.00 (300072) 161 kV Bus a. Apply fault at the 5COFFMN 161.00 (300072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2COFFMN (301048) 69.0 kV to 5COFFMN (300072) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1249 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1250 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1251 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHRP (300302) 69.0 kV to 5LATHRP (300091) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1252 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MORGAN (300782) 69.0 kV to 5MORGAN (300101) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1253 | 3 Phase fault on 5MRSHFL 161.00 (300102) 161 kV Bus a. Apply fault at the 5MRSHFL 161.00 (300102) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MRSHFL (301163) 69.0 kV to 5MRSHFL (300102) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1254 | 3 Phase fault on 5MRSHFL 161.00 (300102) 161 kV Bus a. Apply fault at the 5MRSHFL 161.00 (300102) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MRSHFL (301163) 69.0 kV to 5MRSHFL (300102) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1255 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NORTON (300540) 69.0 kV to 5NORTON (300105) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1256 | 3 Phase fault on 5PHLIPS 161.00 (300109) 161 kV Bus a. Apply fault at the 5PHLIPS 161.00 (300109) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PBURG (301071) 69.0 kV to 5PHLIPS (300109) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1257 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1258 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1259 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HOLDEN (300336) 69.0 kV to 5HOLDENB2 (300124) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1260 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1261 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1262 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SHARSNV (300709) 69.0 kV to 5SHARSNV (301515) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1263 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1264 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to NEO184 5 (547471) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1265 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WASHBRN (300763) 69.0 kV to WASHBURN5 (505485) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1266 | 3 Phase fault on 5OSCEOL 161.00 (301040) 161 kV Bus a. Apply fault at the 5OSCEOL 161.00 (301040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 5OSCEOL (301040) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1267 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1268 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1269 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1270 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1271 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1272 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1273 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1274 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1275 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1276 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1277 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1278 | 3 Phase fault on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR1 (512814) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1279 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1280 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1281 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1282 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1283 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1284 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1285 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1286 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1287 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1288 | 3 Phase fault on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1289 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to G06-44 (560577) 115.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1290 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1291 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to XIT_INTG 3 (523220) 115.0 kV to XIT_INTG TR1 (523219) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1292 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1293 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1294 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to MCDWL_CREEK3 (523322) 115.0 kV to MCDWL_CRKTR1 (523321) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1295 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1296 | 3 Phase fault on ROLLHILLS 6230.00 (524010) 230 kV Bus a. Apply fault at the ROLLHILLS 6230.00 (524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 6 (524010) 230.0 kV to ROLLHILLS 3 (524007) 115.0 kV to ROLHILLS_TR1 (524008) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1297 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1298 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV to BUSHLAND 3 (524266) 115.0 kV to BSHLND_TR1 1 (524263) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1299 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to RANDALL 3 (524364) 115.0 kV to RANDAL_TR1 1 (524361) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1300 | 3 Phase fault on DEAFSMITH 6230.00 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6230.00 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 (524623) 230.0 kV to DFSMTH_WST 3 (524622) 115.0 kV to DEFSMTH_TR11 (524620) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1301 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV to SWISHER_TR11 (525211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1302 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR11 (525459) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1303 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to PLANT_X 3 (525480) 115.0 kV to PLANTX_TR1 1 (525479) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1304 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1305 | 3 Phase fault on SUNDOWN 6230.00 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6230.00 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 (526435) 230.0 kV to SUNDOWN 3 (526434) 115.0 kV to SUNDOWN_TR11 (526432) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1306 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to HUGOTON3 (531481) 115.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1307 | 3 Phase fault on PIONEER3 115.00 (531391) 115 kV Bus a. Apply fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER2 (531390) 69.0 kV to PIONEER3 (531391) 115.0 kV to PIONEER1 (531251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1308 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1309 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1310 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1311 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1312 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1313 | 3 Phase fault on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMSSWRD2 (531466) 69.0 kV to SEWARD-3 (531467) 115.0 kV to SEWARD 1 (531260) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1314 | 3 Phase fault on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1315 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1316 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1317 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1318 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1319 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1320 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1321 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1322 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1323 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1324 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1325 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1326 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1327 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1328 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1329 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1330 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1331 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1332 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1333 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1334 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1335 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1336 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1337 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1338 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1339 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1340 | 3 Phase fault on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1341 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1342 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT6 (532861) 230.0 kV to EMANHAT3 (533326) 115.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1343 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MCDOWEL3 (533335) 115.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1344 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1345 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1346 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1347 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1348 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1349 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1350 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1351 | 3 Phase fault on TECHILL5 161.00 (532920) 161 kV Bus a. Apply fault at the TECHILL5 161.00 (532920) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1352 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1353 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1354 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1355 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1356 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1357 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1358 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1359 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1360 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to COLINE 2 (533456) 69.0 kV to COLINE 1 (533443) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1361 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1362 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1363 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1364 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1365 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1366 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1367 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1368 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1369 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1370 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1371 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN2 (533876) 69.0 kV to FRANKLIN5 (532938) 161.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1372 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1373 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1374 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1375 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1376 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1377 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1378 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1379 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1380 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to LNGVW 5 (541224) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1381 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1382 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 2 (541269) 69.0 kV to WBURGE 5 (541228) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1383 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1384 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1385 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to LBRTYST5 (541248) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1386 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to BELTONS5 (541340) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1387 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1388 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1389 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1390 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1391 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1392 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1393 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1394 | 3 Phase fault on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to SWAVRLY5 (543063) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1395 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1396 | 3 Phase fault on ATL109 5 161.00 (547466) 161 kV Bus a. Apply fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1397 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1398 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1399 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1400 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1401 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 (547471) 161.0 kV to NEO184 2 (547543) 69.0 kV to NEO184B1 (547709) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1402 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1403 | 3 Phase fault on MON383 5 161.00 (547480) 161 kV Bus a. Apply fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1404 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1405 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1406 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1407 | 3 Phase fault on NOL435 5 161.00 (547496) 161 kV Bus a. Apply fault at the NOL435 5 161.00 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 5 (547496) 161.0 kV to NOL435 2 (547610) 69.0 kV to NOL435 1 (547720) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1408 | 3 Phase fault on CPK446 5 161.00 (547499) 161 kV Bus a. Apply fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1409 | 3 Phase fault on RNM393 5 161.00 (547500) 161 kV Bus a. Apply fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1410 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1411 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1412 | 3 Phase fault on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1413 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1414 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1415 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1416 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1417 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1418 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1419 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1420 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Local_Fault_1421 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_001 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_002 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_003 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_004 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_005 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_006 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_007 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_008 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_009 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_010 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_011 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes