## Executive Summary
Executive Summary: Group 16 Interim Availability Interconnection System Impact Study
Interconnection Customer (GEN-2020-014) has requested a Limited Operation or Interim Availability Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions (Scenarios Tab) at the time of service to determine the amount of Interconnection Capacity available to the interconnection customers listed under specific system conditions.
Once a GIA amendment to incorporate Interim GIA is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Interim Operation in accordance with the SPP study results.
Interim
In accordance with Section 11A of the GIP, Interim GIA, Interconnection Customers with a pending Interconnection Request that has an anticipated In-Service Date prior to the expected completion of the DISIS may request a study to evaluate the feasibility of Interim Interconnection Service.
Interim Interconnection Capacity conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Study Limitations
In the event that an Interconnection Request, with queue priority equal to or higher than a Interconnection Request, which was excluded as a study variation (scenario) achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study variation (scenario) is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 1.2
http://opsportal.spp.org/documents/studies/DISIS%20Manual%201.2.pdf
Note: This report and study includes some variations from the DISIS Manual:
- Requests Tab; does not include the preliminary Limited Operation calculation.
- Scenarios Tab; added to detail the Network Upgrades and Interconnection Requests excluded for the various evaluations of system conditions and identification of the available Interim Interconnection Service determined for each evaluated scenario.
- Assigned Upgrade Costs Tab; removed as Network Upgrades are not assigned in Limited Operation or Interim studies
- Upgrades Summary Tab; removed as Network Upgrades are not assigned in Limited Operation or Interim studies
- Sensitivity Dispatch Tab; added to identify dispatch variations from DISIS manual
- Stability Analysis Tab; added to include Stability analysis events and results
- Short Circuit Analysis Tab; added to include Short Circuit analysis results for year 10 summer peak case only
Models Used in Study
Power Flow Analysis: 2019 ITP Series
Light: 2024 (24L)
Summer: 2020 (20SP), 2024 (24SP), 2029 (29SP)
Spring: 2020 (20G)
Winter: 2019 (19WP), 2024 (24WP)
Stability analysis: 2018 Series MDWG Dynamics
Light: 2021 (21L)
Summer: 2021 (21SP), 2028 (28SP)
Winter: 2019 (19WP)
Short Circuit Analysis: 2018 Series MDWG Dynamics
Summer: 2028 (28SP)
Author: 1898 & Co.
Published: 09/09/2021

## Revision History
Revision History
Date | Author | Change Description
2021-09-22 | 1898&Co. | Initial Posting

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | Service | Area | POI | Status | Reactive Compensation Requirements
ASGI-2010-006 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 150 | ER | AECI | Remington 138kV
ASGI-2010-010 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 46.5 | ER | SPS | Lovington 115kV
ASGI-2010-020 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 30 | ER | SPS | Tap LE-Tatum - LE-Crossroads 69kV
ASGI-2010-021 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 15 | ER | SPS | Tap LE-Saunders Tap - LE-Anderson 69kV
ASGI-2011-001 | 06 - South Texas Panhandle/New Mexico | 5 | DIS-10-2 | Wind | 27.3 | ER | SPS | Lovington 115kV
ASGI-2011-002 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 20 | ER | SPS | Herring 115kV
ASGI-2011-003 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 10 | ER | SPS | Hendricks 69kV
ASGI-2011-004 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Wind | 19.8 | ER | SPS | Pleasant Hill 69kV
ASGI-2012-002 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 18.15 | ER | SPS | FE-Clovis Interchange 115kV
ASGI-2012-006 | 03 - Spearville | 8 | DIS-12-1 | Steam | 22.5 | ER | SUNC | ABBK 2 69kV
ASGI-2012-008 | 13 - Northeast Kansas/Northwest Missouri | 8 | PQ | Gas | 3.55 | ER | WERE | Sheffield 69kV
ASGI-2013-001 | 02 - Hitchland | 10 | DIS-13-1 | Wind | 11.5 | ER | SPS | PanTex South 115kV
ASGI-2013-002 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | Wind | 18.4 | ER | SPS | Clovis Intg. 115kV
ASGI-2013-004 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 36.6 | ER | SUNC | Garden City 115kV
ASGI-2013-005 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Wind | 1.65 | ER | SPS | Clovis Intg. 115kV
ASGI-2014-014 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Thermal | 56.4 | ER | GRDA | Ferguson 69kV
ASGI-2015-001 | 03 - Spearville | 14 | DIS-15-1 | Thermal | 6.13 | ER | SUNC | Ninnescah 115kV
ASGI-2015-002 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 2 | ER | SPS | SP-Yuma 69kV
ASGI-2015-004 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Thermal | 54 | ER | GRDA | Coffeyville City 69kV
ASGI-2016-003 | 13 - Northeast Kansas/Northwest Missouri | 16 | DIS-16-1 | Diesel | 12 | ER | KCPL | Paola 161kV
ASGI-2016-004 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | Wind | 10 | ER | SPS | Palo Duro 115kV
ASGI-2016-005NWE205 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER | WAPA | Kimball 69kV
ASGI-2016-010 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 90 | ER | SPS | Powell Corner 115kV
ASGI-2016-011 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 7.4 | ER | SWPA | Allen 138kV
ASGI-2016-012 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 61.73 | ER | SWPA | Tupelo 138kV
ASGI-2016-013 | 14 - South Central Oklahoma | 16.5 | DIS-16-2-PQ | Thermal | 4.92 | ER | WFEC | Ashland 138kV
ASGI-2017-006GIA-53 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | Dis-16-2-PQ | Wind | 242 | ER/NR | AECI | Maryville 161kV
ASGI-2018-001GIA-61 | 13 - Northeast Kansas/Northwest Missouri | 17.5 | DIS-17-1-PQ | Wind | 242 | ER/NR | AECI | Maryville 161kV
BEPCAyrshire | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 21 | ER | BEPC-SPP | Ayershire 69kV
BEPCGerled | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 | ER | BEPC-SPP | Gerled Tap 69kV
BEPCHummel | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 10.5 | ER | BEPC-SPP | Hummel 69kV
BEPCNDPW0 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 7.5 | ER | BEPC-SPP | SW Minot 115kV
BEPCNDPW1 | 16 - Western North Dakota | 17.5 | DIS-17-1-PQ | Wind | 5 | ER | BEPC-SPP | ND Prairie Wind 115kV
Coyote | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 452 | ER | OTP | Coyote 345kV
G034 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Biomass | 55 | ER/NR | XEL
G132 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 90 | ER/NR | MDU | Ellendale Sub 230kV
G237 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Gas | 579.04 | ER | XEL | Highbridge
G255 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 100 | ER/NR | XEL | Yankee
G261 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Combined Cycle | 677.1 | ER | XEL
G287 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | Nobles County
G349 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 | ER | XEL | Brookings County
G359R | 18 - Eastern North Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 | ER/NR | MDU | Merricourt
G362 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 200 | ER/NR | GRE | Pleasant Valley
G370 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 205 | ER | XEL | Anson 4
G380 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 | ER | OTP | Rugby 115kV
G389 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Gas | 200 | ER/NR | GRE | Elk River 230kV
G514 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 | ER | XEL | Lakefield Station via Trimont G263 Interconnect
G540 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 | ER/NR | ALTW | Adams - Lime Creek 161kV
G548 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 80 | ER/NR | ALTW | Barton 161kV
G586 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 30 | ER/NR | XEL | Xcel New Yankee Sub 34.5kV
G595 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 150 | ER | ALTW | Lime Creek 161kV
G602 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 32 | ER/NR | XEL | Nobles County 115kV
G604 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 44 | ER/NR | ALTW | Owatonna - County Line 69kV
G612 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 150 | ER | ALTW | ITC Midwest Fernald 115kV
G619 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 50 | ER/NR | OTP | GRE Tamarac 41kV
G621 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER/NR | XEL | Golf - Wookstock 34.5kV
G645 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 50 | ER/NR | GRE
G685 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER | XEL | Lake Lillian - Atwater 69kV
G735 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | ALTW | Lime Creek
G736 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | OTP | Big Stone South 230kV
G741 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Waste Heat Recovery | 8 | ER/NR | ALTW | Near Alliant 69kV line
G752 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Wind | 150 | ER/NR | MDU | Bison - Hettinger 230kV
G788 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 49 | ER/NR | GRE | Ladish 115kV
G826 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | Xcel Lakefield Generation SW - Lakefield Junction 345kV
G830 | 16 - Western North Dakota | 7.5 | DIS-15-2-PQ | Wind | 99 | ER/NR | GRE | GRE McHenry
G870 | 15 - Eastern South Dakota | 7.5 | DIS-15-2-PQ | Wind | 201 | ER/NR | ALTW | Hayward - Winnebago 161kV
G930 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 60 | ER/NR | XEL | Sherco
G930SHERCO | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Coal | 2491.5 | ER/NR | XEL
G971 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 20 | ER | XEL | 69kV line in SE 1/4 of Sec 17 in Cosmos Twp
GEN-2001-014 | 01 - Woodward | 1 | PQ | Wind | 94.5 | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 74.25 | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 180 | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-036 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 80 | ER | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 01 - Woodward | 1 | PQ | Wind | 102 | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 - Spearville | 1 | PQ | Wind | 104 | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 04 - Northwest Kansas | 1 | PQ | Wind | 100 | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 12 - Northwest Arkansas | 1 | PQ | CT | 50 | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 153 | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 123 | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 02 - Hitchland | 1 | PQ | Wind | 240 | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV]
GEN-2002-009 | 02 - Hitchland | 1 | PQ | Wind | 79.8 | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | ER/NR | BEPC-SPP | Ft Thompson 69kV [Hyde 69kV]
GEN-2002-022 | 02 - Hitchland | 1 | PQ | Wind | 239.2 | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 - Spearville | 1 | PQ | Wind | 100.5 | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100 | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 04 - Northwest Kansas | 1 | PQ | Wind | 201 | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 04 - Northwest Kansas | 1 | PQ | Wind | 249.3 | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 02 - Hitchland | 1 | PQ | Wind | 159.1 | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 09 - Nebraska | 1 | PQ | Wind | 75 | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 120 | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-008 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 904.5 | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 - Spearville | 1 | PQ | Wind | 152 | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 150 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CT/ST | 260 | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-020 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 27 | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 20.6 | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023N | 09 - Nebraska | 1 | PQ | Coal | 75 | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 30.6 | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2005-008 | 01 - Woodward | 1 | PQ | Wind | 120 | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2005-012 | 03 - Spearville | 1 | PQ | Wind | 248.4 | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 08 - North Oklahoma/South Central Kansas | 1 | PQ | Wind | 199.8 | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-001IS | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 10 | ER/NR | XEL
GEN-2006-002 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 100.8 | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002IS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 53 | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 10 | ER/NR | XEL | Marshall 115kV
GEN-2006-010 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 651 | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 150 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2006-018 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | CT | 168.12 | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 09 - Nebraska | 1 | PQ | Wind | 42 | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 02 - Hitchland | 1 | PQ | Wind | 20 | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 - Spearville | 1 | PQ | Wind | 94 | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 01 - Woodward | 1 | PQ | Wind | 18.9 | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Gas | 604 | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 75.6 | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 132 | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 75 | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 09 - Nebraska | 1 | PQ | Wind | 80 | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 09 - Nebraska | 1 | PQ | Wind | 80 | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 07 - Southwestern Oklahoma | 1 | PQ | Wind | 99 | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 02 - Hitchland | 1 | PQ | Wind | 370 | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 09 - Nebraska | 3 | DIS-09-1 | Wind | 40.5 | ER | NPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 01 - Woodward | 1 | PQ | Wind | 129.6 | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 09 - Nebraska | 1 | PQ | Wind | 81 | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-013IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 50 | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-014IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2007-015IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-017IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 166 | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 234 | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-020IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 16 | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2007-021 | 01 - Woodward | 2 | ICS1 | Wind | 198.9 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 299.2 | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 - Spearville | 3 | DIS-09-1 | Wind | 131.1 | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 01 - Woodward | 2 | ICS1 | Wind | 200 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 01 - Woodward | 2 | ICS1 | Wind | 299.2 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 02 - Hitchland | 2 | ICS1 | Wind | 200 | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 01 - Woodward | 2 | ICS1 | Wind | 151.8 | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 07 - Southwestern Oklahoma | 2 | ICS1 | Gas | 150 | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 01 - Woodward | 2 | ICS1 | Wind | 424 | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 01 - Woodward | 2 | ICS1 | Wind | 101.2 | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-008IS | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 5 | ER/NR | WAPA | Nelson 115kV
GEN-2008-013 | 08 - North Oklahoma/South Central Kansas | 2 | ICS1 | Wind | 300 | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Spearville | 2 | ICS1 | Wind | 250 | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Wind | 299.65 | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 07 - Southwestern Oklahoma | 3 | DIS-09-1 | Wind | 150 | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 07 - Southwestern Oklahoma | 4 | DIS-10-1 | Wind | 99 | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 01 - Woodward | 4 | DIS-10-1 | Wind | 197.8 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 263.13 | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 02 - Hitchland | 3 | DIS-09-1 | Wind | 161 | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 - Spearville | 3 | DIS-09-1 | Wind | 98.9 | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 09 - Nebraska | 3 | DIS-09-1 | Wind | 201 | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 04 - Northwest Kansas | 3 | DIS-09-1 | Wind | 200.48 | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-098 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 09 - Nebraska | 1 | PQ | Wind | 60 | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 09 - Nebraska | 4 | DIS-10-1 | Wind | 89.66 | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Spearville | 3 | DIS-09-1 | Wind | 200.1 | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 13 - Northeast Kansas/Northwest Missouri | 3 | DIS-09-1 | CT | 687.1 | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | BEPC-SPP | Groton-Watertown 345kV
GEN-2009-008 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 198.69 | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-018IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER | BEPC-SPP | Groton 115kV
GEN-2009-020 | 04 - Northwest Kansas | 4 | DIS-10-1 | Wind | 48.3 | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020AIS | 17 - Western South Dakota | 14.5 | DIS-15-2-PQ | Wind | 80 | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-025 | 08 - North Oklahoma/South Central Kansas | 3 | DIS-09-1 | Wind | 59.8 | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-026IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 110 | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2009-040 | 09 - Nebraska | 4 | DIS-10-1 | Wind | 72 | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 02 - Hitchland | 5 | DIS-10-2 | Wind | 300 | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 | ER/NR | BEPC-SPP | Bismarck-Glenham 230kV
GEN-2010-003 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 99.5 | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 34 | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2010-005 | 08 - North Oklahoma/South Central Kansas | 4 | DIS-10-1 | Wind | 299.2 | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-006 | 06 - South Texas Panhandle/New Mexico | 4 | DIS-10-1 | Gas | 205 | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 - Spearville | 4 | DIS-10-1 | Wind | 165.6 | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 01 - Woodward | 4 | DIS-10-1 | Wind | 29.7 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 02 - Hitchland | 4 | DIS-10-1 | Wind | 358.8 | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-036 | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 4.6 | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 13 - Northeast Kansas/Northwest Missouri | 5 | DIS-10-2 | Hydro | 1.17 | ER | WERE | Westar 6th Street 115kV
GEN-2010-040 | 01 - Woodward | 5 | DIS-10-2 | Wind | 300 | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 09 - Nebraska | 5 | DIS-10-2 | Wind | 200 | ER | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 08 - North Oklahoma/South Central Kansas | 6 | DIS-11-1 | Gas | 4.5 | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 04 - Northwest Kansas | 6 | DIS-11-1 | Wind | 201 | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 - Spearville | 6 | DIS-11-1 | Wind | 600 | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 01 - Woodward | 6 | DIS-11-1 | Wind | 100.8 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-011 | 13 - Northeast Kansas/Northwest Missouri | 6 | DIS-11-1 | Coal | 50 | ER | KCPL | Iatan 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-014 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 198 | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 73.6 | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 01 - Woodward | 6 | DIS-11-1 | Wind | 175 | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 01 - Woodward | 6 | DIS-11-1 | Wind | 165.6 | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 02 - Hitchland | 6 | DIS-11-1 | Wind | 299 | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-025 | 06 - South Texas Panhandle/New Mexico | 6 | DIS-11-1 | Wind | 79.96 | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | 09 - Nebraska | 6 | DIS-11-1 | Wind | 120 | ER/NR | NPPD | Hoskins-Twin Church 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 07 - Southwestern Oklahoma | 7 | DIS-11-2 | Wind | 6.6 | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 111 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-045 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | NG CT | 205 | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | Diesel CT | 23 | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 06 - South Texas Panhandle/New Mexico | 7 | DIS-11-2 | CT | 175 | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 14 - South Central Oklahoma | 7 | DIS-11-2 | Wind | 108 | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 01 - Woodward | 7 | DIS-11-2 | Wind | 300 | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056 | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 3.6 | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 | ER | NPPD | John 1 115kV
GEN-2011-056B | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 4.5 | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 | ER | NPPD | John 2 115kV
GEN-2011-056PQ | 09 - Nebraska | 7 | DIS-11-2 | Hydro | 18 | ER | NPPD | Jeffrey 115kV
GEN-2011-057 | 08 - North Oklahoma/South Central Kansas | 7 | DIS-11-2 | Wind | 150 | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 06 - South Texas Panhandle/New Mexico | 8 | DIS-12-1 | Wind | 61.2 | ER | SPS | Tap Grassland Â- Borden County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 14 - South Central Oklahoma | 8 | DIS-12-1 | Wind | 40.8 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 - Spearville | 8 | DIS-12-1 | Gas | 120 | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | Wind | 478 | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 09 - Nebraska | 9 | DIS-12-2 | Gas | 4.8 | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Spearville | 9 | DIS-12-2 | Wind | 180 | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 07 - Southwestern Oklahoma | 9 | DIS-12-2 | Wind | 74 | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 299 | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | Wind | 98.82 | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 7 | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 06 - South Texas Panhandle/New Mexico | 9 | DIS-12-2 | CT | 203 | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 08 - North Oklahoma/South Central Kansas | 9 | DIS-12-2 | CT | 121.5 | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-007 | 14 - South Central Oklahoma | 10 | DIS-13-1 | Wind | 100 | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-008 | 09 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-009IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 19.5 | ER | WAPA | Redfield NW 115kV
GEN-2013-011 | 12 - Northwest Arkansas | 10 | DIS-13-1 | Coal | 40 | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 147 | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012PQ | 08 - North Oklahoma/South Central Kansas | 10 | DIS-13-1 | Gas | 1299 | ER | OKGE | Redbud 345kV
GEN-2013-016 | 06 - South Texas Panhandle/New Mexico | 10 | DIS-13-1 | CT | 203 | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-022 | 06 - South Texas Panhandle/New Mexico | 11 | DIS-13-2 | Solar | 25 | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 148.35 | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Gas | 559.4 | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 08 - North Oklahoma/South Central Kansas | 11 | DIS-13-2 | Wind | 299 | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-032 | 09 - Nebraska | 11 | DIS-13-2 | Wind | 202.5 | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 04 - Northwest Kansas | 11 | DIS-13-2 | Gas | 28.02 | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 08 - North Oklahoma/South Central Kansas | 12 | DIS-14-1 | Wind | 200.6 | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-001IS | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 103.24 | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 01 - Woodward | 12 | DIS-14-1 | Wind | 10.53 | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 01 - Woodward | 12 | DIS-14-1 | Wind | 5.67 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-006IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Gas | 125 | ER/NR | BEPC-SPP | Williston 115kV
GEN-2014-010IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | BEPC-SPP | Neset 115kV
GEN-2014-013 | 09 - Nebraska | 12 | DIS-14-1 | Wind | 73.5 | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-014IS | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | BEPC-SPP | Belfield-Rhame 230kV
GEN-2014-020 | 01 - Woodward | 13 | DIS-14-2 | Wind | 100 | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 13 - Northeast Kansas/Northwest Missouri | 13 | DIS-14-2 | Wind | 300 | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 04 - Northwest Kansas | 13 | DIS-14-2 | Wind | 2.42 | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | CC | 50 | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 35.8 | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 70 | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Solar | 30 | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-039 | 09 - Nebraska | 13 | DIS-14-2 | Wind | 73.4 | ER/NR | NPPD | Friend 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 06 - South Texas Panhandle/New Mexico | 13 | DIS-14-2 | Wind | 320 | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 01 - Woodward | 13 | DIS-14-2 | Wind | 250 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 14 - South Central Oklahoma | 13 | DIS-14-2 | Wind | 249.9 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 08 - North Oklahoma/South Central Kansas | 13 | DIS-14-2 | Wind | 248.4 | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 13 - Northeast Kansas/Northwest Missouri | 14 | DIS-15-1 | Wind | 200.11 | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 160 | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 07 - Southwestern Oklahoma | 14 | DIS-15-1 | Solar | 120 | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-014 | 06 - South Texas Panhandle/New Mexico | 14 | DIS-15-1 | Wind | 150 | ER | SPS | Tap Cochran - Lehman 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 154.58 | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 200 | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 - Spearville | 14 | DIS-15-1 | Solar | 20 | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 09 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 220 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 08 - North Oklahoma/South Central Kansas | 14 | DIS-15-1 | Wind | 219.98 | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-036 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 303.6 | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-041 | 06 - South Texas Panhandle/New Mexico | 16 | DIS-16-1 | CT | 5 | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Battery | 20 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-046 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 300 | ER | WAPA | Tande 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 01 - Woodward | 15 | DIS-15-2 | Wind | 200 | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-055 | 07 - Southwestern Oklahoma | 15 | DIS-15-2 | Solar | 40 | ER | WFEC | Erick 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 01 - Woodward | 15 | DIS-15-2 | Wind | 100 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 4.5 | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 197.8 | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 04 - Northwest Kansas | 15 | DIS-15-2 | Wind | 202.4 | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 248.4 | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-069 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 300 | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 200.1 | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 200 | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-088 | 09 - Nebraska | 15 | DIS-15-2 | Wind | 300 | ER/NR | NPPD | Moore-Pauline 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-089 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 200 | ER | WAPA | Utica 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 08 - North Oklahoma/South Central Kansas | 15 | DIS-15-2 | Wind | 219.99 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 14 - South Central Oklahoma | 15 | DIS-15-2 | Wind | 250 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 01 - Woodward | 15 | DIS-15-2 | Wind | 250 | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-095 | 01 - Woodward | 16 | DIS-16-1 | Wind | 176 | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-096 | 16 - Western North Dakota | 15 | DIS-15-2 | Wind | 150 | ER | BEPC-SPP | Brady 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 01 - Woodward | 16 | DIS-16-1 | Wind | 248.4 | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 16 - Western North Dakota | 16 | DIS-16-1 | Wind | 202 | ER/NR | WAPA | Basin Electric 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 18 - Eastern North Dakota | 16 | DIS-16-1 | Wind | 100.05 | ER | WAPA | Valley City 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Steam Turbine | 29 | ER | OKGE | Osage 69kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | 12 - Northwest Arkansas | 16 | DIS-16-1 | CT | 10 | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Spearville | 16 | DIS-16-1 | Wind | 78.2 | ER | MIDW | North Kinsley 115kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 15 - Eastern South Dakota | 16 | DIS-16-1 | Wind | 250.24 | ER | WAPA | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 01 - Woodward | 16 | DIS-16-1 | Wind | 150 | ER | WFEC | Moreland 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 09 - Nebraska | 16 | DIS-16-1 | WIND | 300 | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 151.8 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA PENDING
GEN-2016-028 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 100 | ER | AEPW | Clayton 138kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Solar | 100 | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 1.5 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200 | ER/NR | OKGE | Crescent 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-036 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 44.6 | ER | WAPA | Granite Falls 115kV | FACILITY STUDY STAGE
GEN-2016-043 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 230 | ER | NPPD | Turtle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Spearville | 16 | DIS-16-1 | Wind | 299 | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-047 | 01 - Woodward | 16 | DIS-16-1 | CT | 24 | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 | ER | NPPD | Axtell â€“ Post Rock 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-051 | 07 - Southwestern Oklahoma | 16 | DIS-16-1 | Wind | 9.8 | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 01 - Woodward | 16 | DIS-16-1 | Wind | 499.1 | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250.7 | ER | OKGE | Sooner-Woodring 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | 14 - South Central Oklahoma | 16 | DIS-16-1 | Wind | 200 | ER/NR | OKGE | Hugo-Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-067 | 04 - Northwest Kansas | 16 | DIS-16-1 | Wind | 73.6 | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 250 | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-070 | 02 - Hitchland | 16 | DIS-16-1 | Wind | 5.3 | ER | SPS | Martin 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | Wind | 200.1 | ER | OKGE | Middleton Tap 138kV | IA PENDING
GEN-2016-073 | 08 - North Oklahoma/South Central Kansas | 16 | DIS-16-1 | WIND | 220 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA PENDING
GEN-2016-074 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 200 | ER | NPPD | Sweetwater 345kV | FACILITY STUDY STAGE
GEN-2016-075 | 09 - Nebraska | 16 | DIS-16-1 | Wind | 50 | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
GEN-2016-087 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 98.9 | ER | WAPA | Bismark-Glenham 230kV line | FACILITY STUDY STAGE
GEN-2016-088 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 151.2 | ER/NR | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 303.6 | ER | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-092 | 15 - Eastern South Dakota | 17 | DIS-16-2 | Wind | 175 | ER | WAPA | Fort Thompson-Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-094 | 17 - Western South Dakota | 17 | DIS-16-2 | Wind | 200 | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | FACILITY STUDY STAGE
GEN-2016-095 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 200 | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | FACILITY STUDY STAGE
GEN-2016-097 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 100 | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | FACILITY STUDY STAGE
GEN-2016-100 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-101 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 195 | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-102 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 150.9 | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-106 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 400 | ER | NPPD | Gerald Gentleman Station 345kV | FACILITY STUDY STAGE
GEN-2016-110 | 09 - Nebraska | 17 | DIS-16-2 | Wind | 152 | ER | WAPA | Laramie River-Stegall 345kV Line | FACILITY STUDY STAGE
GEN-2016-111 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | FACILITY STUDY STAGE
GEN-2016-112 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 220 | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | FACILITY STUDY STAGE
GEN-2016-114 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 310 | ER/NR | WERE | Reno-(GEN-2016-112 Tap) Summit 345kV | FACILITY STUDY STAGE
GEN-2016-115 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 300 | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 01 - Woodward | 17 | DIS-16-2 | Wind | 288 | ER | WFEC | Dover Switchyard 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 600 | ER | OKGE | Spring Creek-Sooner 345kV | FACILITY STUDY STAGE
GEN-2016-121 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Solar | 110 | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-122 | 04 - Northwest Kansas | 17 | DIS-16-2 | Wind | 225 | ER | WERE | Reno (GEN-2016-111 Tap)-Summit 345kV | FACILITY STUDY STAGE
GEN-2016-123 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 298 | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-124 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 150 | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-125 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Wind | 74 | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 14 - South Central Oklahoma | 17 | DIS-16-2 | Wind | 172.5 | ER/NR | OKGE | Arbuckle 138kV | IA PENDING
GEN-2016-128 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 176 | ER | OKGE | Woodring 345kV | FACILITY STUDY STAGE
GEN-2016-130 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 | ER | WAPA | Leland Olds 345kV | FACILITY STUDY STAGE
GEN-2016-131 | 01 - Woodward | 17 | DIS-16-2 | Wind | 2.5 | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 07 - Southwestern Oklahoma | 17 | DIS-16-2 | Wind | 6.12 | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-134 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-137 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-138 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 187.5 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-139 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 100 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-141 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-142 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 350 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-145 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-146 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 175 | ER | AEPW | Riverside 345kV | FACILITY STUDY STAGE
GEN-2016-147 | 09 - Nebraska | 17 | DIS-16-2 | Solar | 40 | ER | NPPD | Sidney 115kV Sub | FACILITY STUDY STAGE
GEN-2016-149 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | 16 - Western North Dakota | 17 | DIS-16-2 | Wind | 202 | ER | BEPC-SPP | Tande 345kV | IA PENDING
GEN-2016-153 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 134 | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-157 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-158 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 252 | ER | KCPL | West Gardner 345kV | IA PENDING
GEN-2016-160 | 04 - Northwest Kansas | 17 | DIS-16-2 | Battery | 20 | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-161 | 02 - Hitchland | 17 | DIS-16-2 | Wind | 3.02 | ER | SPS | Martin 115kV | FACILITY STUDY STAGE
GEN-2016-162 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-163 | 08 - North Oklahoma/South Central Kansas | 17 | DIS-16-2 | Wind | 252 | ER | WERE | Benton 345kV | FACILITY STUDY STAGE
GEN-2016-167 | 10 - Southeast Oklahoma/Northeast Texas | 17 | DIS-16-2 | Solar | 73.5 | ER/NR | AEPW | Lieberman - North Benton 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 13 - Northeast Kansas/Northwest Missouri | 17 | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 06 - South Texas Panhandle/New Mexico | 17 | DIS-16-2 | Gas Turbine | 17 | ER | SPS | XTO-Cornell 115kV station | IA PENDING
GEN-2017-094 | 15 - Eastern South Dakota | 18 | DIS-17-1 | Wind | 200 | ER/NR | WAPA | Fort Thompson-Huron 230 kV | DISIS STAGE
GEN-2020-014 | 16 - Western North Dakota |  | DIS-20-1 | Gas | 45 | ER/NR | BEPC | Lonesome Creek 115 kV | DISIS STAGE | Not Applicable, Interconnection at Existing Facility
GrayCountyWindMontezuma | 03 - Spearville | 1 | PQ | Wind | 110 | ER | SUNC | Gray County Tap 115kV
H081 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 201 | ER | XEL | Brookings County - Lyon County 345kV
H092 | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 60 | ER/NR | MP | MP Boswell
H092BOSWELL | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Coal | 585 | ER/NR | MP | MP Boswell
H096 | 09 - Nebraska | 7.5 | DIS-15-2-PQ | Wind | 50 | ER/NR | ALTW | Grand Junction - Perry 161kV
J091 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 66 | ER/NR | ALTW
J171 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Biomass | 7 | ER/NR | XEL | Benson 115kV
J183 | 15 - Eastern South Dakota | 8.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | Split Rock
J191 | 09 - Nebraska | 8.5 | DIS-15-2-PQ | Wind | 101.2 | ER/NR | MEC | Rolling Hills 345kV
J200 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Gas | 99 | ER/NR | MDU | RM Heskett Station 115kV & 41.6kV
J249 | 18 - Eastern North Dakota | 8.5 | DIS-15-2-PQ | Wind | 90 | ER/NR | MDU | MDU Tatanka
J262 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | OTP | OTP Jamestown 345/115kV
J263 | 16 - Western North Dakota | 9.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | OTP | OTP Jamestown 345/115kV
J274 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | MEC | Winterset. - Creston 161kV
J278 | 15 - Eastern South Dakota | 10.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | 161kV bus at the Pleasant Valley Station
J279 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Coal | 30 | ER/NR | MEC | Raun 345kV
J279NEAL | 09 - Nebraska | 1 | DIS-15-2-PQ | Coal | 680 | ER/NR | MEC
J285 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 250 | ER/NR | MEC | Proposed O'Brien County 345kV
J289 | 09 - Nebraska | 10.5 | DIS-15-2-PQ | Wind | 20 | ER/NR | MEC | 161kV sybstation on Winterset Junction to Creston 161kV Line
J290 | 16 - Western North Dakota | 10.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | XEL | 230kV Rugby to Glenboro
J299 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Combined Cycle | 73 | ER | XEL | Wilmarth
J302 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 101.2 | ER/NR | MDU | 230kV Heskett-Wishek
J316 | 16 - Western North Dakota | 12.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | MDU | MDU 230kV Tatanka-Ellendale line
J320 | 18 - Eastern North Dakota | 12.5 | DIS-15-2-PQ | Wind | 55 | ER | XEL | Xcel's existing High Bridge 115kV
J343 | 09 - Nebraska | 12.5 | DIS-15-2-PQ | Wind | 150 | ER/NR | MEC | 161kV on Creston-Clarinda line
J385 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 100 | ER/NR | XEL | Chisago 115kV
J400 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Solar | 62.5 | ER/NR | XEL | Lyon County 115kV
J405 | 16 - Western North Dakota | 13.5 | DIS-15-2-PQ | Gas | 40 | ER/NR | MDU | MDUs existing Lewis & Clark Jct
J407 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | XEL | Glenworth 161kV
J411 | 09 - Nebraska | 13.5 | DIS-15-2-PQ | Wind | 300 | ER/NR | MEC | LeHigh - Raun 345kV Line
J412 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | MEC | LeHigh - Raun 345kV line
J416 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 | ER/NR | ALTW
J426 | 15 - Eastern South Dakota | 13.5 | DIS-15-2-PQ | Wind | 100 | ER/NR | XEL | Chanarambie 35.4kV
J432 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 98 | ER/NR | XEL | Brookings 345kV
J436 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | ER | OTP | Big Stone South - Ellendale 345kV line
J437 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 150 | ER | OTP | Big Stone South - Ellendale 345kV line
J442 | 15 - Eastern South Dakota | 14.5 | DIS-15-2-PQ | Wind | 200 | ER/NR | OTP | Big Stone via a radial 230kV line
J455 | 09 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 300 | ER | ALTW | Kossuth â€“ Obrien 345kV line
J460 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 200 | ER/NR | XEL | on Brookings - H081 345kV line approx. 10 miles west of proposed
J475 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 | ER/NR | MEC
J476 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 246 | ER/NR | AMMO | Atchison County to Booneville 345kV Line Tap
J488 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 151.8 | ER | OTP | 345kV at new Tap on proposed MVP Big Stone to Ellendale line
J493 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 150 | ER/NR | OTP | Big Stone - Brookings 345kV
J495 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 | ER/NR | ALTW | Ledyard-Colby 345kV line
J498 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 | ER/NR | MEC | MEC 345kV Grimes-Lehigh line (18 miles south of Leigh )
J499 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 340 | ER/NR | MEC | MEC 345kV Fallow-Grimes line (18 miles east of Fallow )
J500 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 500 | ER/NR | MEC | New at intersection of MEC 345kV Boone-Atchison and MEC 345kV Rolling Hills-Madison County
J503 | 18 - Eastern North Dakota | 16.5 | DIS-16-2-PQ | Wind | 98.8 | ER/NR | MDU | 230kV Heskett-Wishek, 20 miles NW of Wishek
J506 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 200 | ER/NR | MEC | Raun-Lakefield Jct 345kV line tap (T-19N, R-43W)
J510 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Gas | 284.5 | ER/NR | OTP | Scandinavia Township 113N, Range 48W
J512 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 250 | ER/NR | MP | Nobles - Fenton 115kV line
J524 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Solar | 100 | ER/NR | MEC | Webster 161kV bus
J526 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 300 | ER/NR | OTP | Brooking County to Big Stone South 345kV line
J527 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 | ER/NR | MEC | Booneville Cooper 345kV line
J529 | 15 - Eastern South Dakota | 15.5 | DIS-16-1-PQ | Wind | 250 | ER/NR | MEC | Obrien - Kossuth 345kV line
J530 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 | ER/NR | MEC | Montezuma - Hills 345kV Line
J534 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 250 | ER/NR | ALTW | Kossuth â€“ Webster 345kV Line
J535 | 09 - Nebraska | 15.5 | DIS-16-1-PQ | Wind | 210 | ER/NR | ALTW | J411 â€“ Lehigh 345kV Line
J541 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 400 | ER/NR | AMMO | Zachary-Ottumwa 345kV line
J555 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 140 | ER/NR | MEC
J569 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 100 | ER/NR | XEL | NSP Rock County
J583 | 09 - Nebraska | 16.5 | DIS-16-2-PQ | Wind | 200 | ER/NR | MEC | Fallow Avenue 345kV . Zip Code 50002
J587 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 200 | ER/NR | XEL | J460 on the Brookings-H081 345kV line
J590 | 15 - Eastern South Dakota | 16.5 | DIS-16-2-PQ | Wind | 90 | ER/NR | MEC | Obrien - Kossuth 345kV line
J611 | 13 - Northeast Kansas/Northwest Missouri | 16.5 | DIS-16-2-PQ | Wind | 110 | ER/NR | MEC | Clarinda - Merryville 161kV tap
J718 | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Solar | 49.98 | ER/NR | XEL
J748 | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 200 | ER/NR | MEC
LlanoEstacadoWhiteDeer | 02 - Hitchland | 1 | PQ | Wind | 80 | ER | SPS | Llano Wind 115kV
MPC00100 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 99 | ER | OTP | Langdon 115kV
MPC00200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 60 | ER | OTP | Langdon 115kV
MPC00300 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 40.5 | ER | OTP | Langdon 115kV
MPC00500 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 327.8 | ER/NR | OTP | Maple River 230kV
MPC00500GRE | 18 - Eastern North Dakota | 1 | DIS-15-2-PQ | Wind | 51 | ER/NR | GRE
MPC01200 | 18 - Eastern North Dakota | 14.5 | DIS-15-2-PQ | Wind | 49.6 | ER | OTP | Maple River 230kV
MPC01300 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Coal | 493 | ER/NR | OTP | Square Butte 230kV
MPC02100 | 16 - Western North Dakota | 14.5 | DIS-15-2-PQ | Wind | 100 | ER | OTP | Center - Mandan 230kV
NPPDBrokenBow | 09 - Nebraska | 1 | PQ | Heat | 7.3 | ER | NPPD | Broken Bow 115kV
NPPDBuffaloCountySolar | 09 - Nebraska | 1 | PQ | Solar | 10 | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 09 - Nebraska | 1 | PQ | Wind | 20 | ER | NPPD | Tekamah & Oakland 115kV
NPPDBurwell | 09 - Nebraska | 1 | PQ | Heat | 3.3 | ER | NPPD | Ord 115kV
NPPDColumbusHydro | 09 - Nebraska | 1 | PQ | Hydro | 45 | ER | NPPD | Columbus 115kV
NPPDOrd | 09 - Nebraska | 1 | PQ | Heat | 10.8 | ER | NPPD | Ord 115kV
NPPDSpringview | 09 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 3 | ER | NPPD
NPPDStuart | 09 - Nebraska | 1 | PQ | Heat | 1.8 | ER | NPPD | Ainsworth 115kV
PQOKGEMustang | 01 - Woodward | 16 | DIS-16-1 | CT | 444.1 | ER | OKGE
R15 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 | ER/NR | MEC | Pomeroy 161kV
R22 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 200 | ER/NR | MEC
R23 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 100 | ER/NR | MEC | Monona - Carroll 161kV
R26 | 13 - Northeast Kansas/Northwest Missouri | 1 | DIS-15-2-PQ | Wind | 400 | ER | MEC | MEC Cooper - Booneville 345kV
R34 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 | ER/NR | MEC | Council Bluffs - Madison County 345kV
R35 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 80 | ER/NR | MEC | Pomeroy Wind Farm site
R39 | 15 - Eastern South Dakota | 1 | DIS-15-2-PQ | Wind | 499.98 | ER/NR | MEC | Raun - Lakefield Junction
R42 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 250 | ER/NR | MEC
R49 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 12 | ER/NR | MEC | Pomeroy Generating station
R65 | 09 - Nebraska | 1 | DIS-15-2-PQ | Wind | 92 | ER/NR | MEC | R34 Expansion
SPSCarson | 02 - Hitchland | 1 | PQ | Wind | 10 | ER | SPS | Martin 115kV
SPSChanning | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Wind | 4.2 | ER | SPS
SPSDumas19thSt | 02 - Hitchland | 1 | PQ | Wind | 20 | ER | SPS | Dumas 19th Street 115kV
SPSEtter | 02 - Hitchland | 1 | PQ | Wind | 20 | ER | SPS | Etter 115kV
SPSHopi | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | Hopi 115kV
SPSJal | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | S Jal 115kV
SPSLeaCounty | 06 - South Texas Panhandle/New Mexico | 17.5 | DIS-17-1-PQ | Solar | 5.5 | ER | SPS
SPSLeaRoad | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | Lea Road 115kV
SPSMonument | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | Monument 115kV
SPSMooreE | 02 - Hitchland | 1 | PQ | Wind | 17.5 | ER | SPS | Moore East 115kV
SPSOcotillo | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Solar | 10 | ER | SPS | S_Jal 115kV
SPSSherman | 02 - Hitchland | 1 | PQ | Wind | 20 | ER | SPS | Sherman 115kV
Sunray | 06 - South Texas Panhandle/New Mexico | 1 | PQ | Wind | 34.5 | ER | SPS | Valero 115kV
SWPANixaSolar | 12 - Northwest Arkansas | 17.5 | DIS-17-1-PQ | Solar | 7.9 | ER | SWPA
WAPAMPSWind | 18 - Eastern North Dakota | 17.5 | DIS-17-1-PQ | Wind | 1.5 | ER | WAPA
WAPASEAMSFtRandleHydro | 09 - Nebraska | 1 | PQ | Hydro | 351.2 | ER | WAPA | Ft Randle (WAPA) 230kV & 115kV
WAPASEAMSGavinsPtHydro | 09 - Nebraska | 1 | PQ | Hydro | 102 | ER | WAPA | Gavins Point (WAPA) 115kV
WAPASEAMSSpiritMoundHeat | 09 - Nebraska | 1 | PQ | Heat | 120 | ER | BEPC-SPP | Spirit Mound (WAPA) 115kV
WAPATitanWind | 15 - Eastern South Dakota | 17.5 | DIS-17-1-PQ | Wind | 25 | ER | WAPA
Young1 | 16 - Western North Dakota | 1 | DIS-15-2-PQ | Coal | 274 | ER | OTP

## Scenarios
Generation Interconnection Number or Upgrade ID | Assigned Study Cluster | Cluster Priority | Anticipated Commercial Operation or In-service Date | Service Type | Point of Interconnection or Upgrade Name | Requested Study or Upgrade Type | Requested Capacity or Upgrade Details | Scenario 1: Status or Available ERIS MW | Scenario 2: Status or Available NRIS MW
GEN-2015-046 | DIS-15-2 | 15 | 2017-12-01 | ER | Tande 345kV | NA | 300 | 300 | 300
GEN-2015-096 | DIS-15-2 | 15 | 2017-12-31 | ER | Brady 230kV | NA | 150 | 150 | 150
GEN-2016-004 | DIS-16-1 | 16 | 2022-10-05 | ER/NR | Basin Electric 230kV | NA | 202 | 202 | 202
GEN-2016-007 | DIS-16-1 | 16 | 2018-12-31 | ER | Valley City 115kV | NA | 100.05 | Not In-Service | Not In-Service
GEN-2016-094 | DIS-16-2 | 17 | 2020-10-01 | ER | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | NA | 200 | 200 | 200
GEN-2016-130 | DIS-16-2 | 17 | 2019-09-15 | ER | Leland Olds 345kV | NA | 202 | 202 | 202
GEN-2016-151 | DIS-16-2 | 17 | 2019-09-15 | ER | Tande 345kV | NA | 202 | 202 | 202
GEN-2020-014 | DISIS-2020-001 | NA | 2021-06-17 | ER/NR | Lonesome Creek 115kV | NA | 45 | 28.5 | 0
50442 (NTC 200220) | DISIS-2015-001 | NA | NA | NA | Cherry Co. - Gentleman 345 kV Ckt 1 | Generator Interconnection | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | Not In-Service | Not In-Service
50444 (NTC 200220) | DISIS-2015-001 | NA | NA | NA | Cherry Co. Substation 345 Kv | Generator Interconnection | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | Not In-Service | Not In-Service
50445 (NTC 200220) | DISIS-2015-001 | NA | NA | NA | Cherry Co. - Holt Co. 345 kV Ckt 1 | Generator Interconnection | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | Not In-Service | Not In-Service
50446 (NTC 200220) | DISIS-2015-001 | NA | NA | NA | Holt Co. Substation 345 kV | Generator Interconnection | Build new Holt County 345 kV substation tap on the Grand Island - Fort Thompson 345 kV line owned by WAPA. Install necessary terminal equipment at new substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | In-Service | In-Service
71996 | SPP-2017-AG1-AFS-1 | NA | NA | NA | Hoyt - Jeffrey Energy Center 345 kV Double Circuit Rebuild | AFS | Rebuild Hoyt - Jeffrey Energy Center 345 kV as a double circuit using bundled 1590 ACSR on both circuits. | Not In-Service | Not In-Service
112189 | DISIS-2015-002 | NA | NA | NA | Dickinson 230/115kV CKT 2 | Generator Interconnection | Build new 230/115/13.8kV Transformer circuit #2 at Dickinson and expand Dickinson 115kV switchyard | Not In-Service | Not In-Service
122704 | DISIS-2016-002 | NA | NA | NA | Ft Thompson Xfmr Upgrade CKT1 | Generator Interconnection | Replace Ft. Thompson 345/230kV Transformer CKT 1 with minimum emergency rating 390 MVA | Not In-Service | Not In-Service
122711 | DISIS-2016-002 | NA | NA | NA | Ft Thompson Xfmr Upgrade CKT2 | Generator Interconnection | Replace Ft. Thompson 345/230kV Transformer CKT 2 with minimum emergency rating 390 MVA | Not In-Service | Not In-Service
122699 | DISIS-2016-002 | NA | NA | NA | Antelope - Holt 345kV CKT1 | Generator Interconnection | Build approximately 30 miles of 345kV from Antelope - Holt with a minimum emergency of 1793MVA | Not In-Service | Not In-Service
91904 | DISIS-2017-001 | NA | NA | NA | Chappelle Creek to Ft. Thompson 345k New Build CKT 2 | Generator Interconnection | Build a new 30 mile 345kV line from Chappelle Creek to Ft. Thompson as a second circuit | Not In-Service | Not In-Service
81534 | DISIS-2017-001 | NA | NA | NA | Garrison to Pick City 115kV Rebuild | Generator Interconnection | Rebuild the existing Garrison to Pick City 115kV 5.0 mile line to achieve a minimum summer/emergency rating of 167 MVA | Not In-Service | Not In-Service
81534 | DISIS-2017-001 | NA | NA | NA | Stanton to Beulah 115kV Rebuild | Generator Interconnection | Rebuild the existing Stanton to Beulah 115kV 13.41 mile line to achieve a minimum summer/emergency rating of 168 MVA | Not In-Service | Not In-Service
81534 | DISIS-2017-001 | NA | NA | NA | Stanton to Pick City 115kV Rebuild | Generator Interconnection | Rebuild the existing Stanton to Pick City 115kV 7.43 mile line to achieve a minimum summer/emergency rating of 168 MVA | Not In-Service | Not In-Service
91957 | DISIS-2017-001 | NA | NA | NA | Watertown to Appledorn 230kV Rebuild | Generator Interconnection | Rebuild the existing Watertown to Appledorm 230kV 55.30 mile line to achieve a minimum summer/emergency rating of 376 MVA | Not In-Service | Not In-Service
N/A | DISIS-2017-001 | NA | NA | NA | Eastowne 161kV Reactive Support | Generator Interconnection | Install a 250 MVAR capacitor bank (STATCOM) at Eastowne 161kV Substation | Not In-Service | Not In-Service
N/A | DISIS-2017-001 | NA | NA | NA | Ft. Randall to Lake Platte 230kV Rebuild | Generator Interconnection | Rebuild the existing Ft. Randall to Lake Platte 230kV 43.34 mile line to achieve a minimum summer/emergency rating of 353 MVA | Not In-Service | Not In-Service
N/A | DISIS-2017-001 | NA | NA | NA | Ft. Thompson to Ft. Randall 230kV Rebuild | Generator Interconnection | Rebuild the existing Ft. Thompson to Ft. Randall 230kV 87.32 mile line to achieve a minimum summer/emergency rating of 367 MVA | Not In-Service | Not In-Service
N/A | DISIS-2017-001 | NA | NA | NA | Mark Moore 161kV Reactive Support | Generator Interconnection | Install a 300 MVAR capacitor bank at Mark Moore 161kV Substation | Not In-Service | Not In-Service
N/A | DISIS-2017-001 | NA | NA | NA | Mt. Vernon to Storla 115kV Rebuild | Generator Interconnection | Rebuild the existing Mt. Vernon to Storla 115kV 15.0 mile line to achieve a minimum summer/emergency rating of 128 MVA | Not In-Service | Not In-Service
N/A | DISIS-2017-001 | NA | NA | NA | Utica Jct. to Napa Jct. 115kV Rebuild | Generator Interconnection | Rebuild the existing Utica Jct. to Napa Jct. 115kV 13.16 mile line to achieve a minimum summer/emergency rating of 135 MVA | Not In-Service | Not In-Service
143226 | DISIS-2017-001-P2 | NA | NA | NA | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Generator Interconnection | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | Not In-Service | Not In-Service
143324 | DISIS-2017-001-P2 | NA | NA | NA | G17-010 Tap 230kV Reactive Support (DISIS-2017-001) | Generator Interconnection | Stability identified need to Install 135 MVar SVC for Dynamic Reactive Support at G17-010 Tap 230kV | Not In-Service | Not In-Service
143222 | DISIS-2017-001-P2 | NA | NA | NA | MERRCRT4 to Wishek 230kV Rebuild (DISIS-2017-001) | Generator Interconnection | Rebuild the existing MERRCRT4 to Wishek 230kV 29.3 mile line to achieve a minimum Summer/Normal rating of 401 MVA | Not In-Service | Not In-Service
143229 | DISIS-2017-001-P2 | NA | NA | NA | Napoleon SW to Wishek 230kV Rebuild (DISIS-2017-001) | Generator Interconnection | Rebuild the existing Napoleon SW to Wishek 230kV 24.89 mile line to achieve a minimum Summer/Normal rating of 407 MVA | Not In-Service | Not In-Service
132999 | DISIS-2017-001-P2 | NA | NA | NA | Neset 230 kV Substation GEN-2017-048 Interconnection (Non-Shared NU) (BEPC) | Generator Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-048 (300 MW/Wind), into the Point of Interconnection (POI) at Neset 230 kV Substation. | Not In-Service | Not In-Service
132998 | DISIS-2017-001-P2 | NA | NA | NA | Neset 230 kV Substation GEN-2017-048 Interconnection (TOIF) (BEPC) | Generator Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-048 (300 MW/Wind), into the Point of Interconnection (POI) at Neset 230 kV Substation. | Not In-Service | Not In-Service
143236 | DISIS-2017-001-P2 | NA | NA | NA | Neset to Tioga 230kV Rebuild (DISIS-2017-001) (BEPC) | Generator Interconnection | Rebuild the existing Neset to Tioga 230kV 1.0 mile line to achieve a minimum Summer/Emergency rating of 725 MVA | Not In-Service | Not In-Service
132949 | DISIS-2017-001-P2 | NA | NA | NA | Rhame 230 kV Substation GEN-2017-010 Interconnection (Non-Shared NU) (BEPC) | Generator Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-010 (200.1 MW/Wind), into the Point of Interconnection (POI) at Rhame 230 kV Substation. | Not In-Service | Not In-Service
132948 | DISIS-2017-001-P2 | NA | NA | NA | Rhame 230 kV Substation GEN-2017-010 Interconnection (TOIF) (BEPC) | Generator Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2017-010 (200.1 MW/Wind), into the Point of Interconnection (POI) at Rhame 230 kV Substation. | Not In-Service | Not In-Service
143237 | DISIS-2017-001-P2 | NA | NA | NA | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Generator Interconnection | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | Not In-Service | Not In-Service
143326 | DISIS-2017-001-P2 | NA | NA | NA | Tioga 230kV Terminal Upgrades for Boundary Dam New Line (DISIS-2017-001) (MDU) | Generator Interconnection | Stability identified need to upgrade terminal equipment at Tioga 230kV to accept Boundary Dam CKT 2 | Not In-Service | Not In-Service
143327 | DISIS-2017-001-P2 | NA | NA | NA | Tioga to Boundary Dam 230kV New Line (DISIS-2017-001) (BEPC) | Generator Interconnection | Stability identified need to build approximately 57.5 miles of new 230kV line from Tioga to Boundary Dam (DISIS-2017-001) | Not In-Service | Not In-Service

## Constraints Summary
SCENARIO | Generation Interconnection Number | Group | Service Type | Constraints | Constraint Type | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading (%) | TC Loading (%) | BC Voltage | TC Voltage | VMIN | VMAX | Impact Study Mitigation
Scenario 1 | GEN-2020-014 | 00 | ER | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | Thermal | 20SP, 24SP, 29SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 125 | 125 | 69.34 | 105.02 |  |  |  |  | Re-conductor the Cheery Creek - Arnegard 115 kV line with a minimum rating of 140 MVA
Scenario 1 | GEN-2020-014 | 00 | ER | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | Thermal | 20SP, 24SP, 29SP | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 | 125 | 125 | 75.34 | 111.52 |  |  |  |  | Re-conductor the East Hay Butte - Arnegard 115 kV line with a minimum rating of 140 MVA
Scenario 2 | GEN-2020-014 | 00 | NR | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | Thermal | 20SP, 24SP, 29SP | BASE CASE | 125 | 125 | 68.54 | 103.38 |  |  |  |  | Re-conductor the Cheery Creek - Arnegard 115 kV line with a minimum rating of 140 MVA
Scenario 2 | GEN-2020-014 | 00 | NR | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | Thermal | 20SP, 24SP, 29SP | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z | 125 | 125 | 75.33 | 110.99 |  |  |  |  | Re-conductor the East Hay Butte - Arnegard 115 kV line with a minimum rating of 140 MVA
Scenario 2 | GEN-2020-014 | 00 | NR | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | Thermal | 20SP, 24SP, 29SP | P23:345:OTP:BUFFALO3:3655:V2016 | 342 | 342 | 108.09 | 109.06 |  |  |  |  | Re-build the SHEYNNE4 - FARGO 4 230 kV line with a minimum rating of 374 MVA
Scenario 2 | GEN-2020-014 | 00 | NR | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | Thermal | 20SP, 24SP | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT | 720 | 720 | 99.95 | 100.71 |  |  |  |  | Re-build the HOLT.CO3 - GR ISLD-LNX3 345 kV line with a minimum rating of 726 MVA
Scenario 2 | GEN-2020-014 | 00 | NR | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | Thermal | 24SP, 24WP | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | 250 | 313 | 129.08 | 130.95 |  |  |  |  | Replace the Ft Thompson 345/230 kV transformers 1&2 with a minimum rating of 410 MVA
Scenario 2 | GEN-2020-014 | 00 | NR | 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z | Thermal | 24SP, 29SP | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296) | 212 | 212 | 126.44 | 127.38 |  |  |  |  | Re-build the GROTON 7 - GROTONSOUTH7 115 kV line with a minimum rating of 271 MVA
Scenario 2 | GEN-2020-014 | 00 | NR | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | Thermal | 20SP, 24SP | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT | 720 | 720 | 100.8 | 101.63 |  |  |  |  | Re-build the GR ISLD3 - GR ISLD-LNX3 345 kV line with a minimum rating of 732 MVA
Scenario 1 | GEN-2020-014 | 00 | ER | GRE-RAMSEY 4 | Voltage | 24SP | P23:345:MPC:PRAIRIE3:4440 |  |  |  |  | 1.0061 | 1.0504 | 0.9 | 1.05 | Local switched shunt/transformer tap change
Scenario 1 | GEN-2020-014 | 00 | ER | GRE-BALTA 4 | Voltage | 24SP | P23:345:MPC:PRAIRIE3:4440 |  |  |  |  | 1.0305 | 1.0511 | 0.9 | 1.05 | Local switched shunt/transformer tap change
Scenario 1 | GEN-2020-014 | 00 | ER | GRE-RMSYCB14 | Voltage | 24SP | P23:345:MPC:PRAIRIE3:4440 |  |  |  |  | 1.0061 | 1.0504 | 0.9 | 1.05 | Local switched shunt/transformer tap change
Scenario 1 | GEN-2020-014 | 00 | ER | GRE-RMSYCB24 | Voltage | 24SP | P23:345:MPC:PRAIRIE3:4440 |  |  |  |  | 1.0061 | 1.0505 | 0.9 | 1.05 | Local switched shunt/transformer tap change
Scenario 2 | GEN-2020-014 | 00 | NR | POSTROCK7 | Voltage | 20SP | P11:0:XEL:AUTO-SINGLE:G362GRDMDW:W |  |  |  |  | 1.052 | 1.0519 | 0.9 | 1.05 | Local switched shunt/transformer tap change
Scenario 2 | GEN-2020-014 | 00 | NR | REDWILO3 | Voltage | 20SP | P11:0:XEL:AUTO-SINGLE:G362GRDMDW:W |  |  |  |  | 1.0576 | 1.0574 | 0.9 | 1.05 | Local switched shunt/transformer tap change

## All Thermal
SOLUTION | SCENARIO | GROUP | SEASON | SOURCE | DIRECTION | MONITORED ELEMENT | RATEA (MVA) | RATEB(MVA) | TDF | BC%LOADING (% MVA) | TC%LOADING (% MVA) | CONTINGENCY
FDNS | Scenario 1 | 00LVER | 20SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 68.54 | 103.36 | Base Case
FDNS | Scenario 1 | 00LVER | 20SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.3 | 110.98 | Base Case
FDNS | Scenario 1 | 00LVER | 24SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 68.3 | 103.32 | Base Case
FDNS | Scenario 1 | 00LVER | 24SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.17 | 110.96 | Base Case
FDNS | Scenario 1 | 00LVER | 29SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 68.13 | 102.86 | Base Case
FDNS | Scenario 1 | 00LVER | 29SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.41 | 111.01 | Base Case
FDNS | Scenario 1 | 00LVER | 20SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 69.34 | 105.02 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
FDNS | Scenario 1 | 00LVER | 20SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 69.34 | 105.02 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
FDNS | Scenario 1 | 00LVER | 20SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.34 | 111.52 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
FDNS | Scenario 1 | 00LVER | 20SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.34 | 111.52 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
FDNS | Scenario 1 | 00LVER | 24SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 68.3 | 103.32 | P12:115:MP-XEL:STN-BFT
FDNS | Scenario 1 | 00LVER | 24SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.17 | 110.96 | P12:115:MP-XEL:STN-BFT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 68.54 | 103.38 | Base Case
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.29 | 110.98 | Base Case
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 68.3 | 103.28 | Base Case
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.19 | 110.96 | Base Case
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 68.13 | 103.21 | Base Case
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.42 | 110.97 | Base Case
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06158 | 105.96 | 106.68 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06158 | 105.34 | 106.07 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06156 | 105.34 | 106.07 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06156 | 105.34 | 106.07 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06156 | 105.34 | 106.07 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06156 | 105.34 | 106.07 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06158 | 105.96 | 106.68 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06158 | 105.96 | 106.68 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06158 | 105.34 | 106.07 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06156 | 105.34 | 106.07 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06156 | 105.34 | 106.07 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06156 | 105.34 | 106.07 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06156 | 105.34 | 106.07 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06158 | 105.96 | 106.68 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06158 | 108.09 | 108.83 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06158 | 107.35 | 108.1 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06156 | 107.36 | 108.11 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06156 | 107.36 | 108.11 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06156 | 107.36 | 108.11 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06156 | 107.36 | 108.11 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997164 FT2 KU1B 230 1 | 250 | 313 | 0.06158 | 108.09 | 108.83 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06158 | 108.09 | 108.83 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06158 | 107.35 | 108.1 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06156 | 107.36 | 108.11 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06156 | 107.36 | 108.11 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06156 | 107.36 | 108.11 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06156 | 107.36 | 108.11 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 19WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997165 FT2 KU1A 230 1 | 250 | 313 | 0.06158 | 108.09 | 108.83 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 608624 FORBES 4 230 997688 FBS7ABC 230 1 | 672 | 672 | 0.05514 | 131.17 | 131.6 | P24:500:MP:FBS:601LX
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.11837 | 99.87 | 100.63 | P11:024:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.11837 | 99.87 | 100.63 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.11892 | 99.95 | 100.71 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.11837 | 100.72 | 101.54 | P11:024:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.11837 | 100.72 | 101.54 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.11892 | 100.8 | 101.63 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997167 FT2 KU1B 230 1 | 250 | 313 | 0.06232 | 125.29 | 120.12 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997167 FT2 KU1B 230 1 | 250 | 313 | 0.06232 | 120.2 | 121 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997167 FT2 KU1B 230 1 | 250 | 313 | 0.0623 | 120.28 | 121.18 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997167 FT2 KU1B 230 1 | 250 | 313 | 0.0623 | 120.28 | 121.19 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997167 FT2 KU1B 230 1 | 250 | 313 | 0.0623 | 120.28 | 121.18 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997167 FT2 KU1B 230 1 | 250 | 313 | 0.0623 | 120.28 | 121.18 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997167 FT2 KU1B 230 1 | 250 | 313 | 0.06232 | 125.29 | 120.12 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997168 FT2 KU1A 230 1 | 250 | 313 | 0.06232 | 125.29 | 120.12 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997168 FT2 KU1A 230 1 | 250 | 313 | 0.06232 | 120.2 | 121 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997168 FT2 KU1A 230 1 | 250 | 313 | 0.0623 | 120.28 | 121.18 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997168 FT2 KU1A 230 1 | 250 | 313 | 0.0623 | 120.28 | 121.19 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997168 FT2 KU1A 230 1 | 250 | 313 | 0.0623 | 120.28 | 121.18 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997168 FT2 KU1A 230 1 | 250 | 313 | 0.0623 | 120.28 | 121.18 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997168 FT2 KU1A 230 1 | 250 | 313 | 0.06232 | 125.29 | 120.12 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997167 FT2 KU1B 230 1 | 250 | 313 | 0.06232 | 129.21 | 122.6 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997167 FT2 KU1B 230 1 | 250 | 313 | 0.06232 | 122.84 | 123.7 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997167 FT2 KU1B 230 1 | 250 | 313 | 0.0623 | 122.94 | 123.95 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997167 FT2 KU1B 230 1 | 250 | 313 | 0.0623 | 122.94 | 123.96 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997167 FT2 KU1B 230 1 | 250 | 313 | 0.0623 | 122.94 | 123.95 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997167 FT2 KU1B 230 1 | 250 | 313 | 0.0623 | 122.94 | 123.95 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997167 FT2 KU1B 230 1 | 250 | 313 | 0.06232 | 129.21 | 122.6 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997168 FT2 KU1A 230 1 | 250 | 313 | 0.06232 | 129.21 | 122.6 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997168 FT2 KU1A 230 1 | 250 | 313 | 0.06232 | 122.84 | 123.7 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997168 FT2 KU1A 230 1 | 250 | 313 | 0.0623 | 122.94 | 123.95 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997168 FT2 KU1A 230 1 | 250 | 313 | 0.0623 | 122.94 | 123.96 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997168 FT2 KU1A 230 1 | 250 | 313 | 0.0623 | 122.94 | 123.95 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997168 FT2 KU1A 230 1 | 250 | 313 | 0.0623 | 122.94 | 123.95 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997168 FT2 KU1A 230 1 | 250 | 313 | 0.06232 | 129.21 | 122.6 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 68.55 | 103.35 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 68.54 | 103.38 | P11:0:XEL:AUTO-SINGLE:G362GRDMDW:W
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 68.54 | 103.38 | P13:161-34:XEL:AUTO-SINGLE:GRNDMDOW5:GMFDR1:1
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 68.55 | 103.35 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.33 | 110.99 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.29 | 110.98 | P11:0:XEL:AUTO-SINGLE:G362GRDMDW:W
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.29 | 110.98 | P13:161-34:XEL:AUTO-SINGLE:GRNDMDOW5:GMFDR1:1
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.33 | 110.99 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 601001 FORBES 2 500 997688 FBS7ABC 230 1 | 672 | 672 | 0.05514 | 129.34 | 129.74 | P24:500:MP:FBS:601LX
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07381 | 104.15 | 105.05 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07378 | 104.2 | 105.1 | P23:345:OTP:BUFFALO3:3655:V2016
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07381 | 104.13 | 105.03 | P23:345:OTP:JAMESTN3:3145:V2020
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07381 | 104.13 | 105.03 | P23:345:OTP:JAMESTN3:3135:V2020
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07362 | 103.4 | 104.26 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
FDNS | Scenario 2 | 00NR | 20SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07381 | 104.15 | 105.05 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.1194 | 100.19 | 101.25 | P11:024:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.1194 | 100.19 | 101.25 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 720 | 720 | 0.11995 | 100.28 | 101.15 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06344 | 125.58 | 127.17 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06344 | 122.15 | 122.79 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06342 | 122.03 | 123.1 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06342 | 122.03 | 123.1 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06342 | 122.03 | 123.1 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06342 | 122.03 | 123.1 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06344 | 125.58 | 127.17 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06344 | 125.58 | 127.17 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06344 | 122.15 | 122.79 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06342 | 122.03 | 123.1 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06342 | 122.03 | 123.1 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06342 | 122.03 | 123.1 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06342 | 122.03 | 123.1 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06344 | 125.58 | 127.17 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06344 | 129.08 | 130.95 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06344 | 124.76 | 125.4 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06342 | 124.6 | 125.81 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06342 | 124.6 | 125.81 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06342 | 124.6 | 125.81 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06342 | 124.6 | 125.81 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06344 | 129.08 | 130.95 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06344 | 129.08 | 130.95 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06344 | 124.76 | 125.4 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06342 | 124.6 | 125.81 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06342 | 124.6 | 125.81 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06342 | 124.6 | 125.81 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06342 | 124.6 | 125.81 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06344 | 129.08 | 130.95 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z | 212 | 212 | 0.04609 | 109.9 | 110.87 | P12:345:UMZW:# 1681 #: WT2 IN SD. WT2-GRT BRANCH FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z | 212 | 212 | 0.04518 | 109.83 | 110.79 | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z | 212 | 212 | 0.04518 | 109.84 | 110.79 | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.1194 | 99.67 | 100.69 | P11:024:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.1194 | 99.67 | 100.69 | P11:345:UMZB:# 33 #: LRS IN WY. LARAMIE RIVER STATION 1
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 720 | 720 | 0.11995 | 99.75 | 100.6 | P45:345:UMZB:# 2507 #: LRS IN NE. LRS BUS FAULT
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07863 | 108.1 | 109.01 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07862 | 100.68 | 101.73 | P12:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07866 | 100.79 | 101.84 | P23:345:OTP:CENTER 3:3235
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07866 | 100.79 | 101.83 | P23:345:OTP:CENTER 3:3245
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07859 | 108.09 | 109.06 | P23:345:OTP:BUFFALO3:3655:V2016
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07863 | 100.7 | 101.73 | P23:345:OTP:JAMESTN3:3115:V2020
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07863 | 108.1 | 108.99 | P23:345:OTP:JAMESTN3:3145:V2020
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07863 | 100.72 | 101.76 | P23:345:OTP:JAMESTN3:3125:V2020
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07863 | 108.1 | 108.99 | P23:345:OTP:JAMESTN3:3135:V2020
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07843 | 105.89 | 106.62 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07862 | 108.1 | 109.01 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
FDNS | Scenario 2 | 00NR | 24SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07862 | 100.68 | 101.73 | P21:345:OTP:AUTO-SINGLE:JAMESTN3:CENTER3:1
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06191 | 111.97 | 112.66 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06191 | 111.36 | 112.15 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06189 | 111.39 | 112.14 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06189 | 111.39 | 112.14 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06189 | 111.39 | 112.14 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06189 | 111.39 | 112.14 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06191 | 111.97 | 112.66 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06191 | 111.97 | 112.66 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06191 | 111.36 | 112.15 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06189 | 111.39 | 112.14 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06189 | 111.39 | 112.14 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06189 | 111.39 | 112.14 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06189 | 111.39 | 112.14 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06191 | 111.97 | 112.66 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06191 | 114.25 | 114.96 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06191 | 113.53 | 114.33 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06189 | 113.55 | 114.32 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06189 | 113.55 | 114.32 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06189 | 113.55 | 114.32 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06189 | 113.55 | 114.32 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1B 230 1 | 250 | 313 | 0.06191 | 114.25 | 114.96 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06191 | 114.25 | 114.96 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06191 | 113.53 | 114.33 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06189 | 113.55 | 114.32 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06189 | 113.55 | 114.32 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06189 | 113.55 | 114.32 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06189 | 113.55 | 114.32 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 24WP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997160 FT2 KU1A 230 1 | 250 | 313 | 0.06191 | 114.25 | 114.96 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997158 FT2 KU1B 230 1 | 250 | 313 | 0.06352 | 122.08 | 123 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997158 FT2 KU1B 230 1 | 250 | 313 | 0.06352 | 119.91 | 120.64 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997158 FT2 KU1B 230 1 | 250 | 313 | 0.0635 | 119.97 | 120.65 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997158 FT2 KU1B 230 1 | 250 | 313 | 0.0635 | 119.97 | 120.65 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997158 FT2 KU1B 230 1 | 250 | 313 | 0.0635 | 119.97 | 120.65 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997158 FT2 KU1B 230 1 | 250 | 313 | 0.0635 | 119.97 | 120.65 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997158 FT2 KU1B 230 1 | 250 | 313 | 0.06352 | 122.08 | 123 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1A 230 1 | 250 | 313 | 0.06352 | 122.08 | 123 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1A 230 1 | 250 | 313 | 0.06352 | 119.91 | 120.64 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1A 230 1 | 250 | 313 | 0.0635 | 119.97 | 120.65 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1A 230 1 | 250 | 313 | 0.0635 | 119.97 | 120.65 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1A 230 1 | 250 | 313 | 0.0635 | 119.97 | 120.65 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1A 230 1 | 250 | 313 | 0.0635 | 119.97 | 120.65 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652506 FTTHOMP3 345 997159 FT2 KU1A 230 1 | 250 | 313 | 0.06352 | 122.08 | 123 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997158 FT2 KU1B 230 1 | 250 | 313 | 0.06352 | 125.13 | 126.14 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997158 FT2 KU1B 230 1 | 250 | 313 | 0.06352 | 122.43 | 123.18 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997158 FT2 KU1B 230 1 | 250 | 313 | 0.0635 | 122.49 | 123.19 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997158 FT2 KU1B 230 1 | 250 | 313 | 0.0635 | 122.49 | 123.19 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997158 FT2 KU1B 230 1 | 250 | 313 | 0.0635 | 122.49 | 123.19 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997158 FT2 KU1B 230 1 | 250 | 313 | 0.0635 | 122.49 | 123.19 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997158 FT2 KU1B 230 1 | 250 | 313 | 0.06352 | 125.13 | 126.14 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1A 230 1 | 250 | 313 | 0.06352 | 125.13 | 126.14 | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1A 230 1 | 250 | 313 | 0.06352 | 122.43 | 123.18 | P21:345:UMZW:# 2421 #: GI IN NE. GI-GILNX3 OPENED
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1A 230 1 | 250 | 313 | 0.0635 | 122.49 | 123.19 | P23:345:UMZW:# 2423 #: GI IN NE. GI 1596 BKR FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1A 230 1 | 250 | 313 | 0.0635 | 122.49 | 123.19 | P45:345:UMZW:# 1328 #: GI IN NE.
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1A 230 1 | 250 | 313 | 0.0635 | 122.49 | 123.19 | P23:345:UMZW:# 2425 #: GI IN NE. GI 1196 BKR FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1A 230 1 | 250 | 313 | 0.0635 | 122.49 | 123.19 | P23:345:UMZW:# 2426 #: GI IN NE. GI 1592 BKR FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652507 FTTHOMP4 230 997159 FT2 KU1A 230 1 | 250 | 313 | 0.06352 | 125.13 | 126.14 | P12:345:UMZ:# 6231 #: OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 OR 653571-653871-Z
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z | 212 | 212 | 0.04512 | 126.34 | 127.3 | P12:345:UMZW:# 1681 #: WT2 IN SD. WT2-GRT BRANCH FAULT
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z | 212 | 212 | 0.0442 | 126.44 | 127.38 | P23:345:UMZW:# 844 #: WT2 IN SD. BREAKER FAULT (7296)
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 652512 GROTON 7 115 652568 GROTONSOUTH7 115 Z | 212 | 212 | 0.0442 | 126.44 | 127.38 | P23:345:UMZW:# 845 #: WT2 IN SD. BREAKER FAULT (7192)
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 655840 CHRRYCRK-MK7 115 655841 ARNEGARD-MK7 115 1 | 125 | 125 | 1 | 68.13 | 103.2 | P13:230-34:MIDW:BUFFALO CREEK (PRW) 230-34 KV
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 655841 ARNEGARD-MK7 115 655887 E.HAY_BT-MK7 115 1 | 125 | 125 | 1 | 75.42 | 110.97 | P13:230-34:MIDW:BUFFALO CREEK (PRW) 230-34 KV
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07899 | 102.82 | 103.77 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07896 | 102.89 | 103.83 | P23:345:OTP:BUFFALO3:3655:V2016
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07899 | 102.8 | 103.75 | P23:345:OTP:JAMESTN3:3145:V2020
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07899 | 102.8 | 103.75 | P23:345:OTP:JAMESTN3:3135:V2020
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.0788 | 102.43 | 103.4 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
FDNS | Scenario 2 | 00NR | 29SP | GEN-2020-014 | 'FROM -> TO' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07899 | 102.82 | 103.77 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1

## All Voltage
SOLUTION | GROUP | SCENARIO | SEASON | SOURCE | MONITORED ELEMENT | BC Voltage (PU) | TC Voltage (PU) | Voltage Differ (PU) | VINIT (PU) | VMIN (PU) | VMAX(PU) | TDF | CONTINGENCY
FDNS | 00LVER | Scenario 1 | 24SP | GEN-2020-014 | GRE-RAMSEY 4 | 1.0061 | 1.0504 | 0.0443 | 1.0098 | 0.9 | 1.05 | 9999 | P23:345:MPC:PRAIRIE3:4440
FDNS | 00LVER | Scenario 1 | 24SP | GEN-2020-014 | GRE-BALTA 4 | 1.0256 | 1.0508 | 0.0252 | 1.0203 | 0.9 | 1.05 | 9999 | P23:345:MPC:CENTER 3:8810
FDNS | 00LVER | Scenario 1 | 24SP | GEN-2020-014 | GRE-BALTA 4 | 1.0256 | 1.0509 | 0.0253 | 1.0203 | 0.9 | 1.05 | 9999 | P23:345:MPC:CENTER 3:8820
FDNS | 00LVER | Scenario 1 | 24SP | GEN-2020-014 | GRE-BALTA 4 | 1.0305 | 1.0511 | 0.0206 | 1.0203 | 0.9 | 1.05 | 9999 | P23:345:MPC:PRAIRIE3:4440
FDNS | 00LVER | Scenario 1 | 24SP | GEN-2020-014 | GRE-RMSYCB14 | 1.0061 | 1.0504 | 0.0443 | 1.0098 | 0.9 | 1.05 | 9999 | P23:345:MPC:PRAIRIE3:4440
FDNS | 00LVER | Scenario 1 | 24SP | GEN-2020-014 | GRE-RMSYCB24 | 1.0061 | 1.0505 | 0.0444 | 1.0099 | 0.9 | 1.05 | 9999 | P23:345:MPC:PRAIRIE3:4440
FDNS | 00NR | Scenario 2 | 20SP | GEN-2020-014 | POSTROCK7 | 1.052 | 1.0519 | -0.0001 | 1.0519 | 0.9 | 1.05 | 0.06637 | P11:0:XEL:AUTO-SINGLE:G362GRDMDW:W
FDNS | 00NR | Scenario 2 | 20SP | GEN-2020-014 | POSTROCK7 | 1.052 | 1.0519 | -9e-05 | 1.0519 | 0.9 | 1.05 | 0.06637 | P13:161-34:XEL:AUTO-SINGLE:GRNDMDOW5:GMFDR1:1
FDNS | 00NR | Scenario 2 | 20SP | GEN-2020-014 | REDWILO3 | 1.0576 | 1.0574 | -0.00025 | 1.0574 | 0.9 | 1.05 | 0.06047 | P11:0:XEL:AUTO-SINGLE:G362GRDMDW:W
FDNS | 00NR | Scenario 2 | 20SP | GEN-2020-014 | REDWILO3 | 1.0576 | 1.0574 | -0.00025 | 1.0574 | 0.9 | 1.05 | 0.06047 | P13:161-34:XEL:AUTO-SINGLE:GRNDMDOW5:GMFDR1:1

## Stability Anaysis
Group | Season | Model Dispatch | Event ID | Event Description | Event Detailed Clearing Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping factor > 0.81633% | Fault Ride-through | Violation Summary | Primary Mitigation | Alternate Mitigation
16 | 19W | Normal | F01 | Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F02 | Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F03 | Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F04 | Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F05 | Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F06 | Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F07 | Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F08 | Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F09 | Apply 3PH ault near Watord City 230 kV on Watord City to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 230 kV on Watord City to Williston 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 27 cycles: Reclose Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 34 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F10 | Apply 3PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 27 cycles: Reclose Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 34 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F11 | Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Normal | F12 | Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Normal | F13 | Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F14 | Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F15 | Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Normal | F16 | Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Normal | F17 | Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P1 | Yes | Yes | No | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the generator tripping and high voltage issue were still observed. | No Mitigation
16 | 19W | Normal | F18 | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F19 | Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 6 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F20 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F21 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F22 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Mont 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 2 115 kV on Williston 2 to Mont 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 27 cycles: Reclose Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 34 cycles: Trip Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F23 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Little Muddy 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Little Muddy 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 27 cycles: Reclose Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 34 cycles: Trip Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Normal | F24 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to N.W. Williston 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 2 115 kV on Williston 2 to N.W. Williston 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 27 cycles: Reclose Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 34 cycles: Trip Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Normal | F25 | Apply 3PH ault near Williston 115 kV on Williston to airview West 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston115 kV on Williston to airview West 115 kV line 7 cycles: Trip Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 27 cycles: Reclose Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 34 cycles: Trip Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Normal | F26 | Apply 3PH ault near Williston 115 kV on Williston to Judson 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Judson 115 kV line 7 cycles: Trip Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 27 cycles: Reclose Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 34 cycles: Trip Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F27 | Apply 3PH ault near Judson 115 kV on Judson to Stateline 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Judson 115 kV on Judson 115 to Stateline 115 kV line 7 cycles: Trip Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 27 cycles: Reclose Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 34 cycles: Trip Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F28 | Apply 3PH ault near Judson 115 kV on Judson to SW.WLSTN-MW7 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Judson115 kV on Judson 115 to SW.WLSTN-MW7 115 kV line 7 cycles: Trip Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) 27 cycles: Reclose Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) 34 cycles: Trip Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F29 | Apply 3PH ault near Williston 115 kV on Williston to Marley 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Marley 115 kV line 7 cycles: Trip Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) 27 cycles: Reclose Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) 34 cycles: Trip Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Normal | F30 | Apply 3PH ault near Williston 115 kV on Williston to Culbertson 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Culbertson 115 kV line 7 cycles: Trip Williston 115 kV breaker 1562 and Culbertson Generatio Station 115 kV breaker 161 and Wol Point Breaker 262 27 cycles: Reclose Williston 115 kV breaker 1562 and Wol Point Breaker 262 34 cycles: Trip Williston 115 kV breaker 1562 and Wol Point Breaker 262 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Normal | F31 | Apply 3PH ault on Wheelock 230/115 kV Transormer #1, near Wheelock 230 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Wheelock 230/115 Transormer #1, near Wheelock 230 kV 7 cycles: Trip Wheelock 230 kV breakers 1486 and 1686 and Wheelock 115 kV breakers 6210 and 6260 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F32 | Apply 3PH ault near Wheelock 230 kV on Wheelock to Tioga 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Wheelock 230 kV on Wheelock to Tioga 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Normal | F33 | Apply 3PH ault on Patent Gate 345/115 kV Transormer #1, near Patent Gate 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Patent Gate 345/115 kV Transormer #1, near Patent Gate 345 kV or 6 cycles 6 cycles: Trip Patent Gate 345 kV breakers 1696 and 1792 7 cycles: Trip Patent Gate 115 kV breakers 166 and 262 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F34 | Apply 3PH ault on Patent Gate 345/115 kV Transormer #2, near Patent Gate 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Patent Gate 345/115 kV Transormer #2, near Patent Gate 345 kV or 6 cycles 6 cycles: Trip Patent Gate 345 kV breakers 1896 and 1992 7 cycles: Trip Patent Gate 115 kV breakers 366 and 462 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F35 | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Kummer Ridge 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Kummer Ridge 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 26 cycles: Reclose Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 32 cycles: Trip Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Normal | F36 | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 6 cycles 6 cycles: Trip Kummer Ridge 345 kV breakers 192 and 592 7 cycles: Trip Kummer Ridge 115 kV breakers 362 and 366 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F37 | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #2, near Kummer Ridge 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 6 cycles 6 cycles: Trip Kummer Ridge 345 kV breakers 596 and 692 7 cycles: Trip Kummer Ridge 115 kV breakers 162 and 166 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F38 | Apply 3PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to GEN-2015-046 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near TANDE___-BE3 345 kV on TANDE to GEN-2015-046 345 kV line 6 cycles: Trip TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers 26 cycles: Reclose TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers 32 cycles: Trip TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F39 | Apply 3PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to BURKE___-PP3 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to BURKE___-PP3 345 kV line 6 cycles: Trip TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers 26 cycles: Reclose TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers 32 cycles: Trip TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Normal | F40 | Apply 3PH ault on TANDE 345/230 kV Transormer, near TANDE 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on TANDE 345/230 kV Transormer, near TANDE 345 kV 6 cycles: Trip TANDE 345 kV breakers 7 cycles: Trip TANDE 230 kV breakers | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage on the 345 kV network near the TANDE substation was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the high voltage issue was still observed. | No Mitigation
16 | 19W | Normal | F41 | Apply 3PH ault on G15-046 345/34.5 kV Transormer #1, near G15-046 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on G15-046 345/34.5 kV Transormer #1, near G15-046 345 kV 6 cycles: Trip G15-046 345 kV breakers 7 cycles: Trip G15-046 34.5 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Normal | F42 | Apply 3PH ault on G15-046 345/34.5 kV Transormer #2, near G15-046 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on G15-046 345/34.5 kV Transormer #2, near G15-046 345 kV 6 cycles: Trip G15-046 345 kV breakers 7 cycles: Trip G15-046 34.5 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Normal | F43 | Apply 3PH ault on Charlie Creek 345/115 kV Transormer, near Charlie Creek 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Charlie Creek 345/115 kV Transormer, near Charlie Creek 345 kV 6 cycles: Trip Charlie Creek 345 kV breakers 3896 and 3992 7 cycles :Trip Charlie Creek 115 kV breaker 962 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F44 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Roundup 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Roundup 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 26 cycles: Reclose Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 32 cycles: Trip Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F45 | Apply 3PH ault on Belield 345/230 kV Transormer #1, near Belield 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Belield 345/230 kV Transormer #1, near Belield 345 kV 6 cycles: Trip Belield 345 kV breakers 292 and 396 7 cycles: Trip Belield 230 kV breakers 1282 and 1482 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F46 | Apply 3PH ault on Belield 345/230 kV Transormer #2, near Belield 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Belield 345/230 kV Transormer #2, near Belield 345 kV 6 cycles: Trip Belield 345 kV breakers 292 and 492 7 cycles: Trip Belield 230 kV breakers 1382 and 1582 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F47 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Roundup 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Roundup 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 26 cycles: Reclose Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 32 cycles: Trip Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F48 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Coteau (RREC) 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Coteau (RREC) 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4592, Coteau breakers 27122, 2112 26 cycles: Reclose Antelope Valley 345 kV breakers 4596 and 4592 32 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4592 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F49 | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #1, near Antelope Valley 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #1, near Antelope Valley 345 kV 6 cycles: Trip Antelope Valley 345 kV breakers 4192 and 4196 7 cycles: Trip Antelope Valley 23 kV breaker | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F50 | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #2, near Antelope Valley 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #2, near Antelope Valley 345 kV 6 cycles: Trip Antelope Valley 345 kV breakers 4392 and 4396 7 cycles: Trip Antelope Valley 23 kV breaker | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F51 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #1 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #1 6 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 7 cycles: Trip Great Plains breakers 128, 228,328, 428, 528, 628, 728 26 cycles: Reclose Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 32 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F52 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #2 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #2 6 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 7 cycles: Trip Great Plains breakers 128, 228,328, 428, 528, 628, 728 26 cycles: Reclose Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 32 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F53 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Broadland 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Broadland 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 26 cycles: Reclose Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 32 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection off the plots showed a undamped response. Fault was tested with GEN-2020-014 offline and the undamped response was still observed. | No Mitigation
16 | 19W | Normal | F54 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #1 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #1 6 cycles: Trip Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 26 cycles: Reclose Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 32 cycles: Trip Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F55 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #2 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #2 6 cycles: Trip Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 26 cycles: Reclose Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 32 cycles: Trip Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F56 | Apply SLG ault near East Haybutte 115 kV with stuck breaker, cleared by opening the Lonesome Creek Switchyard to Cherry Creek 115 kV line, and opening the Lonesome Creek Switchyard to Lonesome Creek 115 kV line. | Apply SLG ault near East Haybutte 115 kV with Lonesome Creek Switchyard 115 kV breaker 1466 stuck 7 cycles: Trip Cherry Creek 115 kV breakers CB2 and CB3 and Lonesome Creek 115 kV breaker 1462 16 cycles: Trip Lonesome Creek Switchyard 115 kV breaker 1562. Trip Lonesome Creek generators 4, 5, and 6 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F57 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Roosevelt 115 kV line, and opening the Cherry Creek to Lonesome Creek Switchyard 115 kV line. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB3 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB4 16 cycles: Trip Cherry Creek 115 kV breaker CB2 and Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F58 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Roosevelt 115 kV line, and opening the Cherry Creek 25 kV load. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB4 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB3 16 cycles: Trip Cherry Creek 115 kV breaker CB1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F59 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Watord City 115 kV line, and opening the Cherry Creek to Lonesome Creek Switchyard 115 kV line. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB2 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB1 and Watord City 115 kV breakers 1362 and 1462 16 cycles: Trip Cherry Creek 115 kV breaker CB3 and Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F60 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Watord City 115 kV line, and opening the Cherry Creek 25 kV load. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB1 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB2 and Watord City 115 kV breakers 1362 and 1462 16 cycles: Trip Cherry Creek 115 kV breaker CB4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F61 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Coyote Charlie 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. opening the Watord City to Oasis 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1162 stuck 7 cycles: Trip Watord City 115 kV breaker 1262, Coyote Charlie 115 kV breakers 16 cycles: Trip Watord City 115 kV breakers 1062 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F62 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Coyote Charlie 115 kV line, and opening the Watord City 34.5 kV load. opening the Watord City 115 kV 15 MVAR Cap Bank. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1262 stuck 7 cycles: Trip Watord City 115 kV breaker 1162, Coyote Charlie 115 kV breakers 16 cycles: Trip Watord City 115 kV breaker 1362 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F63 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Garden Creek 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1062 stuck 7 cycles: Trip Watord City 115 kV breaker 1562, Garden Creek 115 kV breakers 16 cycles: Trip Watord City 115 kV breakers 1162 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F64 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Garden Creek 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. opening the Watord City 115 kV 15 MVAR Cap Bank. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1562 stuck 7 cycles: Trip Watord City 115 kV breaker 1062, Garden Creek 115 kV breakers 16 cycles: Trip Watord City 115 kV breaker 1462 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F65 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #1, and opening the Watord City 230/115 kV Transormer #2 opening the Watord City 115 kV 15 MVAR Cap Bank. opening the Watord City to Garden Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1062 stuck 7 cycles: Trip Watord City 115 kV breaker 1162 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breakers 1562, Garden Creek 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F66 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #1, and opening the Watord City 230/115 kV Transormer #2. opening the Watord City to Coyote Charlie 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1162 stuck 7 cycles: Trip Watord City 115 kV breakers 1062 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1262, Coyote Charlie 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F67 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #2, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City to Cherry Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1462 stuck 7 cycles: Trip Watord City 115 kV breakers 1562 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1362 and Cherry Creek 115 kV breakers CB1 and CB2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F68 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #2, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City to Garden Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1562 stuck 7 cycles: Trip Watord City 115 kV breaker 1462 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1062 , Garden Creek 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F69 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Williston 230 kV line | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 682 stuck 7 cycles: Trip Watord City 230 kV breaker 782 and Williston 230 kV breakers 382 and 486 16 cycles: Trip Watord City 230 kV breaker 982 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F70 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Williston 230 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 782 stuck 7 cycles: Trip Watord City 230 kV breaker 682 and Williston 230 kV breakers 382 and 486 16 cycles: Trip Watord City 230 kV breaker 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F71 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Charlie Creek 230 kV line | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 982 stuck 7 cycles: Trip Watord City 230 kV breaker 882 and Charlie Creek 230 kV breakers 282 and 382 16 cycles: Trip Watord City 230 kV breaker 682 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F72 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Charlie Creek 230 kV line, and opening the Watord City 230/115 kV Transormer #1 opening the Watord City 230/115 kV Transormer #2 | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 882 stuck 7 cycles: Trip Watord City 230 kV breaker 982 and Charlie Creek 230 kV breakers 282 and 382 16 cycles: Trip Watord City 230 kV breaker 782 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F73 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #1, and tripping the Williston 230 kV East Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 182 stuck 7 cycles: Trip Williston 230 kV breaker 286 and Williston 115 kV breakers 2162 and 2266 16 cycles: Trip Williston 230 kV breaker 382 and 582 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F74 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #1, and opening the Williston to Judson 230 kV line. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 286 stuck 7 cycles: Trip Williston 230 kV breaker 182 and Williston 115 kV breakers 2162 and 2266 16 cycles: Trip Williston 230 kV breaker 282 and Judson breakers 1082 and 1182 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F75 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #2, and tripping the Williston 230 kV West Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 482 stuck 7 cycles: Trip Williston 230 kV breaker 486 and Williston 115 kV breaker 1762 16 cycles: Trip Williston 230 kV breakers 282 and 686 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F76 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #2, and opening the Williston to Watord City 230 kV line. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 486 stuck 7 cycles: Trip Williston 230 kV breaker 482 and Williston 115 kV breaker 1762 16 cycles: Trip Williston 230 kV breaker 382 and Watord City 230 kV breakers 682 and 782 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F77 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Judson 230 kV line, and tripping the Williston 230 kV West Bus | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 282 stuck 7 cycles: Trip Williston 230 kV breaker 286 and Judson 230 kV breakers 1082 and 1182 16 cycles: Trip Williston 230 kV breakers 482 and 686 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F78 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Judson 230 kV line, and opening the Williston 230/115 kV Transormer #1 | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 286 stuck 7 cycles: Trip Williston 230 kV breaker 282 and Judson 230 kV breakers 1082 and 1182 16 cycles: Trip Williston 230 kV breaker 182 and Williston 115 kV breakers 2162 and 2266 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F79 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Wheelock 230 kV line, and tripping the Williston 230 kV East Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 582 stuck 7 cycles: Trip Williston 230 kV breaker 686 and Wheelock 230 kV breakers 1482 and 1486 16 cycles: Trip Williston 230 kV breakers 382 and 182 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F80 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Wheelock 230 kV line, and tripping the Williston 230 kV West Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 686 stuck 7 cycles: Trip Williston 230 kV breaker 582 and Wheelock 230 kV breakers 1482 and 1486 16 cycles: Trip Williston 230 kV breakers 482 and 282 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F81 | Apply SLG ault near Judson 230 kV with stuck breaker, cleared by opening the Judson 230/345 kV Transormer #1, and opening the Judson to Williston 230 kV line. | Apply SLG ault near Judson 230 kV with Judson 230 kV breaker 1082 stuck 6 cycles: Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breaker 1282 16 cycles: Trip Judson 230 kV breaker 1182 and Williston 230 kV breakers 282 and 286 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F82 | Apply SLG ault near Judson 230 kV with stuck breaker, cleared by opening the Judson 230/345 kV Transormer #1, and opening the Judson to Williston 230 kV line. | Apply SLG ault near Judson 230 kV with Judson 230 kV breaker 1282 stuck 6 cycles: Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breaker 1082 16 cycles: Trip Judson 230 kV breaker 1382 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F83 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to Patent Gate 345 kV line #1, and tripping the Judson 345 kV West Bus | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 496 stuck 6 cycles: Trip Judson 345 kV breaker 492 and Patent Gate 345 kV breakers 1492 and 1496 16 cycles: Trip Judson 345 kV breakers 592 and 192 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F84 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to Patent Gate 345 kV line #1, and tripping the Judson 345 kV East Bus | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 492 stuck 6 cycles: Trip Judson 345 kV breaker 496 and Patent Gate 345 kV breakers 1492 and 1496 16 cycles: Trip Judson 345 kV breakers 692 and 292 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F85 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to TN.LS-JD-BE3 345 kV line, and tripping the Judson 345kV East Bus. | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 292 stuck 6 cycles: Trip Judson 345 kV breaker 296 and TANDE 345 kV breakers 16 cycles: Trip Judson 345 kV breakers 492 and 692 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F86 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to TN.LS-JD-BE3 345 kV line | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 296 stuck 6 cycles: Trip Judson 345 kV breaker 292 and TANDE 345 kV breakers 16 cycles: Trip Judson 345 kV breaker 192 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F87 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Patent Gate 345 kV line, and tripping the Charlie Creek 345 kV West Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3792 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3696 and Patent Gate 345 kV breakers 1892 and 1896 16 cycles: Trip Charlie Creek 345 kV breakers 3992 and 4192 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F88 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Patent Gate 345 kV line, and opening the Charlie Creek to Roundup 345 kV line. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3696 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3792 and Patent Gate 345 kV breakers 1892 and 1896 16 cycles: Trip Charlie Creek 345 kV breaker 3692 and Roundup 345 kV breakers 892 and 896 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F89 | Apply SLG ault near Charlie Creek 230 kV with stuck breaker, cleared by opening Charlie Creek 345/230 kV Transormers #1 and #2, and opening the Charlie Creek to Watord City 230 kV line. | Apply SLG ault near Charlie Creek 230 kV with Charlie Creek 230 kV breaker 382 stuck 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4092 7 cycles: Trip Charlie Creek 230 kV breaker 282 16 cycles: Trip Watord City 230 kV breakers 682 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F90 | Apply SLG ault near Charlie Creek 230 kV with stuck breaker, cleared by opening Charlie Creek 345/230 kV Transormers #1 and #2, and opening the Charlie Creek to Watord City 230 kV line. | Apply SLG ault near Charlie Creek 230 kV with Charlie Creek 230 kV breaker 282 stuck 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4092 7 cycles: Trip Charlie Creek 230 kV breaker 382 16 cycles: Trip Watord City 230 kV breakers 682 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F91 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Belield 345 kV line, and tripping the Charlie Creek 345 kV West Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 4192 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 4096 and Belield 345 kV breakers 396 and 492 16 cycles: Trip Charlie Creek 345 kV breakers 3792 and 3992 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F92 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Belield 345 kV line, and opening the Charlie Creek 345/230 kV Transormer #1. opening the Charlie Creek 345/230 kV Transormer #2. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 4096 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 4192 and Belield 345 kV breakers 396 and 492 16 cycles: Trip Charlie Creek 345 kV breaker 4092 and Charlie Creek 230 kV breakers 282 and 382 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F93 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Antelope Valley 345 kV line, and tripping the Charlie Creek 345 kV East Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3892 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3896 and Antelope Valley 345 kV breakers 4796 and 4892 16 cycles: Trip Charlie Creek 345 kV breakers 3692 and 4092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F94 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Antelope Valley 345 kV line, and opening the Charlie Creek 345/115 kV Transormer #1. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3896 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3892 and Antelope Valley 345 kV breakers 4796 and 4892 16 cycles: Trip Charlie Creek 345 kV breaker 3992 and Charlie Creek 115 kV breaker 962 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F95 | Prior Outage o Watord City to Williston Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F96 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F97 | Prior Outage o Watord City to Williston Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Prior Outage o Watord City to Williston Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F98 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F99 | Prior Outage o Watord City to Williston Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F100 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Normal | F101 | Prior Outage o Watord City to Williston Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F102 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F103 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F104 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F105 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F106 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Normal | F107 | Prior Outage o Watord City to Williston Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F108 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F109 | Prior Outage o Watord City to Williston Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F110 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F111 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 230 kV on Watord City to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 230 kV on Watord City to Williston 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 27 cycles: Reclose Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 34 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F112 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 27 cycles: Reclose Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 34 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F113 | Prior Outage o Watord City to Williston Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F114 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F115 | Prior Outage o Watord City to Williston Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F116 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F117 | Prior Outage o Watord City to Williston Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F118 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F119 | Prior Outage o Watord City to Williston Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F120 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F121 | Prior Outage o Watord City to Williston Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Normal | F122 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Normal | F123 | Prior Outage o Watord City to Williston Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P6 | Yes | Yes | No | Yes | Yes | No | Yes | Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the high voltage issue was still observed. Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection off the plots showed a well-damped response. | No Mitigation
16 | 19W | Normal | F124 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Normal | F125 | Prior Outage o Watord City to Williston Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P6 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the high voltage issue was still observed. | No Mitigation
16 | 19W | Normal | F126 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P6 | Yes | Yes | No | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the generator tripping and high voltage issue were still observed. | No Mitigation
16 | 19W | Normal | F127 | Prior Outage o Watord City to Williston Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F128 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F129 | Prior Outage o Watord City to Williston Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F130 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F131 | Prior Outage o Watord City to Williston Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F132 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F133 | Prior Outage o Watord City to Williston Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Normal | F134 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F01 | Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F02 | Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F03 | Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F04 | Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F05 | Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F06 | Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F07 | Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F08 | Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F09 | Apply 3PH ault near Watord City 230 kV on Watord City to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 230 kV on Watord City to Williston 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 27 cycles: Reclose Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 34 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F10 | Apply 3PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 27 cycles: Reclose Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 34 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F11 | Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F12 | Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F13 | Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F14 | Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F15 | Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F16 | Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F17 | Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Voltage of GEN-2015-046 and BURKE 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the high voltage issue was still observed. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection off the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F18 | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F19 | Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 6 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F20 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F21 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F22 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Mont 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 2 115 kV on Williston 2 to Mont 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 27 cycles: Reclose Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 34 cycles: Trip Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F23 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Little Muddy 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Little Muddy 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 27 cycles: Reclose Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 34 cycles: Trip Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F24 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to N.W. Williston 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 2 115 kV on Williston 2 to N.W. Williston 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 27 cycles: Reclose Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 34 cycles: Trip Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F25 | Apply 3PH ault near Williston 115 kV on Williston to airview West 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston115 kV on Williston to airview West 115 kV line 7 cycles: Trip Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 27 cycles: Reclose Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 34 cycles: Trip Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F26 | Apply 3PH ault near Williston 115 kV on Williston to Judson 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Judson 115 kV line 7 cycles: Trip Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 27 cycles: Reclose Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 34 cycles: Trip Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F27 | Apply 3PH ault near Judson 115 kV on Judson to Stateline 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Judson 115 kV on Judson 115 to Stateline 115 kV line 7 cycles: Trip Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 27 cycles: Reclose Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 34 cycles: Trip Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F28 | Apply 3PH ault near Judson 115 kV on Judson to SW.WLSTN-MW7 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Judson115 kV on Judson 115 to SW.WLSTN-MW7 115 kV line 7 cycles: Trip Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) 27 cycles: Reclose Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) 34 cycles: Trip Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F29 | Apply 3PH ault near Williston 115 kV on Williston to Marley 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Marley 115 kV line 7 cycles: Trip Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) 27 cycles: Reclose Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) 34 cycles: Trip Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F30 | Apply 3PH ault near Williston 115 kV on Williston to Culbertson 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Culbertson 115 kV line 7 cycles: Trip Williston 115 kV breaker 1562 and Culbertson Generatio Station 115 kV breaker 161 and Wol Point Breaker 262 27 cycles: Reclose Williston 115 kV breaker 1562 and Wol Point Breaker 262 34 cycles: Trip Williston 115 kV breaker 1562 and Wol Point Breaker 262 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F31 | Apply 3PH ault on Wheelock 230/115 kV Transormer #1, near Wheelock 230 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Wheelock 230/115 Transormer #1, near Wheelock 230 kV 7 cycles: Trip Wheelock 230 kV breakers 1486 and 1686 and Wheelock 115 kV breakers 6210 and 6260 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F32 | Apply 3PH ault near Wheelock 230 kV on Wheelock to Tioga 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Wheelock 230 kV on Wheelock to Tioga 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F33 | Apply 3PH ault on Patent Gate 345/115 kV Transormer #1, near Patent Gate 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Patent Gate 345/115 kV Transormer #1, near Patent Gate 345 kV or 6 cycles 6 cycles: Trip Patent Gate 345 kV breakers 1696 and 1792 7 cycles: Trip Patent Gate 115 kV breakers 166 and 262 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F34 | Apply 3PH ault on Patent Gate 345/115 kV Transormer #2, near Patent Gate 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Patent Gate 345/115 kV Transormer #2, near Patent Gate 345 kV or 6 cycles 6 cycles: Trip Patent Gate 345 kV breakers 1896 and 1992 7 cycles: Trip Patent Gate 115 kV breakers 366 and 462 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F35 | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Kummer Ridge 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Kummer Ridge 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 26 cycles: Reclose Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 32 cycles: Trip Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F36 | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 6 cycles 6 cycles: Trip Kummer Ridge 345 kV breakers 192 and 592 7 cycles: Trip Kummer Ridge 115 kV breakers 362 and 366 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F37 | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #2, near Kummer Ridge 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 6 cycles 6 cycles: Trip Kummer Ridge 345 kV breakers 596 and 692 7 cycles: Trip Kummer Ridge 115 kV breakers 162 and 166 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F38 | Apply 3PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to GEN-2015-046 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near TANDE___-BE3 345 kV on TANDE to GEN-2015-046 345 kV line 6 cycles: Trip TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers 26 cycles: Reclose TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers 32 cycles: Trip TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F39 | Apply 3PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to BURKE___-PP3 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to BURKE___-PP3 345 kV line 6 cycles: Trip TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers 26 cycles: Reclose TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers 32 cycles: Trip TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2015-046 generators tripped due to overvoltage relay (>1,2 p.u.). The overvoltage relay setting met PRC-024-2 requirement for voltage higher than 1.2 p.u. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 21L | Normal | F40 | Apply 3PH ault on TANDE 345/230 kV Transormer, near TANDE 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on TANDE 345/230 kV Transormer, near TANDE 345 kV 6 cycles: Trip TANDE 345 kV breakers 7 cycles: Trip TANDE 230 kV breakers | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Voltage on the 345 kV network near the TANDE substation was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the high voltage issue was still observed. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection off the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F41 | Apply 3PH ault on G15-046 345/34.5 kV Transormer #1, near G15-046 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on G15-046 345/34.5 kV Transormer #1, near G15-046 345 kV 6 cycles: Trip G15-046 345 kV breakers 7 cycles: Trip G15-046 34.5 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F42 | Apply 3PH ault on G15-046 345/34.5 kV Transormer #2, near G15-046 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on G15-046 345/34.5 kV Transormer #2, near G15-046 345 kV 6 cycles: Trip G15-046 345 kV breakers 7 cycles: Trip G15-046 34.5 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F43 | Apply 3PH ault on Charlie Creek 345/115 kV Transormer, near Charlie Creek 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Charlie Creek 345/115 kV Transormer, near Charlie Creek 345 kV 6 cycles: Trip Charlie Creek 345 kV breakers 3896 and 3992 7 cycles :Trip Charlie Creek 115 kV breaker 962 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F44 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Roundup 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Roundup 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 26 cycles: Reclose Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 32 cycles: Trip Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F45 | Apply 3PH ault on Belield 345/230 kV Transormer #1, near Belield 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Belield 345/230 kV Transormer #1, near Belield 345 kV 6 cycles: Trip Belield 345 kV breakers 292 and 396 7 cycles: Trip Belield 230 kV breakers 1282 and 1482 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F46 | Apply 3PH ault on Belield 345/230 kV Transormer #2, near Belield 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Belield 345/230 kV Transormer #2, near Belield 345 kV 6 cycles: Trip Belield 345 kV breakers 292 and 492 7 cycles: Trip Belield 230 kV breakers 1382 and 1582 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F47 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Roundup 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Roundup 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 26 cycles: Reclose Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 32 cycles: Trip Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F48 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Coteau (RREC) 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Coteau (RREC) 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4592, Coteau breakers 27122, 2112 26 cycles: Reclose Antelope Valley 345 kV breakers 4596 and 4592 32 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4592 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F49 | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #1, near Antelope Valley 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #1, near Antelope Valley 345 kV 6 cycles: Trip Antelope Valley 345 kV breakers 4192 and 4196 7 cycles: Trip Antelope Valley 23 kV breaker | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F50 | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #2, near Antelope Valley 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #2, near Antelope Valley 345 kV 6 cycles: Trip Antelope Valley 345 kV breakers 4392 and 4396 7 cycles: Trip Antelope Valley 23 kV breaker | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F51 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #1 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #1 6 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 7 cycles: Trip Great Plains breakers 128, 228,328, 428, 528, 628, 728 26 cycles: Reclose Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 32 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F52 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #2 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #2 6 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 7 cycles: Trip Great Plains breakers 128, 228,328, 428, 528, 628, 728 26 cycles: Reclose Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 32 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F53 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Broadland 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Broadland 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 26 cycles: Reclose Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 32 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F54 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #1 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #1 6 cycles: Trip Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 26 cycles: Reclose Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 32 cycles: Trip Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F55 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #2 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #2 6 cycles: Trip Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 26 cycles: Reclose Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 32 cycles: Trip Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F56 | Apply SLG ault near East Haybutte 115 kV with stuck breaker, cleared by opening the Lonesome Creek Switchyard to Cherry Creek 115 kV line, and opening the Lonesome Creek Switchyard to Lonesome Creek 115 kV line. | Apply SLG ault near East Haybutte 115 kV with Lonesome Creek Switchyard 115 kV breaker 1466 stuck 7 cycles: Trip Cherry Creek 115 kV breakers CB2 and CB3 and Lonesome Creek 115 kV breaker 1462 16 cycles: Trip Lonesome Creek Switchyard 115 kV breaker 1562. Trip Lonesome Creek generators 4, 5, and 6 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F57 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Roosevelt 115 kV line, and opening the Cherry Creek to Lonesome Creek Switchyard 115 kV line. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB3 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB4 16 cycles: Trip Cherry Creek 115 kV breaker CB2 and Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F58 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Roosevelt 115 kV line, and opening the Cherry Creek 25 kV load. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB4 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB3 16 cycles: Trip Cherry Creek 115 kV breaker CB1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F59 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Watord City 115 kV line, and opening the Cherry Creek to Lonesome Creek Switchyard 115 kV line. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB2 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB1 and Watord City 115 kV breakers 1362 and 1462 16 cycles: Trip Cherry Creek 115 kV breaker CB3 and Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F60 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Watord City 115 kV line, and opening the Cherry Creek 25 kV load. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB1 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB2 and Watord City 115 kV breakers 1362 and 1462 16 cycles: Trip Cherry Creek 115 kV breaker CB4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F61 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Coyote Charlie 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. opening the Watord City to Oasis 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1162 stuck 7 cycles: Trip Watord City 115 kV breaker 1262, Coyote Charlie 115 kV breakers 16 cycles: Trip Watord City 115 kV breakers 1062 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F62 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Coyote Charlie 115 kV line, and opening the Watord City 34.5 kV load. opening the Watord City 115 kV 15 MVAR Cap Bank. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1262 stuck 7 cycles: Trip Watord City 115 kV breaker 1162, Coyote Charlie 115 kV breakers 16 cycles: Trip Watord City 115 kV breaker 1362 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F63 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Garden Creek 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1062 stuck 7 cycles: Trip Watord City 115 kV breaker 1562, Garden Creek 115 kV breakers 16 cycles: Trip Watord City 115 kV breakers 1162 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F64 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Garden Creek 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. opening the Watord City 115 kV 15 MVAR Cap Bank. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1562 stuck 7 cycles: Trip Watord City 115 kV breaker 1062, Garden Creek 115 kV breakers 16 cycles: Trip Watord City 115 kV breaker 1462 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F65 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #1, and opening the Watord City 230/115 kV Transormer #2 opening the Watord City 115 kV 15 MVAR Cap Bank. opening the Watord City to Garden Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1062 stuck 7 cycles: Trip Watord City 115 kV breaker 1162 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breakers 1562, Garden Creek 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F66 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #1, and opening the Watord City 230/115 kV Transormer #2. opening the Watord City to Coyote Charlie 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1162 stuck 7 cycles: Trip Watord City 115 kV breakers 1062 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1262, Coyote Charlie 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F67 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #2, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City to Cherry Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1462 stuck 7 cycles: Trip Watord City 115 kV breakers 1562 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1362 and Cherry Creek 115 kV breakers CB1 and CB2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F68 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #2, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City to Garden Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1562 stuck 7 cycles: Trip Watord City 115 kV breaker 1462 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1062 , Garden Creek 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F69 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Williston 230 kV line | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 682 stuck 7 cycles: Trip Watord City 230 kV breaker 782 and Williston 230 kV breakers 382 and 486 16 cycles: Trip Watord City 230 kV breaker 982 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F70 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Williston 230 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 782 stuck 7 cycles: Trip Watord City 230 kV breaker 682 and Williston 230 kV breakers 382 and 486 16 cycles: Trip Watord City 230 kV breaker 882 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F71 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Charlie Creek 230 kV line | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 982 stuck 7 cycles: Trip Watord City 230 kV breaker 882 and Charlie Creek 230 kV breakers 282 and 382 16 cycles: Trip Watord City 230 kV breaker 682 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F72 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Charlie Creek 230 kV line, and opening the Watord City 230/115 kV Transormer #1 opening the Watord City 230/115 kV Transormer #2 | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 882 stuck 7 cycles: Trip Watord City 230 kV breaker 982 and Charlie Creek 230 kV breakers 282 and 382 16 cycles: Trip Watord City 230 kV breaker 782 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F73 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #1, and tripping the Williston 230 kV East Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 182 stuck 7 cycles: Trip Williston 230 kV breaker 286 and Williston 115 kV breakers 2162 and 2266 16 cycles: Trip Williston 230 kV breaker 382 and 582 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F74 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #1, and opening the Williston to Judson 230 kV line. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 286 stuck 7 cycles: Trip Williston 230 kV breaker 182 and Williston 115 kV breakers 2162 and 2266 16 cycles: Trip Williston 230 kV breaker 282 and Judson breakers 1082 and 1182 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F75 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #2, and tripping the Williston 230 kV West Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 482 stuck 7 cycles: Trip Williston 230 kV breaker 486 and Williston 115 kV breaker 1762 16 cycles: Trip Williston 230 kV breakers 282 and 686 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F76 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #2, and opening the Williston to Watord City 230 kV line. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 486 stuck 7 cycles: Trip Williston 230 kV breaker 482 and Williston 115 kV breaker 1762 16 cycles: Trip Williston 230 kV breaker 382 and Watord City 230 kV breakers 682 and 782 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F77 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Judson 230 kV line, and tripping the Williston 230 kV West Bus | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 282 stuck 7 cycles: Trip Williston 230 kV breaker 286 and Judson 230 kV breakers 1082 and 1182 16 cycles: Trip Williston 230 kV breakers 482 and 686 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F78 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Judson 230 kV line, and opening the Williston 230/115 kV Transormer #1 | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 286 stuck 7 cycles: Trip Williston 230 kV breaker 282 and Judson 230 kV breakers 1082 and 1182 16 cycles: Trip Williston 230 kV breaker 182 and Williston 115 kV breakers 2162 and 2266 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F79 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Wheelock 230 kV line, and tripping the Williston 230 kV East Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 582 stuck 7 cycles: Trip Williston 230 kV breaker 686 and Wheelock 230 kV breakers 1482 and 1486 16 cycles: Trip Williston 230 kV breakers 382 and 182 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F80 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Wheelock 230 kV line, and tripping the Williston 230 kV West Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 686 stuck 7 cycles: Trip Williston 230 kV breaker 582 and Wheelock 230 kV breakers 1482 and 1486 16 cycles: Trip Williston 230 kV breakers 482 and 282 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F81 | Apply SLG ault near Judson 230 kV with stuck breaker, cleared by opening the Judson 230/345 kV Transormer #1, and opening the Judson to Williston 230 kV line. | Apply SLG ault near Judson 230 kV with Judson 230 kV breaker 1082 stuck 6 cycles: Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breaker 1282 16 cycles: Trip Judson 230 kV breaker 1182 and Williston 230 kV breakers 282 and 286 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F82 | Apply SLG ault near Judson 230 kV with stuck breaker, cleared by opening the Judson 230/345 kV Transormer #1, and opening the Judson to Williston 230 kV line. | Apply SLG ault near Judson 230 kV with Judson 230 kV breaker 1282 stuck 6 cycles: Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breaker 1082 16 cycles: Trip Judson 230 kV breaker 1382 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F83 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to Patent Gate 345 kV line #1, and tripping the Judson 345 kV West Bus | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 496 stuck 6 cycles: Trip Judson 345 kV breaker 492 and Patent Gate 345 kV breakers 1492 and 1496 16 cycles: Trip Judson 345 kV breakers 592 and 192 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F84 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to Patent Gate 345 kV line #1, and tripping the Judson 345 kV East Bus | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 492 stuck 6 cycles: Trip Judson 345 kV breaker 496 and Patent Gate 345 kV breakers 1492 and 1496 16 cycles: Trip Judson 345 kV breakers 692 and 292 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F85 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to TN.LS-JD-BE3 345 kV line, and tripping the Judson 345kV East Bus. | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 292 stuck 6 cycles: Trip Judson 345 kV breaker 296 and TANDE 345 kV breakers 16 cycles: Trip Judson 345 kV breakers 492 and 692 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F86 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to TN.LS-JD-BE3 345 kV line | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 296 stuck 6 cycles: Trip Judson 345 kV breaker 292 and TANDE 345 kV breakers 16 cycles: Trip Judson 345 kV breaker 192 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F87 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Patent Gate 345 kV line, and tripping the Charlie Creek 345 kV West Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3792 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3696 and Patent Gate 345 kV breakers 1892 and 1896 16 cycles: Trip Charlie Creek 345 kV breakers 3992 and 4192 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F88 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Patent Gate 345 kV line, and opening the Charlie Creek to Roundup 345 kV line. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3696 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3792 and Patent Gate 345 kV breakers 1892 and 1896 16 cycles: Trip Charlie Creek 345 kV breaker 3692 and Roundup 345 kV breakers 892 and 896 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F89 | Apply SLG ault near Charlie Creek 230 kV with stuck breaker, cleared by opening Charlie Creek 345/230 kV Transormers #1 and #2, and opening the Charlie Creek to Watord City 230 kV line. | Apply SLG ault near Charlie Creek 230 kV with Charlie Creek 230 kV breaker 382 stuck 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4092 7 cycles: Trip Charlie Creek 230 kV breaker 282 16 cycles: Trip Watord City 230 kV breakers 682 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F90 | Apply SLG ault near Charlie Creek 230 kV with stuck breaker, cleared by opening Charlie Creek 345/230 kV Transormers #1 and #2, and opening the Charlie Creek to Watord City 230 kV line. | Apply SLG ault near Charlie Creek 230 kV with Charlie Creek 230 kV breaker 282 stuck 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4092 7 cycles: Trip Charlie Creek 230 kV breaker 382 16 cycles: Trip Watord City 230 kV breakers 682 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F91 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Belield 345 kV line, and tripping the Charlie Creek 345 kV West Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 4192 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 4096 and Belield 345 kV breakers 396 and 492 16 cycles: Trip Charlie Creek 345 kV breakers 3792 and 3992 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F92 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Belield 345 kV line, and opening the Charlie Creek 345/230 kV Transormer #1. opening the Charlie Creek 345/230 kV Transormer #2. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 4096 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 4192 and Belield 345 kV breakers 396 and 492 16 cycles: Trip Charlie Creek 345 kV breaker 4092 and Charlie Creek 230 kV breakers 282 and 382 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F93 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Antelope Valley 345 kV line, and tripping the Charlie Creek 345 kV East Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3892 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3896 and Antelope Valley 345 kV breakers 4796 and 4892 16 cycles: Trip Charlie Creek 345 kV breakers 3692 and 4092 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F94 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Antelope Valley 345 kV line, and opening the Charlie Creek 345/115 kV Transormer #1. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3896 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3892 and Antelope Valley 345 kV breakers 4796 and 4892 16 cycles: Trip Charlie Creek 345 kV breaker 3992 and Charlie Creek 115 kV breaker 962 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F95 | Prior Outage o Watord City to Williston Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F96 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F97 | Prior Outage o Watord City to Williston Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Prior Outage o Watord City to Williston Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F98 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F99 | Prior Outage o Watord City to Williston Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F100 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F101 | Prior Outage o Watord City to Williston Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F102 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F103 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F104 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F105 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F106 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F107 | Prior Outage o Watord City to Williston Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F108 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F109 | Prior Outage o Watord City to Williston Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F110 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F111 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 230 kV on Watord City to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 230 kV on Watord City to Williston 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 27 cycles: Reclose Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 34 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F112 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 27 cycles: Reclose Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 34 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F113 | Prior Outage o Watord City to Williston Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F114 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F115 | Prior Outage o Watord City to Williston Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F116 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F117 | Prior Outage o Watord City to Williston Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F118 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F119 | Prior Outage o Watord City to Williston Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F120 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F121 | Prior Outage o Watord City to Williston Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F122 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F123 | Prior Outage o Watord City to Williston Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P6 | Yes | Yes | No | Yes | Yes | No | Yes | Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the high voltage issue was still observed. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection off the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F124 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F125 | Prior Outage o Watord City to Williston Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P6 | Yes | Yes | No | Yes | Yes | No | Yes | Voltage on 345 kV network near TANDE substation was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the high voltage issue was still observed. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection off the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F126 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P6 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage of GEN-2015-046 and BURKE 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the high voltage issue was still observed. | No Mitigation
16 | 21L | Normal | F127 | Prior Outage o Watord City to Williston Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F128 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F129 | Prior Outage o Watord City to Williston Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F130 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F131 | Prior Outage o Watord City to Williston Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Normal | F132 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F133 | Prior Outage o Watord City to Williston Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Normal | F134 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F01 | Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F02 | Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F03 | Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F04 | Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F05 | Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F06 | Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F07 | Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F08 | Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F09 | Apply 3PH ault near Watord City 230 kV on Watord City to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 230 kV on Watord City to Williston 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 27 cycles: Reclose Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 34 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F10 | Apply 3PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 27 cycles: Reclose Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 34 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F11 | Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F12 | Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F13 | Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F14 | Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F15 | Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F16 | Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F17 | Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F18 | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F19 | Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 6 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F20 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F21 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F22 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Mont 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 2 115 kV on Williston 2 to Mont 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 27 cycles: Reclose Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 34 cycles: Trip Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F23 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Little Muddy 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Little Muddy 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 27 cycles: Reclose Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 34 cycles: Trip Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F24 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to N.W. Williston 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 2 115 kV on Williston 2 to N.W. Williston 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 27 cycles: Reclose Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 34 cycles: Trip Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F25 | Apply 3PH ault near Williston 115 kV on Williston to airview West 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston115 kV on Williston to airview West 115 kV line 7 cycles: Trip Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 27 cycles: Reclose Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 34 cycles: Trip Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F26 | Apply 3PH ault near Williston 115 kV on Williston to Judson 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Judson 115 kV line 7 cycles: Trip Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 27 cycles: Reclose Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 34 cycles: Trip Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F27 | Apply 3PH ault near Judson 115 kV on Judson to Stateline 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Judson 115 kV on Judson 115 to Stateline 115 kV line 7 cycles: Trip Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 27 cycles: Reclose Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 34 cycles: Trip Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F28 | Apply 3PH ault near Judson 115 kV on Judson to SW.WLSTN-MW7 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Judson115 kV on Judson 115 to SW.WLSTN-MW7 115 kV line 7 cycles: Trip Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) 27 cycles: Reclose Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) 34 cycles: Trip Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F29 | Apply 3PH ault near Williston 115 kV on Williston to Marley 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Marley 115 kV line 7 cycles: Trip Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) 27 cycles: Reclose Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) 34 cycles: Trip Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F30 | Apply 3PH ault near Williston 115 kV on Williston to Culbertson 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Culbertson 115 kV line 7 cycles: Trip Williston 115 kV breaker 1562 and Culbertson Generatio Station 115 kV breaker 161 and Wol Point Breaker 262 27 cycles: Reclose Williston 115 kV breaker 1562 and Wol Point Breaker 262 34 cycles: Trip Williston 115 kV breaker 1562 and Wol Point Breaker 262 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F31 | Apply 3PH ault on Wheelock 230/115 kV Transormer #1, near Wheelock 230 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Wheelock 230/115 Transormer #1, near Wheelock 230 kV 7 cycles: Trip Wheelock 230 kV breakers 1486 and 1686 and Wheelock 115 kV breakers 6210 and 6260 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F32 | Apply 3PH ault near Wheelock 230 kV on Wheelock to Tioga 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Wheelock 230 kV on Wheelock to Tioga 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F33 | Apply 3PH ault on Patent Gate 345/115 kV Transormer #1, near Patent Gate 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Patent Gate 345/115 kV Transormer #1, near Patent Gate 345 kV or 6 cycles 6 cycles: Trip Patent Gate 345 kV breakers 1696 and 1792 7 cycles: Trip Patent Gate 115 kV breakers 166 and 262 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F34 | Apply 3PH ault on Patent Gate 345/115 kV Transormer #2, near Patent Gate 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Patent Gate 345/115 kV Transormer #2, near Patent Gate 345 kV or 6 cycles 6 cycles: Trip Patent Gate 345 kV breakers 1896 and 1992 7 cycles: Trip Patent Gate 115 kV breakers 366 and 462 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F35 | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Kummer Ridge 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Kummer Ridge 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 26 cycles: Reclose Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 32 cycles: Trip Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F36 | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 6 cycles 6 cycles: Trip Kummer Ridge 345 kV breakers 192 and 592 7 cycles: Trip Kummer Ridge 115 kV breakers 362 and 366 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F37 | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #2, near Kummer Ridge 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 6 cycles 6 cycles: Trip Kummer Ridge 345 kV breakers 596 and 692 7 cycles: Trip Kummer Ridge 115 kV breakers 162 and 166 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F38 | Apply 3PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to GEN-2015-046 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near TANDE___-BE3 345 kV on TANDE to GEN-2015-046 345 kV line 6 cycles: Trip TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers 26 cycles: Reclose TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers 32 cycles: Trip TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F39 | Apply 3PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to BURKE___-PP3 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to BURKE___-PP3 345 kV line 6 cycles: Trip TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers 26 cycles: Reclose TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers 32 cycles: Trip TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F40 | Apply 3PH ault on TANDE 345/230 kV Transormer, near TANDE 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on TANDE 345/230 kV Transormer, near TANDE 345 kV 6 cycles: Trip TANDE 345 kV breakers 7 cycles: Trip TANDE 230 kV breakers | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Voltage on the 345 kV network near the TANDE substation was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the high voltage issue was still observed. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection off the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F41 | Apply 3PH ault on G15-046 345/34.5 kV Transormer #1, near G15-046 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on G15-046 345/34.5 kV Transormer #1, near G15-046 345 kV 6 cycles: Trip G15-046 345 kV breakers 7 cycles: Trip G15-046 34.5 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F42 | Apply 3PH ault on G15-046 345/34.5 kV Transormer #2, near G15-046 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on G15-046 345/34.5 kV Transormer #2, near G15-046 345 kV 6 cycles: Trip G15-046 345 kV breakers 7 cycles: Trip G15-046 34.5 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F43 | Apply 3PH ault on Charlie Creek 345/115 kV Transormer, near Charlie Creek 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Charlie Creek 345/115 kV Transormer, near Charlie Creek 345 kV 6 cycles: Trip Charlie Creek 345 kV breakers 3896 and 3992 7 cycles :Trip Charlie Creek 115 kV breaker 962 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F44 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Roundup 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Roundup 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 26 cycles: Reclose Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 32 cycles: Trip Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F45 | Apply 3PH ault on Belield 345/230 kV Transormer #1, near Belield 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Belield 345/230 kV Transormer #1, near Belield 345 kV 6 cycles: Trip Belield 345 kV breakers 292 and 396 7 cycles: Trip Belield 230 kV breakers 1282 and 1482 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F46 | Apply 3PH ault on Belield 345/230 kV Transormer #2, near Belield 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Belield 345/230 kV Transormer #2, near Belield 345 kV 6 cycles: Trip Belield 345 kV breakers 292 and 492 7 cycles: Trip Belield 230 kV breakers 1382 and 1582 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F47 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Roundup 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Roundup 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 26 cycles: Reclose Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 32 cycles: Trip Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F48 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Coteau (RREC) 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Coteau (RREC) 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4592, Coteau breakers 27122, 2112 26 cycles: Reclose Antelope Valley 345 kV breakers 4596 and 4592 32 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4592 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response.
16 | 21S | Normal | F49 | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #1, near Antelope Valley 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #1, near Antelope Valley 345 kV 6 cycles: Trip Antelope Valley 345 kV breakers 4192 and 4196 7 cycles: Trip Antelope Valley 23 kV breaker | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F50 | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #2, near Antelope Valley 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #2, near Antelope Valley 345 kV 6 cycles: Trip Antelope Valley 345 kV breakers 4392 and 4396 7 cycles: Trip Antelope Valley 23 kV breaker | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F51 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #1 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #1 6 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 7 cycles: Trip Great Plains breakers 128, 228,328, 428, 528, 628, 728 26 cycles: Reclose Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 32 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F52 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #2 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #2 6 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 7 cycles: Trip Great Plains breakers 128, 228,328, 428, 528, 628, 728 26 cycles: Reclose Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 32 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F53 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Broadland 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Broadland 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 26 cycles: Reclose Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 32 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response.
16 | 21S | Normal | F54 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #1 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #1 6 cycles: Trip Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 26 cycles: Reclose Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 32 cycles: Trip Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F55 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #2 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #2 6 cycles: Trip Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 26 cycles: Reclose Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 32 cycles: Trip Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F56 | Apply SLG ault near East Haybutte 115 kV with stuck breaker, cleared by opening the Lonesome Creek Switchyard to Cherry Creek 115 kV line, and opening the Lonesome Creek Switchyard to Lonesome Creek 115 kV line. | Apply SLG ault near East Haybutte 115 kV with Lonesome Creek Switchyard 115 kV breaker 1466 stuck 7 cycles: Trip Cherry Creek 115 kV breakers CB2 and CB3 and Lonesome Creek 115 kV breaker 1462 16 cycles: Trip Lonesome Creek Switchyard 115 kV breaker 1562. Trip Lonesome Creek generators 4, 5, and 6 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F57 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Roosevelt 115 kV line, and opening the Cherry Creek to Lonesome Creek Switchyard 115 kV line. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB3 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB4 16 cycles: Trip Cherry Creek 115 kV breaker CB2 and Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F58 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Roosevelt 115 kV line, and opening the Cherry Creek 25 kV load. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB4 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB3 16 cycles: Trip Cherry Creek 115 kV breaker CB1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F59 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Watord City 115 kV line, and opening the Cherry Creek to Lonesome Creek Switchyard 115 kV line. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB2 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB1 and Watord City 115 kV breakers 1362 and 1462 16 cycles: Trip Cherry Creek 115 kV breaker CB3 and Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F60 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Watord City 115 kV line, and opening the Cherry Creek 25 kV load. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB1 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB2 and Watord City 115 kV breakers 1362 and 1462 16 cycles: Trip Cherry Creek 115 kV breaker CB4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F61 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Coyote Charlie 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. opening the Watord City to Oasis 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1162 stuck 7 cycles: Trip Watord City 115 kV breaker 1262, Coyote Charlie 115 kV breakers 16 cycles: Trip Watord City 115 kV breakers 1062 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F62 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Coyote Charlie 115 kV line, and opening the Watord City 34.5 kV load. opening the Watord City 115 kV 15 MVAR Cap Bank. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1262 stuck 7 cycles: Trip Watord City 115 kV breaker 1162, Coyote Charlie 115 kV breakers 16 cycles: Trip Watord City 115 kV breaker 1362 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F63 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Garden Creek 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1062 stuck 7 cycles: Trip Watord City 115 kV breaker 1562, Garden Creek 115 kV breakers 16 cycles: Trip Watord City 115 kV breakers 1162 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F64 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Garden Creek 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. opening the Watord City 115 kV 15 MVAR Cap Bank. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1562 stuck 7 cycles: Trip Watord City 115 kV breaker 1062, Garden Creek 115 kV breakers 16 cycles: Trip Watord City 115 kV breaker 1462 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F65 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #1, and opening the Watord City 230/115 kV Transormer #2 opening the Watord City 115 kV 15 MVAR Cap Bank. opening the Watord City to Garden Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1062 stuck 7 cycles: Trip Watord City 115 kV breaker 1162 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breakers 1562, Garden Creek 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F66 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #1, and opening the Watord City 230/115 kV Transormer #2. opening the Watord City to Coyote Charlie 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1162 stuck 7 cycles: Trip Watord City 115 kV breakers 1062 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1262, Coyote Charlie 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F67 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #2, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City to Cherry Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1462 stuck 7 cycles: Trip Watord City 115 kV breakers 1562 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1362 and Cherry Creek 115 kV breakers CB1 and CB2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F68 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #2, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City to Garden Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1562 stuck 7 cycles: Trip Watord City 115 kV breaker 1462 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1062 , Garden Creek 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F69 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Williston 230 kV line | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 682 stuck 7 cycles: Trip Watord City 230 kV breaker 782 and Williston 230 kV breakers 382 and 486 16 cycles: Trip Watord City 230 kV breaker 982 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F70 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Williston 230 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 782 stuck 7 cycles: Trip Watord City 230 kV breaker 682 and Williston 230 kV breakers 382 and 486 16 cycles: Trip Watord City 230 kV breaker 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F71 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Charlie Creek 230 kV line | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 982 stuck 7 cycles: Trip Watord City 230 kV breaker 882 and Charlie Creek 230 kV breakers 282 and 382 16 cycles: Trip Watord City 230 kV breaker 682 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F72 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Charlie Creek 230 kV line, and opening the Watord City 230/115 kV Transormer #1 opening the Watord City 230/115 kV Transormer #2 | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 882 stuck 7 cycles: Trip Watord City 230 kV breaker 982 and Charlie Creek 230 kV breakers 282 and 382 16 cycles: Trip Watord City 230 kV breaker 782 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F73 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #1, and tripping the Williston 230 kV East Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 182 stuck 7 cycles: Trip Williston 230 kV breaker 286 and Williston 115 kV breakers 2162 and 2266 16 cycles: Trip Williston 230 kV breaker 382 and 582 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F74 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #1, and opening the Williston to Judson 230 kV line. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 286 stuck 7 cycles: Trip Williston 230 kV breaker 182 and Williston 115 kV breakers 2162 and 2266 16 cycles: Trip Williston 230 kV breaker 282 and Judson breakers 1082 and 1182 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F75 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #2, and tripping the Williston 230 kV West Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 482 stuck 7 cycles: Trip Williston 230 kV breaker 486 and Williston 115 kV breaker 1762 16 cycles: Trip Williston 230 kV breakers 282 and 686 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F76 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #2, and opening the Williston to Watord City 230 kV line. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 486 stuck 7 cycles: Trip Williston 230 kV breaker 482 and Williston 115 kV breaker 1762 16 cycles: Trip Williston 230 kV breaker 382 and Watord City 230 kV breakers 682 and 782 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F77 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Judson 230 kV line, and tripping the Williston 230 kV West Bus | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 282 stuck 7 cycles: Trip Williston 230 kV breaker 286 and Judson 230 kV breakers 1082 and 1182 16 cycles: Trip Williston 230 kV breakers 482 and 686 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F78 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Judson 230 kV line, and opening the Williston 230/115 kV Transormer #1 | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 286 stuck 7 cycles: Trip Williston 230 kV breaker 282 and Judson 230 kV breakers 1082 and 1182 16 cycles: Trip Williston 230 kV breaker 182 and Williston 115 kV breakers 2162 and 2266 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F79 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Wheelock 230 kV line, and tripping the Williston 230 kV East Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 582 stuck 7 cycles: Trip Williston 230 kV breaker 686 and Wheelock 230 kV breakers 1482 and 1486 16 cycles: Trip Williston 230 kV breakers 382 and 182 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F80 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Wheelock 230 kV line, and tripping the Williston 230 kV West Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 686 stuck 7 cycles: Trip Williston 230 kV breaker 582 and Wheelock 230 kV breakers 1482 and 1486 16 cycles: Trip Williston 230 kV breakers 482 and 282 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F81 | Apply SLG ault near Judson 230 kV with stuck breaker, cleared by opening the Judson 230/345 kV Transormer #1, and opening the Judson to Williston 230 kV line. | Apply SLG ault near Judson 230 kV with Judson 230 kV breaker 1082 stuck 6 cycles: Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breaker 1282 16 cycles: Trip Judson 230 kV breaker 1182 and Williston 230 kV breakers 282 and 286 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F82 | Apply SLG ault near Judson 230 kV with stuck breaker, cleared by opening the Judson 230/345 kV Transormer #1, and opening the Judson to Williston 230 kV line. | Apply SLG ault near Judson 230 kV with Judson 230 kV breaker 1282 stuck 6 cycles: Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breaker 1082 16 cycles: Trip Judson 230 kV breaker 1382 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F83 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to Patent Gate 345 kV line #1, and tripping the Judson 345 kV West Bus | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 496 stuck 6 cycles: Trip Judson 345 kV breaker 492 and Patent Gate 345 kV breakers 1492 and 1496 16 cycles: Trip Judson 345 kV breakers 592 and 192 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F84 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to Patent Gate 345 kV line #1, and tripping the Judson 345 kV East Bus | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 492 stuck 6 cycles: Trip Judson 345 kV breaker 496 and Patent Gate 345 kV breakers 1492 and 1496 16 cycles: Trip Judson 345 kV breakers 692 and 292 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F85 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to TN.LS-JD-BE3 345 kV line, and tripping the Judson 345kV East Bus. | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 292 stuck 6 cycles: Trip Judson 345 kV breaker 296 and TANDE 345 kV breakers 16 cycles: Trip Judson 345 kV breakers 492 and 692 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F86 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to TN.LS-JD-BE3 345 kV line | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 296 stuck 6 cycles: Trip Judson 345 kV breaker 292 and TANDE 345 kV breakers 16 cycles: Trip Judson 345 kV breaker 192 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F87 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Patent Gate 345 kV line, and tripping the Charlie Creek 345 kV West Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3792 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3696 and Patent Gate 345 kV breakers 1892 and 1896 16 cycles: Trip Charlie Creek 345 kV breakers 3992 and 4192 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F88 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Patent Gate 345 kV line, and opening the Charlie Creek to Roundup 345 kV line. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3696 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3792 and Patent Gate 345 kV breakers 1892 and 1896 16 cycles: Trip Charlie Creek 345 kV breaker 3692 and Roundup 345 kV breakers 892 and 896 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F89 | Apply SLG ault near Charlie Creek 230 kV with stuck breaker, cleared by opening Charlie Creek 345/230 kV Transormers #1 and #2, and opening the Charlie Creek to Watord City 230 kV line. | Apply SLG ault near Charlie Creek 230 kV with Charlie Creek 230 kV breaker 382 stuck 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4092 7 cycles: Trip Charlie Creek 230 kV breaker 282 16 cycles: Trip Watord City 230 kV breakers 682 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F90 | Apply SLG ault near Charlie Creek 230 kV with stuck breaker, cleared by opening Charlie Creek 345/230 kV Transormers #1 and #2, and opening the Charlie Creek to Watord City 230 kV line. | Apply SLG ault near Charlie Creek 230 kV with Charlie Creek 230 kV breaker 282 stuck 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4092 7 cycles: Trip Charlie Creek 230 kV breaker 382 16 cycles: Trip Watord City 230 kV breakers 682 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F91 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Belield 345 kV line, and tripping the Charlie Creek 345 kV West Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 4192 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 4096 and Belield 345 kV breakers 396 and 492 16 cycles: Trip Charlie Creek 345 kV breakers 3792 and 3992 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F92 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Belield 345 kV line, and opening the Charlie Creek 345/230 kV Transormer #1. opening the Charlie Creek 345/230 kV Transormer #2. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 4096 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 4192 and Belield 345 kV breakers 396 and 492 16 cycles: Trip Charlie Creek 345 kV breaker 4092 and Charlie Creek 230 kV breakers 282 and 382 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F93 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Antelope Valley 345 kV line, and tripping the Charlie Creek 345 kV East Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3892 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3896 and Antelope Valley 345 kV breakers 4796 and 4892 16 cycles: Trip Charlie Creek 345 kV breakers 3692 and 4092 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F94 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Antelope Valley 345 kV line, and opening the Charlie Creek 345/115 kV Transormer #1. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3896 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3892 and Antelope Valley 345 kV breakers 4796 and 4892 16 cycles: Trip Charlie Creek 345 kV breaker 3992 and Charlie Creek 115 kV breaker 962 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F95 | Prior Outage o Watord City to Williston Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F96 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F97 | Prior Outage o Watord City to Williston Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Prior Outage o Watord City to Williston Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F98 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F99 | Prior Outage o Watord City to Williston Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F100 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F101 | Prior Outage o Watord City to Williston Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F102 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F103 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F104 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F105 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F106 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F107 | Prior Outage o Watord City to Williston Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F108 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F109 | Prior Outage o Watord City to Williston Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F110 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F111 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 230 kV on Watord City to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 230 kV on Watord City to Williston 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 27 cycles: Reclose Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 34 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F112 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 27 cycles: Reclose Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 34 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F113 | Prior Outage o Watord City to Williston Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F114 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F115 | Prior Outage o Watord City to Williston Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F116 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F117 | Prior Outage o Watord City to Williston Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F118 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F119 | Prior Outage o Watord City to Williston Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F120 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F121 | Prior Outage o Watord City to Williston Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F122 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F123 | Prior Outage o Watord City to Williston Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F124 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F125 | Prior Outage o Watord City to Williston Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P6 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the high voltage issue was still observed. | No Mitigation
16 | 21S | Normal | F126 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F127 | Prior Outage o Watord City to Williston Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F128 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F129 | Prior Outage o Watord City to Williston Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F130 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21S | Normal | F131 | Prior Outage o Watord City to Williston Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F132 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F133 | Prior Outage o Watord City to Williston Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21S | Normal | F134 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F01 | Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F02 | Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F03 | Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F04 | Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F05 | Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F06 | Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F07 | Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F08 | Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F09 | Apply 3PH ault near Watord City 230 kV on Watord City to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 230 kV on Watord City to Williston 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 27 cycles: Reclose Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 34 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F10 | Apply 3PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 27 cycles: Reclose Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 34 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F11 | Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F12 | Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F13 | Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F14 | Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F15 | Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F16 | Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F17 | Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F18 | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F19 | Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 6 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F20 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F21 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F22 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Mont 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 2 115 kV on Williston 2 to Mont 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 27 cycles: Reclose Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 34 cycles: Trip Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F23 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Little Muddy 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Little Muddy 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 27 cycles: Reclose Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 34 cycles: Trip Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F24 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to N.W. Williston 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 2 115 kV on Williston 2 to N.W. Williston 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 27 cycles: Reclose Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 34 cycles: Trip Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F25 | Apply 3PH ault near Williston 115 kV on Williston to airview West 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston115 kV on Williston to airview West 115 kV line 7 cycles: Trip Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 27 cycles: Reclose Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 34 cycles: Trip Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F26 | Apply 3PH ault near Williston 115 kV on Williston to Judson 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Judson 115 kV line 7 cycles: Trip Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 27 cycles: Reclose Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 34 cycles: Trip Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F27 | Apply 3PH ault near Judson 115 kV on Judson to Stateline 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Judson 115 kV on Judson 115 to Stateline 115 kV line 7 cycles: Trip Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 27 cycles: Reclose Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 34 cycles: Trip Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F28 | Apply 3PH ault near Judson 115 kV on Judson to SW.WLSTN-MW7 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Judson115 kV on Judson 115 to SW.WLSTN-MW7 115 kV line 7 cycles: Trip Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) 27 cycles: Reclose Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) 34 cycles: Trip Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F29 | Apply 3PH ault near Williston 115 kV on Williston to Marley 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Marley 115 kV line 7 cycles: Trip Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) 27 cycles: Reclose Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) 34 cycles: Trip Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F30 | Apply 3PH ault near Williston 115 kV on Williston to Culbertson 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Culbertson 115 kV line 7 cycles: Trip Williston 115 kV breaker 1562 and Culbertson Generatio Station 115 kV breaker 161 and Wol Point Breaker 262 27 cycles: Reclose Williston 115 kV breaker 1562 and Wol Point Breaker 262 34 cycles: Trip Williston 115 kV breaker 1562 and Wol Point Breaker 262 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F31 | Apply 3PH ault on Wheelock 230/115 kV Transormer #1, near Wheelock 230 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Wheelock 230/115 Transormer #1, near Wheelock 230 kV 7 cycles: Trip Wheelock 230 kV breakers 1486 and 1686 and Wheelock 115 kV breakers 6210 and 6260 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F32 | Apply 3PH ault near Wheelock 230 kV on Wheelock to Tioga 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Wheelock 230 kV on Wheelock to Tioga 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F33 | Apply 3PH ault on Patent Gate 345/115 kV Transormer #1, near Patent Gate 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Patent Gate 345/115 kV Transormer #1, near Patent Gate 345 kV or 6 cycles 6 cycles: Trip Patent Gate 345 kV breakers 1696 and 1792 7 cycles: Trip Patent Gate 115 kV breakers 166 and 262 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F34 | Apply 3PH ault on Patent Gate 345/115 kV Transormer #2, near Patent Gate 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Patent Gate 345/115 kV Transormer #2, near Patent Gate 345 kV or 6 cycles 6 cycles: Trip Patent Gate 345 kV breakers 1896 and 1992 7 cycles: Trip Patent Gate 115 kV breakers 366 and 462 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F35 | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Kummer Ridge 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Kummer Ridge 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 26 cycles: Reclose Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 32 cycles: Trip Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F36 | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 6 cycles 6 cycles: Trip Kummer Ridge 345 kV breakers 192 and 592 7 cycles: Trip Kummer Ridge 115 kV breakers 362 and 366 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F37 | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #2, near Kummer Ridge 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 6 cycles 6 cycles: Trip Kummer Ridge 345 kV breakers 596 and 692 7 cycles: Trip Kummer Ridge 115 kV breakers 162 and 166 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F38 | Apply 3PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to GEN-2015-046 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near TANDE___-BE3 345 kV on TANDE to GEN-2015-046 345 kV line 6 cycles: Trip TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers 26 cycles: Reclose TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers 32 cycles: Trip TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F39 | Apply 3PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to BURKE___-PP3 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to BURKE___-PP3 345 kV line 6 cycles: Trip TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers 26 cycles: Reclose TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers 32 cycles: Trip TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F40 | Apply 3PH ault on TANDE 345/230 kV Transormer, near TANDE 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on TANDE 345/230 kV Transormer, near TANDE 345 kV 6 cycles: Trip TANDE 345 kV breakers 7 cycles: Trip TANDE 230 kV breakers | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage on the 345 kV network near the TANDE substation was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the high voltage issue was still observed. | No Mitigation
16 | 28S | Normal | F41 | Apply 3PH ault on G15-046 345/34.5 kV Transormer #1, near G15-046 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on G15-046 345/34.5 kV Transormer #1, near G15-046 345 kV 6 cycles: Trip G15-046 345 kV breakers 7 cycles: Trip G15-046 34.5 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F42 | Apply 3PH ault on G15-046 345/34.5 kV Transormer #2, near G15-046 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on G15-046 345/34.5 kV Transormer #2, near G15-046 345 kV 6 cycles: Trip G15-046 345 kV breakers 7 cycles: Trip G15-046 34.5 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F43 | Apply 3PH ault on Charlie Creek 345/115 kV Transormer, near Charlie Creek 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Charlie Creek 345/115 kV Transormer, near Charlie Creek 345 kV 6 cycles: Trip Charlie Creek 345 kV breakers 3896 and 3992 7 cycles :Trip Charlie Creek 115 kV breaker 962 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F44 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Roundup 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Roundup 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 26 cycles: Reclose Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 32 cycles: Trip Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F45 | Apply 3PH ault on Belield 345/230 kV Transormer #1, near Belield 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Belield 345/230 kV Transormer #1, near Belield 345 kV 6 cycles: Trip Belield 345 kV breakers 292 and 396 7 cycles: Trip Belield 230 kV breakers 1282 and 1482 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F46 | Apply 3PH ault on Belield 345/230 kV Transormer #2, near Belield 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Belield 345/230 kV Transormer #2, near Belield 345 kV 6 cycles: Trip Belield 345 kV breakers 292 and 492 7 cycles: Trip Belield 230 kV breakers 1382 and 1582 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F47 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Roundup 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Roundup 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 26 cycles: Reclose Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 32 cycles: Trip Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F48 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Coteau (RREC) 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Coteau (RREC) 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4592, Coteau breakers 27122, 2112 26 cycles: Reclose Antelope Valley 345 kV breakers 4596 and 4592 32 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4592 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F49 | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #1, near Antelope Valley 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #1, near Antelope Valley 345 kV 6 cycles: Trip Antelope Valley 345 kV breakers 4192 and 4196 7 cycles: Trip Antelope Valley 23 kV breaker | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F50 | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #2, near Antelope Valley 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #2, near Antelope Valley 345 kV 6 cycles: Trip Antelope Valley 345 kV breakers 4392 and 4396 7 cycles: Trip Antelope Valley 23 kV breaker | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F51 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #1 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #1 6 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 7 cycles: Trip Great Plains breakers 128, 228,328, 428, 528, 628, 728 26 cycles: Reclose Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 32 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F52 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #2 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #2 6 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 7 cycles: Trip Great Plains breakers 128, 228,328, 428, 528, 628, 728 26 cycles: Reclose Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 32 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F53 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Broadland 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Broadland 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 26 cycles: Reclose Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 32 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F54 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #1 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #1 6 cycles: Trip Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 26 cycles: Reclose Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 32 cycles: Trip Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F55 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #2 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #2 6 cycles: Trip Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 26 cycles: Reclose Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 32 cycles: Trip Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F56 | Apply SLG ault near East Haybutte 115 kV with stuck breaker, cleared by opening the Lonesome Creek Switchyard to Cherry Creek 115 kV line, and opening the Lonesome Creek Switchyard to Lonesome Creek 115 kV line. | Apply SLG ault near East Haybutte 115 kV with Lonesome Creek Switchyard 115 kV breaker 1466 stuck 7 cycles: Trip Cherry Creek 115 kV breakers CB2 and CB3 and Lonesome Creek 115 kV breaker 1462 16 cycles: Trip Lonesome Creek Switchyard 115 kV breaker 1562. Trip Lonesome Creek generators 4, 5, and 6 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F57 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Roosevelt 115 kV line, and opening the Cherry Creek to Lonesome Creek Switchyard 115 kV line. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB3 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB4 16 cycles: Trip Cherry Creek 115 kV breaker CB2 and Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F58 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Roosevelt 115 kV line, and opening the Cherry Creek 25 kV load. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB4 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB3 16 cycles: Trip Cherry Creek 115 kV breaker CB1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F59 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Watord City 115 kV line, and opening the Cherry Creek to Lonesome Creek Switchyard 115 kV line. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB2 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB1 and Watord City 115 kV breakers 1362 and 1462 16 cycles: Trip Cherry Creek 115 kV breaker CB3 and Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F60 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Watord City 115 kV line, and opening the Cherry Creek 25 kV load. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB1 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB2 and Watord City 115 kV breakers 1362 and 1462 16 cycles: Trip Cherry Creek 115 kV breaker CB4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F61 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Coyote Charlie 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. opening the Watord City to Oasis 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1162 stuck 7 cycles: Trip Watord City 115 kV breaker 1262, Coyote Charlie 115 kV breakers 16 cycles: Trip Watord City 115 kV breakers 1062 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F62 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Coyote Charlie 115 kV line, and opening the Watord City 34.5 kV load. opening the Watord City 115 kV 15 MVAR Cap Bank. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1262 stuck 7 cycles: Trip Watord City 115 kV breaker 1162, Coyote Charlie 115 kV breakers 16 cycles: Trip Watord City 115 kV breaker 1362 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F63 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Garden Creek 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1062 stuck 7 cycles: Trip Watord City 115 kV breaker 1562, Garden Creek 115 kV breakers 16 cycles: Trip Watord City 115 kV breakers 1162 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F64 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Garden Creek 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. opening the Watord City 115 kV 15 MVAR Cap Bank. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1562 stuck 7 cycles: Trip Watord City 115 kV breaker 1062, Garden Creek 115 kV breakers 16 cycles: Trip Watord City 115 kV breaker 1462 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F65 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #1, and opening the Watord City 230/115 kV Transormer #2 opening the Watord City 115 kV 15 MVAR Cap Bank. opening the Watord City to Garden Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1062 stuck 7 cycles: Trip Watord City 115 kV breaker 1162 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breakers 1562, Garden Creek 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F66 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #1, and opening the Watord City 230/115 kV Transormer #2. opening the Watord City to Coyote Charlie 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1162 stuck 7 cycles: Trip Watord City 115 kV breakers 1062 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1262, Coyote Charlie 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F67 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #2, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City to Cherry Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1462 stuck 7 cycles: Trip Watord City 115 kV breakers 1562 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1362 and Cherry Creek 115 kV breakers CB1 and CB2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F68 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #2, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City to Garden Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1562 stuck 7 cycles: Trip Watord City 115 kV breaker 1462 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1062 , Garden Creek 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F69 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Williston 230 kV line | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 682 stuck 7 cycles: Trip Watord City 230 kV breaker 782 and Williston 230 kV breakers 382 and 486 16 cycles: Trip Watord City 230 kV breaker 982 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F70 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Williston 230 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 782 stuck 7 cycles: Trip Watord City 230 kV breaker 682 and Williston 230 kV breakers 382 and 486 16 cycles: Trip Watord City 230 kV breaker 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F71 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Charlie Creek 230 kV line | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 982 stuck 7 cycles: Trip Watord City 230 kV breaker 882 and Charlie Creek 230 kV breakers 282 and 382 16 cycles: Trip Watord City 230 kV breaker 682 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F72 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Charlie Creek 230 kV line, and opening the Watord City 230/115 kV Transormer #1 opening the Watord City 230/115 kV Transormer #2 | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 882 stuck 7 cycles: Trip Watord City 230 kV breaker 982 and Charlie Creek 230 kV breakers 282 and 382 16 cycles: Trip Watord City 230 kV breaker 782 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F73 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #1, and tripping the Williston 230 kV East Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 182 stuck 7 cycles: Trip Williston 230 kV breaker 286 and Williston 115 kV breakers 2162 and 2266 16 cycles: Trip Williston 230 kV breaker 382 and 582 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F74 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #1, and opening the Williston to Judson 230 kV line. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 286 stuck 7 cycles: Trip Williston 230 kV breaker 182 and Williston 115 kV breakers 2162 and 2266 16 cycles: Trip Williston 230 kV breaker 282 and Judson breakers 1082 and 1182 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F75 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #2, and tripping the Williston 230 kV West Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 482 stuck 7 cycles: Trip Williston 230 kV breaker 486 and Williston 115 kV breaker 1762 16 cycles: Trip Williston 230 kV breakers 282 and 686 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F76 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #2, and opening the Williston to Watord City 230 kV line. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 486 stuck 7 cycles: Trip Williston 230 kV breaker 482 and Williston 115 kV breaker 1762 16 cycles: Trip Williston 230 kV breaker 382 and Watord City 230 kV breakers 682 and 782 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F77 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Judson 230 kV line, and tripping the Williston 230 kV West Bus | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 282 stuck 7 cycles: Trip Williston 230 kV breaker 286 and Judson 230 kV breakers 1082 and 1182 16 cycles: Trip Williston 230 kV breakers 482 and 686 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F78 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Judson 230 kV line, and opening the Williston 230/115 kV Transormer #1 | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 286 stuck 7 cycles: Trip Williston 230 kV breaker 282 and Judson 230 kV breakers 1082 and 1182 16 cycles: Trip Williston 230 kV breaker 182 and Williston 115 kV breakers 2162 and 2266 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F79 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Wheelock 230 kV line, and tripping the Williston 230 kV East Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 582 stuck 7 cycles: Trip Williston 230 kV breaker 686 and Wheelock 230 kV breakers 1482 and 1486 16 cycles: Trip Williston 230 kV breakers 382 and 182 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F80 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Wheelock 230 kV line, and tripping the Williston 230 kV West Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 686 stuck 7 cycles: Trip Williston 230 kV breaker 582 and Wheelock 230 kV breakers 1482 and 1486 16 cycles: Trip Williston 230 kV breakers 482 and 282 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F81 | Apply SLG ault near Judson 230 kV with stuck breaker, cleared by opening the Judson 230/345 kV Transormer #1, and opening the Judson to Williston 230 kV line. | Apply SLG ault near Judson 230 kV with Judson 230 kV breaker 1082 stuck 6 cycles: Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breaker 1282 16 cycles: Trip Judson 230 kV breaker 1182 and Williston 230 kV breakers 282 and 286 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F82 | Apply SLG ault near Judson 230 kV with stuck breaker, cleared by opening the Judson 230/345 kV Transormer #1, and opening the Judson to Williston 230 kV line. | Apply SLG ault near Judson 230 kV with Judson 230 kV breaker 1282 stuck 6 cycles: Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breaker 1082 16 cycles: Trip Judson 230 kV breaker 1382 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F83 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to Patent Gate 345 kV line #1, and tripping the Judson 345 kV West Bus | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 496 stuck 6 cycles: Trip Judson 345 kV breaker 492 and Patent Gate 345 kV breakers 1492 and 1496 16 cycles: Trip Judson 345 kV breakers 592 and 192 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F84 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to Patent Gate 345 kV line #1, and tripping the Judson 345 kV East Bus | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 492 stuck 6 cycles: Trip Judson 345 kV breaker 496 and Patent Gate 345 kV breakers 1492 and 1496 16 cycles: Trip Judson 345 kV breakers 692 and 292 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F85 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to TN.LS-JD-BE3 345 kV line, and tripping the Judson 345kV East Bus. | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 292 stuck 6 cycles: Trip Judson 345 kV breaker 296 and TANDE 345 kV breakers 16 cycles: Trip Judson 345 kV breakers 492 and 692 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F86 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to TN.LS-JD-BE3 345 kV line | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 296 stuck 6 cycles: Trip Judson 345 kV breaker 292 and TANDE 345 kV breakers 16 cycles: Trip Judson 345 kV breaker 192 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F87 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Patent Gate 345 kV line, and tripping the Charlie Creek 345 kV West Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3792 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3696 and Patent Gate 345 kV breakers 1892 and 1896 16 cycles: Trip Charlie Creek 345 kV breakers 3992 and 4192 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F88 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Patent Gate 345 kV line, and opening the Charlie Creek to Roundup 345 kV line. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3696 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3792 and Patent Gate 345 kV breakers 1892 and 1896 16 cycles: Trip Charlie Creek 345 kV breaker 3692 and Roundup 345 kV breakers 892 and 896 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F89 | Apply SLG ault near Charlie Creek 230 kV with stuck breaker, cleared by opening Charlie Creek 345/230 kV Transormers #1 and #2, and opening the Charlie Creek to Watord City 230 kV line. | Apply SLG ault near Charlie Creek 230 kV with Charlie Creek 230 kV breaker 382 stuck 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4092 7 cycles: Trip Charlie Creek 230 kV breaker 282 16 cycles: Trip Watord City 230 kV breakers 682 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F90 | Apply SLG ault near Charlie Creek 230 kV with stuck breaker, cleared by opening Charlie Creek 345/230 kV Transormers #1 and #2, and opening the Charlie Creek to Watord City 230 kV line. | Apply SLG ault near Charlie Creek 230 kV with Charlie Creek 230 kV breaker 282 stuck 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4092 7 cycles: Trip Charlie Creek 230 kV breaker 382 16 cycles: Trip Watord City 230 kV breakers 682 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F91 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Belield 345 kV line, and tripping the Charlie Creek 345 kV West Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 4192 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 4096 and Belield 345 kV breakers 396 and 492 16 cycles: Trip Charlie Creek 345 kV breakers 3792 and 3992 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F92 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Belield 345 kV line, and opening the Charlie Creek 345/230 kV Transormer #1. opening the Charlie Creek 345/230 kV Transormer #2. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 4096 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 4192 and Belield 345 kV breakers 396 and 492 16 cycles: Trip Charlie Creek 345 kV breaker 4092 and Charlie Creek 230 kV breakers 282 and 382 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F93 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Antelope Valley 345 kV line, and tripping the Charlie Creek 345 kV East Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3892 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3896 and Antelope Valley 345 kV breakers 4796 and 4892 16 cycles: Trip Charlie Creek 345 kV breakers 3692 and 4092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F94 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Antelope Valley 345 kV line, and opening the Charlie Creek 345/115 kV Transormer #1. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3896 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3892 and Antelope Valley 345 kV breakers 4796 and 4892 16 cycles: Trip Charlie Creek 345 kV breaker 3992 and Charlie Creek 115 kV breaker 962 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F95 | Prior Outage o Watord City to Williston Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F96 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F97 | Prior Outage o Watord City to Williston Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Prior Outage o Watord City to Williston Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F98 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F99 | Prior Outage o Watord City to Williston Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F100 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F101 | Prior Outage o Watord City to Williston Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F102 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F103 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F104 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F105 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F106 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F107 | Prior Outage o Watord City to Williston Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F108 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F109 | Prior Outage o Watord City to Williston Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F110 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F111 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 230 kV on Watord City to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 230 kV on Watord City to Williston 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 27 cycles: Reclose Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 34 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F112 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 27 cycles: Reclose Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 34 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F113 | Prior Outage o Watord City to Williston Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F114 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F115 | Prior Outage o Watord City to Williston Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F116 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F117 | Prior Outage o Watord City to Williston Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F118 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F119 | Prior Outage o Watord City to Williston Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F120 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F121 | Prior Outage o Watord City to Williston Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F122 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F123 | Prior Outage o Watord City to Williston Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F124 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F125 | Prior Outage o Watord City to Williston Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P6 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and the high voltage issue was still observed. | No Mitigation
16 | 28S | Normal | F126 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F127 | Prior Outage o Watord City to Williston Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F128 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F129 | Prior Outage o Watord City to Williston Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F130 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F131 | Prior Outage o Watord City to Williston Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F132 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 28S | Normal | F133 | Prior Outage o Watord City to Williston Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 28S | Normal | F134 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Sensitivity | F01 | Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F02 | Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F03 | Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F04 | Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F05 | Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F06 | Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F07 | Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F08 | Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F09 | Apply 3PH ault near Watord City 230 kV on Watord City to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 230 kV on Watord City to Williston 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 27 cycles: Reclose Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 34 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F10 | Apply 3PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 27 cycles: Reclose Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 34 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F11 | Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F12 | Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F13 | Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F14 | Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F15 | Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Sensitivity | F16 | Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Sensitivity | F17 | Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P1 | Yes | Yes | No | Yes | Yes | Yes | No | Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping and high voltage issue were still observed. | No Mitigation
16 | 19W | Sensitivity | F18 | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F19 | Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 6 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F20 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F21 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F22 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Mont 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 2 115 kV on Williston 2 to Mont 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 27 cycles: Reclose Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 34 cycles: Trip Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Sensitivity | F23 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Little Muddy 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Little Muddy 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 27 cycles: Reclose Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 34 cycles: Trip Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Sensitivity | F24 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to N.W. Williston 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 2 115 kV on Williston 2 to N.W. Williston 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 27 cycles: Reclose Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 34 cycles: Trip Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Sensitivity | F25 | Apply 3PH ault near Williston 115 kV on Williston to airview West 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston115 kV on Williston to airview West 115 kV line 7 cycles: Trip Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 27 cycles: Reclose Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 34 cycles: Trip Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Sensitivity | F26 | Apply 3PH ault near Williston 115 kV on Williston to Judson 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Judson 115 kV line 7 cycles: Trip Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 27 cycles: Reclose Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 34 cycles: Trip Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F27 | Apply 3PH ault near Judson 115 kV on Judson to Stateline 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Judson 115 kV on Judson 115 to Stateline 115 kV line 7 cycles: Trip Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 27 cycles: Reclose Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 34 cycles: Trip Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F28 | Apply 3PH ault near Judson 115 kV on Judson to SW.WLSTN-MW7 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Judson115 kV on Judson 115 to SW.WLSTN-MW7 115 kV line 7 cycles: Trip Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) 27 cycles: Reclose Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) 34 cycles: Trip Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F29 | Apply 3PH ault near Williston 115 kV on Williston to Marley 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Marley 115 kV line 7 cycles: Trip Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) 27 cycles: Reclose Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) 34 cycles: Trip Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Sensitivity | F30 | Apply 3PH ault near Williston 115 kV on Williston to Culbertson 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Culbertson 115 kV line 7 cycles: Trip Williston 115 kV breaker 1562 and Culbertson Generatio Station 115 kV breaker 161 and Wol Point Breaker 262 27 cycles: Reclose Williston 115 kV breaker 1562 and Wol Point Breaker 262 34 cycles: Trip Williston 115 kV breaker 1562 and Wol Point Breaker 262 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Sensitivity | F31 | Apply 3PH ault on Wheelock 230/115 kV Transormer #1, near Wheelock 230 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Wheelock 230/115 Transormer #1, near Wheelock 230 kV 7 cycles: Trip Wheelock 230 kV breakers 1486 and 1686 and Wheelock 115 kV breakers 6210 and 6260 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F32 | Apply 3PH ault near Wheelock 230 kV on Wheelock to Tioga 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Wheelock 230 kV on Wheelock to Tioga 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Sensitivity | F33 | Apply 3PH ault on Patent Gate 345/115 kV Transormer #1, near Patent Gate 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Patent Gate 345/115 kV Transormer #1, near Patent Gate 345 kV or 6 cycles 6 cycles: Trip Patent Gate 345 kV breakers 1696 and 1792 7 cycles: Trip Patent Gate 115 kV breakers 166 and 262 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F34 | Apply 3PH ault on Patent Gate 345/115 kV Transormer #2, near Patent Gate 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Patent Gate 345/115 kV Transormer #2, near Patent Gate 345 kV or 6 cycles 6 cycles: Trip Patent Gate 345 kV breakers 1896 and 1992 7 cycles: Trip Patent Gate 115 kV breakers 366 and 462 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F35 | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Kummer Ridge 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Kummer Ridge 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 26 cycles: Reclose Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 32 cycles: Trip Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Sensitivity | F36 | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 6 cycles 6 cycles: Trip Kummer Ridge 345 kV breakers 192 and 592 7 cycles: Trip Kummer Ridge 115 kV breakers 362 and 366 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F37 | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #2, near Kummer Ridge 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 6 cycles 6 cycles: Trip Kummer Ridge 345 kV breakers 596 and 692 7 cycles: Trip Kummer Ridge 115 kV breakers 162 and 166 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F38 | Apply 3PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to GEN-2015-046 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near TANDE___-BE3 345 kV on TANDE to GEN-2015-046 345 kV line 6 cycles: Trip TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers 26 cycles: Reclose TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers 32 cycles: Trip TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F39 | Apply 3PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to BURKE___-PP3 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to BURKE___-PP3 345 kV line 6 cycles: Trip TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers 26 cycles: Reclose TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers 32 cycles: Trip TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F40 | Apply 3PH ault on TANDE 345/230 kV Transormer, near TANDE 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on TANDE 345/230 kV Transormer, near TANDE 345 kV 6 cycles: Trip TANDE 345 kV breakers 7 cycles: Trip TANDE 230 kV breakers | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage on the 345 kV network near the TANDE substation was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and high voltage issue was still observed. | No Mitigation
16 | 19W | Sensitivity | F41 | Apply 3PH ault on G15-046 345/34.5 kV Transormer #1, near G15-046 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on G15-046 345/34.5 kV Transormer #1, near G15-046 345 kV 6 cycles: Trip G15-046 345 kV breakers 7 cycles: Trip G15-046 34.5 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Sensitivity | F42 | Apply 3PH ault on G15-046 345/34.5 kV Transormer #2, near G15-046 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on G15-046 345/34.5 kV Transormer #2, near G15-046 345 kV 6 cycles: Trip G15-046 345 kV breakers 7 cycles: Trip G15-046 34.5 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Sensitivity | F43 | Apply 3PH ault on Charlie Creek 345/115 kV Transormer, near Charlie Creek 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Charlie Creek 345/115 kV Transormer, near Charlie Creek 345 kV 6 cycles: Trip Charlie Creek 345 kV breakers 3896 and 3992 7 cycles :Trip Charlie Creek 115 kV breaker 962 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F44 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Roundup 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Roundup 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 26 cycles: Reclose Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 32 cycles: Trip Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F45 | Apply 3PH ault on Belield 345/230 kV Transormer #1, near Belield 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Belield 345/230 kV Transormer #1, near Belield 345 kV 6 cycles: Trip Belield 345 kV breakers 292 and 396 7 cycles: Trip Belield 230 kV breakers 1282 and 1482 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F46 | Apply 3PH ault on Belield 345/230 kV Transormer #2, near Belield 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Belield 345/230 kV Transormer #2, near Belield 345 kV 6 cycles: Trip Belield 345 kV breakers 292 and 492 7 cycles: Trip Belield 230 kV breakers 1382 and 1582 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F47 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Roundup 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Roundup 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 26 cycles: Reclose Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 32 cycles: Trip Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F48 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Coteau (RREC) 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Coteau (RREC) 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4592, Coteau breakers 27122, 2112 26 cycles: Reclose Antelope Valley 345 kV breakers 4596 and 4592 32 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4592 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F49 | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #1, near Antelope Valley 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #1, near Antelope Valley 345 kV 6 cycles: Trip Antelope Valley 345 kV breakers 4192 and 4196 7 cycles: Trip Antelope Valley 23 kV breaker | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F50 | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #2, near Antelope Valley 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #2, near Antelope Valley 345 kV 6 cycles: Trip Antelope Valley 345 kV breakers 4392 and 4396 7 cycles: Trip Antelope Valley 23 kV breaker | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F51 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #1 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #1 6 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 7 cycles: Trip Great Plains breakers 128, 228,328, 428, 528, 628, 728 26 cycles: Reclose Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 32 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F52 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #2 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #2 6 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 7 cycles: Trip Great Plains breakers 128, 228,328, 428, 528, 628, 728 26 cycles: Reclose Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 32 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F53 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Broadland 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Broadland 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 26 cycles: Reclose Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 32 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection off the plots showed a undamped response. Fault was tested with GEN-2020-014 offline and the undamped response was still observed. | No Mitigation
16 | 19W | Sensitivity | F54 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #1 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #1 6 cycles: Trip Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 26 cycles: Reclose Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 32 cycles: Trip Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F55 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #2 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #2 6 cycles: Trip Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 26 cycles: Reclose Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 32 cycles: Trip Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F56 | Apply SLG ault near East Haybutte 115 kV with stuck breaker, cleared by opening the Lonesome Creek Switchyard to Cherry Creek 115 kV line, and opening the Lonesome Creek Switchyard to Lonesome Creek 115 kV line. | Apply SLG ault near East Haybutte 115 kV with Lonesome Creek Switchyard 115 kV breaker 1466 stuck 7 cycles: Trip Cherry Creek 115 kV breakers CB2 and CB3 and Lonesome Creek 115 kV breaker 1462 16 cycles: Trip Lonesome Creek Switchyard 115 kV breaker 1562. Trip Lonesome Creek generators 4, 5, and 6 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F57 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Roosevelt 115 kV line, and opening the Cherry Creek to Lonesome Creek Switchyard 115 kV line. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB3 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB4 16 cycles: Trip Cherry Creek 115 kV breaker CB2 and Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F58 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Roosevelt 115 kV line, and opening the Cherry Creek 25 kV load. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB4 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB3 16 cycles: Trip Cherry Creek 115 kV breaker CB1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F59 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Watord City 115 kV line, and opening the Cherry Creek to Lonesome Creek Switchyard 115 kV line. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB2 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB1 and Watord City 115 kV breakers 1362 and 1462 16 cycles: Trip Cherry Creek 115 kV breaker CB3 and Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F60 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Watord City 115 kV line, and opening the Cherry Creek 25 kV load. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB1 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB2 and Watord City 115 kV breakers 1362 and 1462 16 cycles: Trip Cherry Creek 115 kV breaker CB4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F61 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Coyote Charlie 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. opening the Watord City to Oasis 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1162 stuck 7 cycles: Trip Watord City 115 kV breaker 1262, Coyote Charlie 115 kV breakers 16 cycles: Trip Watord City 115 kV breakers 1062 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F62 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Coyote Charlie 115 kV line, and opening the Watord City 34.5 kV load. opening the Watord City 115 kV 15 MVAR Cap Bank. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1262 stuck 7 cycles: Trip Watord City 115 kV breaker 1162, Coyote Charlie 115 kV breakers 16 cycles: Trip Watord City 115 kV breaker 1362 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F63 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Garden Creek 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1062 stuck 7 cycles: Trip Watord City 115 kV breaker 1562, Garden Creek 115 kV breakers 16 cycles: Trip Watord City 115 kV breakers 1162 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F64 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Garden Creek 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. opening the Watord City 115 kV 15 MVAR Cap Bank. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1562 stuck 7 cycles: Trip Watord City 115 kV breaker 1062, Garden Creek 115 kV breakers 16 cycles: Trip Watord City 115 kV breaker 1462 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F65 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #1, and opening the Watord City 230/115 kV Transormer #2 opening the Watord City 115 kV 15 MVAR Cap Bank. opening the Watord City to Garden Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1062 stuck 7 cycles: Trip Watord City 115 kV breaker 1162 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breakers 1562, Garden Creek 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F66 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #1, and opening the Watord City 230/115 kV Transormer #2. opening the Watord City to Coyote Charlie 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1162 stuck 7 cycles: Trip Watord City 115 kV breakers 1062 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1262, Coyote Charlie 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F67 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #2, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City to Cherry Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1462 stuck 7 cycles: Trip Watord City 115 kV breakers 1562 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1362 and Cherry Creek 115 kV breakers CB1 and CB2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F68 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #2, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City to Garden Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1562 stuck 7 cycles: Trip Watord City 115 kV breaker 1462 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1062 , Garden Creek 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F69 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Williston 230 kV line | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 682 stuck 7 cycles: Trip Watord City 230 kV breaker 782 and Williston 230 kV breakers 382 and 486 16 cycles: Trip Watord City 230 kV breaker 982 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F70 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Williston 230 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 782 stuck 7 cycles: Trip Watord City 230 kV breaker 682 and Williston 230 kV breakers 382 and 486 16 cycles: Trip Watord City 230 kV breaker 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F71 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Charlie Creek 230 kV line | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 982 stuck 7 cycles: Trip Watord City 230 kV breaker 882 and Charlie Creek 230 kV breakers 282 and 382 16 cycles: Trip Watord City 230 kV breaker 682 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F72 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Charlie Creek 230 kV line, and opening the Watord City 230/115 kV Transormer #1 opening the Watord City 230/115 kV Transormer #2 | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 882 stuck 7 cycles: Trip Watord City 230 kV breaker 982 and Charlie Creek 230 kV breakers 282 and 382 16 cycles: Trip Watord City 230 kV breaker 782 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F73 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #1, and tripping the Williston 230 kV East Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 182 stuck 7 cycles: Trip Williston 230 kV breaker 286 and Williston 115 kV breakers 2162 and 2266 16 cycles: Trip Williston 230 kV breaker 382 and 582 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F74 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #1, and opening the Williston to Judson 230 kV line. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 286 stuck 7 cycles: Trip Williston 230 kV breaker 182 and Williston 115 kV breakers 2162 and 2266 16 cycles: Trip Williston 230 kV breaker 282 and Judson breakers 1082 and 1182 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F75 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #2, and tripping the Williston 230 kV West Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 482 stuck 7 cycles: Trip Williston 230 kV breaker 486 and Williston 115 kV breaker 1762 16 cycles: Trip Williston 230 kV breakers 282 and 686 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F76 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #2, and opening the Williston to Watord City 230 kV line. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 486 stuck 7 cycles: Trip Williston 230 kV breaker 482 and Williston 115 kV breaker 1762 16 cycles: Trip Williston 230 kV breaker 382 and Watord City 230 kV breakers 682 and 782 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F77 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Judson 230 kV line, and tripping the Williston 230 kV West Bus | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 282 stuck 7 cycles: Trip Williston 230 kV breaker 286 and Judson 230 kV breakers 1082 and 1182 16 cycles: Trip Williston 230 kV breakers 482 and 686 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F78 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Judson 230 kV line, and opening the Williston 230/115 kV Transormer #1 | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 286 stuck 7 cycles: Trip Williston 230 kV breaker 282 and Judson 230 kV breakers 1082 and 1182 16 cycles: Trip Williston 230 kV breaker 182 and Williston 115 kV breakers 2162 and 2266 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F79 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Wheelock 230 kV line, and tripping the Williston 230 kV East Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 582 stuck 7 cycles: Trip Williston 230 kV breaker 686 and Wheelock 230 kV breakers 1482 and 1486 16 cycles: Trip Williston 230 kV breakers 382 and 182 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F80 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Wheelock 230 kV line, and tripping the Williston 230 kV West Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 686 stuck 7 cycles: Trip Williston 230 kV breaker 582 and Wheelock 230 kV breakers 1482 and 1486 16 cycles: Trip Williston 230 kV breakers 482 and 282 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F81 | Apply SLG ault near Judson 230 kV with stuck breaker, cleared by opening the Judson 230/345 kV Transormer #1, and opening the Judson to Williston 230 kV line. | Apply SLG ault near Judson 230 kV with Judson 230 kV breaker 1082 stuck 6 cycles: Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breaker 1282 16 cycles: Trip Judson 230 kV breaker 1182 and Williston 230 kV breakers 282 and 286 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F82 | Apply SLG ault near Judson 230 kV with stuck breaker, cleared by opening the Judson 230/345 kV Transormer #1, and opening the Judson to Williston 230 kV line. | Apply SLG ault near Judson 230 kV with Judson 230 kV breaker 1282 stuck 6 cycles: Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breaker 1082 16 cycles: Trip Judson 230 kV breaker 1382 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F83 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to Patent Gate 345 kV line #1, and tripping the Judson 345 kV West Bus | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 496 stuck 6 cycles: Trip Judson 345 kV breaker 492 and Patent Gate 345 kV breakers 1492 and 1496 16 cycles: Trip Judson 345 kV breakers 592 and 192 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F84 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to Patent Gate 345 kV line #1, and tripping the Judson 345 kV East Bus | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 492 stuck 6 cycles: Trip Judson 345 kV breaker 496 and Patent Gate 345 kV breakers 1492 and 1496 16 cycles: Trip Judson 345 kV breakers 692 and 292 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F85 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to TN.LS-JD-BE3 345 kV line, and tripping the Judson 345kV East Bus. | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 292 stuck 6 cycles: Trip Judson 345 kV breaker 296 and TANDE 345 kV breakers 16 cycles: Trip Judson 345 kV breakers 492 and 692 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F86 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to TN.LS-JD-BE3 345 kV line | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 296 stuck 6 cycles: Trip Judson 345 kV breaker 292 and TANDE 345 kV breakers 16 cycles: Trip Judson 345 kV breaker 192 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F87 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Patent Gate 345 kV line, and tripping the Charlie Creek 345 kV West Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3792 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3696 and Patent Gate 345 kV breakers 1892 and 1896 16 cycles: Trip Charlie Creek 345 kV breakers 3992 and 4192 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F88 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Patent Gate 345 kV line, and opening the Charlie Creek to Roundup 345 kV line. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3696 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3792 and Patent Gate 345 kV breakers 1892 and 1896 16 cycles: Trip Charlie Creek 345 kV breaker 3692 and Roundup 345 kV breakers 892 and 896 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F89 | Apply SLG ault near Charlie Creek 230 kV with stuck breaker, cleared by opening Charlie Creek 345/230 kV Transormers #1 and #2, and opening the Charlie Creek to Watord City 230 kV line. | Apply SLG ault near Charlie Creek 230 kV with Charlie Creek 230 kV breaker 382 stuck 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4092 7 cycles: Trip Charlie Creek 230 kV breaker 282 16 cycles: Trip Watord City 230 kV breakers 682 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F90 | Apply SLG ault near Charlie Creek 230 kV with stuck breaker, cleared by opening Charlie Creek 345/230 kV Transormers #1 and #2, and opening the Charlie Creek to Watord City 230 kV line. | Apply SLG ault near Charlie Creek 230 kV with Charlie Creek 230 kV breaker 282 stuck 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4092 7 cycles: Trip Charlie Creek 230 kV breaker 382 16 cycles: Trip Watord City 230 kV breakers 682 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F91 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Belield 345 kV line, and tripping the Charlie Creek 345 kV West Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 4192 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 4096 and Belield 345 kV breakers 396 and 492 16 cycles: Trip Charlie Creek 345 kV breakers 3792 and 3992 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F92 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Belield 345 kV line, and opening the Charlie Creek 345/230 kV Transormer #1. opening the Charlie Creek 345/230 kV Transormer #2. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 4096 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 4192 and Belield 345 kV breakers 396 and 492 16 cycles: Trip Charlie Creek 345 kV breaker 4092 and Charlie Creek 230 kV breakers 282 and 382 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F93 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Antelope Valley 345 kV line, and tripping the Charlie Creek 345 kV East Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3892 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3896 and Antelope Valley 345 kV breakers 4796 and 4892 16 cycles: Trip Charlie Creek 345 kV breakers 3692 and 4092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F94 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Antelope Valley 345 kV line, and opening the Charlie Creek 345/115 kV Transormer #1. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3896 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3892 and Antelope Valley 345 kV breakers 4796 and 4892 16 cycles: Trip Charlie Creek 345 kV breaker 3992 and Charlie Creek 115 kV breaker 962 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F95 | Prior Outage o Watord City to Williston Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F96 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F97 | Prior Outage o Watord City to Williston Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Prior Outage o Watord City to Williston Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F98 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F99 | Prior Outage o Watord City to Williston Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F100 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F101 | Prior Outage o Watord City to Williston Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F102 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F103 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F104 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Sensitivity | F105 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F106 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F107 | Prior Outage o Watord City to Williston Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F108 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F109 | Prior Outage o Watord City to Williston Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F110 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F111 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 230 kV on Watord City to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 230 kV on Watord City to Williston 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 27 cycles: Reclose Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 34 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F112 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 27 cycles: Reclose Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 34 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F113 | Prior Outage o Watord City to Williston Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F114 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F115 | Prior Outage o Watord City to Williston Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F116 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F117 | Prior Outage o Watord City to Williston Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F118 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F119 | Prior Outage o Watord City to Williston Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F120 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F121 | Prior Outage o Watord City to Williston Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Sensitivity | F122 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F123 | Prior Outage o Watord City to Williston Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P6 | Yes | Yes | No | Yes | Yes | No | Yes | Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and high voltage issue was still observed. Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 19W | Sensitivity | F124 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Sensitivity | F125 | Prior Outage o Watord City to Williston Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P6 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and high voltage issue was still observed. | No Mitigation
16 | 19W | Sensitivity | F126 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | No | GEN-2014-010IS generator tripped due to overvoltage. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. | No Mitigation
16 | 19W | Sensitivity | F127 | Prior Outage o Watord City to Williston Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F128 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F129 | Prior Outage o Watord City to Williston Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F130 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F131 | Prior Outage o Watord City to Williston Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F132 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F133 | Prior Outage o Watord City to Williston Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 19W | Sensitivity | F134 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F01 | Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F02 | Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F03 | Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F04 | Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F05 | Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F06 | Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F07 | Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F08 | Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F09 | Apply 3PH ault near Watord City 230 kV on Watord City to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 230 kV on Watord City to Williston 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 27 cycles: Reclose Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 34 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F10 | Apply 3PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 27 cycles: Reclose Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 34 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F11 | Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F12 | Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F13 | Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F14 | Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F15 | Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F16 | Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F17 | Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and high voltage issue was still observed. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F18 | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F19 | Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 6 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F20 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F21 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F22 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Mont 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Williston 2 115 kV on Williston 2 to Mont 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 27 cycles: Reclose Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 34 cycles: Trip Williston 2 115 kV breakers 2462 and 2466 and Mont 115 kV breakers 2410 and 2420 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F23 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Little Muddy 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 2 115 kV on Williston 2 to Little Muddy 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 27 cycles: Reclose Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 34 cycles: Trip Williston 2 115 kV breakers 2362 and 2466 and Little Muddy 115 kV breakers 5851 and 5882 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F24 | Apply 3PH ault near Williston 2 115 kV on Williston 2 to N.W. Williston 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 2 115 kV on Williston 2 to N.W. Williston 115 kV line 7 cycles: Trip Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 27 cycles: Reclose Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 34 cycles: Trip Williston 2 115 kV breakers 2262 and 2266 and N.W. Williston 115 kV breakers 5950 and 5960 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F25 | Apply 3PH ault near Williston 115 kV on Williston to airview West 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston115 kV on Williston to airview West 115 kV line 7 cycles: Trip Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 27 cycles: Reclose Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 34 cycles: Trip Williston 115 kV breaker 1362 and airview West 115 kV breakers 162 and 462 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F26 | Apply 3PH ault near Williston 115 kV on Williston to Judson 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Judson 115 kV line 7 cycles: Trip Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 27 cycles: Reclose Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 34 cycles: Trip Williston 115 kV breaker 1662 and Judson 115 kV breakers 5540 and 5550 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F27 | Apply 3PH ault near Judson 115 kV on Judson to Stateline 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Judson 115 kV on Judson 115 to Stateline 115 kV line 7 cycles: Trip Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 27 cycles: Reclose Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 34 cycles: Trip Judson 115 kV breakers 5510 and 5520 and Stateline 115 kV breakers 5530 and 5540 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F28 | Apply 3PH ault near Judson 115 kV on Judson to SW.WLSTN-MW7 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near Judson115 kV on Judson 115 to SW.WLSTN-MW7 115 kV line 7 cycles: Trip Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) 27 cycles: Reclose Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) 34 cycles: Trip Judson 115 kV breakers 5520, 5540 and SW.WLSTN-MW7 115 kV breaker(s) | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F29 | Apply 3PH ault near Williston 115 kV on Williston to Marley 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Marley 115 kV line 7 cycles: Trip Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) 27 cycles: Reclose Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) 34 cycles: Trip Williston 115 kV breaker 1262 and Marley 115 kV breaker(s) | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F30 | Apply 3PH ault near Williston 115 kV on Williston to Culbertson 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Williston 115 kV on Williston to Culbertson 115 kV line 7 cycles: Trip Williston 115 kV breaker 1562 and Culbertson Generatio Station 115 kV breaker 161 and Wol Point Breaker 262 27 cycles: Reclose Williston 115 kV breaker 1562 and Wol Point Breaker 262 34 cycles: Trip Williston 115 kV breaker 1562 and Wol Point Breaker 262 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F31 | Apply 3PH ault on Wheelock 230/115 kV Transormer #1, near Wheelock 230 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Wheelock 230/115 Transormer #1, near Wheelock 230 kV 7 cycles: Trip Wheelock 230 kV breakers 1486 and 1686 and Wheelock 115 kV breakers 6210 and 6260 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F32 | Apply 3PH ault near Wheelock 230 kV on Wheelock to Tioga 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3PH ault near Wheelock 230 kV on Wheelock to Tioga 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1686 and Tioga 230 kV breakers 582 and 882 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F33 | Apply 3PH ault on Patent Gate 345/115 kV Transormer #1, near Patent Gate 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Patent Gate 345/115 kV Transormer #1, near Patent Gate 345 kV or 6 cycles 6 cycles: Trip Patent Gate 345 kV breakers 1696 and 1792 7 cycles: Trip Patent Gate 115 kV breakers 166 and 262 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F34 | Apply 3PH ault on Patent Gate 345/115 kV Transormer #2, near Patent Gate 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Patent Gate 345/115 kV Transormer #2, near Patent Gate 345 kV or 6 cycles 6 cycles: Trip Patent Gate 345 kV breakers 1896 and 1992 7 cycles: Trip Patent Gate 115 kV breakers 366 and 462 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F35 | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Kummer Ridge 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Kummer Ridge 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 26 cycles: Reclose Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 32 cycles: Trip Patent Gate 345 kV breakers 1692 and 1696 and Kummer Ridge 345 kV breakers 592 and 596 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F36 | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 6 cycles 6 cycles: Trip Kummer Ridge 345 kV breakers 192 and 592 7 cycles: Trip Kummer Ridge 115 kV breakers 362 and 366 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F37 | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #2, near Kummer Ridge 345 kV or 7 cycles Clear ault by tripping the aulted transormer. | Apply 3PH ault on Kummer Ridge 345/115 kV Transormer #1, near Kummer Ridge 345 kV or 6 cycles 6 cycles: Trip Kummer Ridge 345 kV breakers 596 and 692 7 cycles: Trip Kummer Ridge 115 kV breakers 162 and 166 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F38 | Apply 3PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to GEN-2015-046 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Apply 3 PH ault near TANDE___-BE3 345 kV on TANDE to GEN-2015-046 345 kV line 6 cycles: Trip TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers 26 cycles: Reclose TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers 32 cycles: Trip TANDE___-BE3 345 kV breakers and GEN-2015-046 345 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F39 | Apply 3PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to BURKE___-PP3 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3 PH ault near TANDE___-BE3 345 kV on TANDE___-BE3 to BURKE___-PP3 345 kV line 6 cycles: Trip TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers 26 cycles: Reclose TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers 32 cycles: Trip TANDE___-BE3 345 kV breakers and BURKE___-PP3 345 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | No | No | GEN-2015-046 generators tripped due to overvoltage relay (>1,2 p.u.). The overvoltage relay setting met PRC-024-2 requirement for voltage higher than 1.2 p.u. Fault was tested with GEN-2020-014 offline and generator tripping was still observed. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F40 | Apply 3PH ault on TANDE 345/230 kV Transormer, near TANDE 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on TANDE 345/230 kV Transormer, near TANDE 345 kV 6 cycles: Trip TANDE 345 kV breakers 7 cycles: Trip TANDE 230 kV breakers | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Voltage on the 345 kV network near the TANDE substation was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and high voltage issue was still observed. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F41 | Apply 3PH ault on G15-046 345/34.5 kV Transormer #1, near G15-046 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on G15-046 345/34.5 kV Transormer #1, near G15-046 345 kV 6 cycles: Trip G15-046 345 kV breakers 7 cycles: Trip G15-046 34.5 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F42 | Apply 3PH ault on G15-046 345/34.5 kV Transormer #2, near G15-046 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on G15-046 345/34.5 kV Transormer #2, near G15-046 345 kV 6 cycles: Trip G15-046 345 kV breakers 7 cycles: Trip G15-046 34.5 kV breakers | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F43 | Apply 3PH ault on Charlie Creek 345/115 kV Transormer, near Charlie Creek 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Charlie Creek 345/115 kV Transormer, near Charlie Creek 345 kV 6 cycles: Trip Charlie Creek 345 kV breakers 3896 and 3992 7 cycles :Trip Charlie Creek 115 kV breaker 962 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F44 | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Roundup 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Roundup 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 26 cycles: Reclose Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 32 cycles: Trip Charlie Creek 345 kV breakers 3692 and 3696 and Roundup 345 kV breakers 892 and 896 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F45 | Apply 3PH ault on Belield 345/230 kV Transormer #1, near Belield 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Belield 345/230 kV Transormer #1, near Belield 345 kV 6 cycles: Trip Belield 345 kV breakers 292 and 396 7 cycles: Trip Belield 230 kV breakers 1282 and 1482 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F46 | Apply 3PH ault on Belield 345/230 kV Transormer #2, near Belield 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Belield 345/230 kV Transormer #2, near Belield 345 kV 6 cycles: Trip Belield 345 kV breakers 292 and 492 7 cycles: Trip Belield 230 kV breakers 1382 and 1582 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F47 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Roundup 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Roundup 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 26 cycles: Reclose Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 32 cycles: Trip Antelope Valley 345 kV breakers 4396 and 4492 and Roundup 345 kV breakers 492 and 496 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F48 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Coteau (RREC) 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Coteau (RREC) 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4592, Coteau breakers 27122, 2112 26 cycles: Reclose Antelope Valley 345 kV breakers 4596 and 4592 32 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4592 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F49 | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #1, near Antelope Valley 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #1, near Antelope Valley 345 kV 6 cycles: Trip Antelope Valley 345 kV breakers 4192 and 4196 7 cycles: Trip Antelope Valley 23 kV breaker | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F50 | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #2, near Antelope Valley 345 kV or 7 cycles. Clear ault by tripping the aulted transormer. | Apply 3PH ault on Antelope Valley 345/23 kV Transormer #2, near Antelope Valley 345 kV 6 cycles: Trip Antelope Valley 345 kV breakers 4392 and 4396 7 cycles: Trip Antelope Valley 23 kV breaker | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F51 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #1 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #1 6 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 7 cycles: Trip Great Plains breakers 128, 228,328, 428, 528, 628, 728 26 cycles: Reclose Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 32 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F52 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #2 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Great Plains 345 kV line #2 6 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 7 cycles: Trip Great Plains breakers 128, 228,328, 428, 528, 628, 728 26 cycles: Reclose Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 32 cycles: Trip Antelope Valley 345 kV breakers 3792, 3796, 3992 and 3996 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F53 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Broadland 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Broadland 345 kV line 6 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 26 cycles: Reclose Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 32 cycles: Trip Antelope Valley 345 kV breakers 4596 and 4692 and Broadland 345 kV breaker 192 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F54 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #1 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #1 6 cycles: Trip Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 26 cycles: Reclose Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 32 cycles: Trip Antelope Valley 345 kV breakers 3892 and 3796 and Leland Olds 345 kV breakers 2796 and 2892 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F55 | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #2 Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Apply 3PH ault near Antelope Valley 345 kV on Antelope Valley to Leland Olds 345 kV line #2 6 cycles: Trip Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 26 cycles: Reclose Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 32 cycles: Trip Antelope Valley 345 kV breakers 3996 and 4092 and Leland Olds 345 kV breakers 2196 and 2292 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F56 | Apply SLG ault near East Haybutte 115 kV with stuck breaker, cleared by opening the Lonesome Creek Switchyard to Cherry Creek 115 kV line, and opening the Lonesome Creek Switchyard to Lonesome Creek 115 kV line. | Apply SLG ault near East Haybutte 115 kV with Lonesome Creek Switchyard 115 kV breaker 1466 stuck 7 cycles: Trip Cherry Creek 115 kV breakers CB2 and CB3 and Lonesome Creek 115 kV breaker 1462 16 cycles: Trip Lonesome Creek Switchyard 115 kV breaker 1562. Trip Lonesome Creek generators 4, 5, and 6 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F57 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Roosevelt 115 kV line, and opening the Cherry Creek to Lonesome Creek Switchyard 115 kV line. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB3 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB4 16 cycles: Trip Cherry Creek 115 kV breaker CB2 and Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F58 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Roosevelt 115 kV line, and opening the Cherry Creek 25 kV load. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB4 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB3 16 cycles: Trip Cherry Creek 115 kV breaker CB1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F59 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Watord City 115 kV line, and opening the Cherry Creek to Lonesome Creek Switchyard 115 kV line. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB2 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB1 and Watord City 115 kV breakers 1362 and 1462 16 cycles: Trip Cherry Creek 115 kV breaker CB3 and Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F60 | Apply SLG ault near Cherry Creek 115 kV with stuck breaker, cleared by opening the Cherry Creek to Watord City 115 kV line, and opening the Cherry Creek 25 kV load. | Apply SLG ault near Cherry Creek 115 kV with Cherry Creek 115 kV breaker CB1 stuck 7 cycles: Trip Cherry Creek 115 kV breaker CB2 and Watord City 115 kV breakers 1362 and 1462 16 cycles: Trip Cherry Creek 115 kV breaker CB4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F61 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Coyote Charlie 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. opening the Watord City to Oasis 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1162 stuck 7 cycles: Trip Watord City 115 kV breaker 1262, Coyote Charlie 115 kV breakers 16 cycles: Trip Watord City 115 kV breakers 1062 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F62 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Coyote Charlie 115 kV line, and opening the Watord City 34.5 kV load. opening the Watord City 115 kV 15 MVAR Cap Bank. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1262 stuck 7 cycles: Trip Watord City 115 kV breaker 1162, Coyote Charlie 115 kV breakers 16 cycles: Trip Watord City 115 kV breaker 1362 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F63 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Garden Creek 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1062 stuck 7 cycles: Trip Watord City 115 kV breaker 1562, Garden Creek 115 kV breakers 16 cycles: Trip Watord City 115 kV breakers 1162 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F64 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City to Garden Creek 115 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. opening the Watord City 115 kV 15 MVAR Cap Bank. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1562 stuck 7 cycles: Trip Watord City 115 kV breaker 1062, Garden Creek 115 kV breakers 16 cycles: Trip Watord City 115 kV breaker 1462 and 230 kV breakers 782 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F65 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #1, and opening the Watord City 230/115 kV Transormer #2 opening the Watord City 115 kV 15 MVAR Cap Bank. opening the Watord City to Garden Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1062 stuck 7 cycles: Trip Watord City 115 kV breaker 1162 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breakers 1562, Garden Creek 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F66 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #1, and opening the Watord City 230/115 kV Transormer #2. opening the Watord City to Coyote Charlie 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1162 stuck 7 cycles: Trip Watord City 115 kV breakers 1062 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1262, Coyote Charlie 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F67 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #2, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City to Cherry Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1462 stuck 7 cycles: Trip Watord City 115 kV breakers 1562 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1362 and Cherry Creek 115 kV breakers CB1 and CB2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F68 | Apply SLG ault near Watord City 115 kV with stuck breaker, cleared by opening the Watord City 230/115 kV Transormer #2, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City to Garden Creek 115 kV line. | Apply SLG ault near Watord City 115 kV with Watord City 115 kV breaker 1562 stuck 7 cycles: Trip Watord City 115 kV breaker 1462 and Watord City 230 kV breakers 782 and 882 16 cycles: Trip Watord City 115 kV breaker 1062 , Garden Creek 115 kV breakers | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F69 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Williston 230 kV line | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 682 stuck 7 cycles: Trip Watord City 230 kV breaker 782 and Williston 230 kV breakers 382 and 486 16 cycles: Trip Watord City 230 kV breaker 982 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F70 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Williston 230 kV line, and opening the Watord City 230/115 kV Transormer #1. opening the Watord City 230/115 kV Transormer #2. | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 782 stuck 7 cycles: Trip Watord City 230 kV breaker 682 and Williston 230 kV breakers 382 and 486 16 cycles: Trip Watord City 230 kV breaker 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F71 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Charlie Creek 230 kV line | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 982 stuck 7 cycles: Trip Watord City 230 kV breaker 882 and Charlie Creek 230 kV breakers 282 and 382 16 cycles: Trip Watord City 230 kV breaker 682 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F72 | Apply SLG ault near Watord City 230 kV with stuck breaker, cleared by opening the Watord City to Charlie Creek 230 kV line, and opening the Watord City 230/115 kV Transormer #1 opening the Watord City 230/115 kV Transormer #2 | Apply SLG ault near Watord City 230 kV with Watord City 230 kV breaker 882 stuck 7 cycles: Trip Watord City 230 kV breaker 982 and Charlie Creek 230 kV breakers 282 and 382 16 cycles: Trip Watord City 230 kV breaker 782 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F73 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #1, and tripping the Williston 230 kV East Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 182 stuck 7 cycles: Trip Williston 230 kV breaker 286 and Williston 115 kV breakers 2162 and 2266 16 cycles: Trip Williston 230 kV breaker 382 and 582 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F74 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #1, and opening the Williston to Judson 230 kV line. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 286 stuck 7 cycles: Trip Williston 230 kV breaker 182 and Williston 115 kV breakers 2162 and 2266 16 cycles: Trip Williston 230 kV breaker 282 and Judson breakers 1082 and 1182 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F75 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #2, and tripping the Williston 230 kV West Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 482 stuck 7 cycles: Trip Williston 230 kV breaker 486 and Williston 115 kV breaker 1762 16 cycles: Trip Williston 230 kV breakers 282 and 686 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F76 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Williston 230/115 kV Transormer #2, and opening the Williston to Watord City 230 kV line. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 486 stuck 7 cycles: Trip Williston 230 kV breaker 482 and Williston 115 kV breaker 1762 16 cycles: Trip Williston 230 kV breaker 382 and Watord City 230 kV breakers 682 and 782 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F77 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Judson 230 kV line, and tripping the Williston 230 kV West Bus | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 282 stuck 7 cycles: Trip Williston 230 kV breaker 286 and Judson 230 kV breakers 1082 and 1182 16 cycles: Trip Williston 230 kV breakers 482 and 686 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F78 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Judson 230 kV line, and opening the Williston 230/115 kV Transormer #1 | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 286 stuck 7 cycles: Trip Williston 230 kV breaker 282 and Judson 230 kV breakers 1082 and 1182 16 cycles: Trip Williston 230 kV breaker 182 and Williston 115 kV breakers 2162 and 2266 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F79 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Wheelock 230 kV line, and tripping the Williston 230 kV East Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 582 stuck 7 cycles: Trip Williston 230 kV breaker 686 and Wheelock 230 kV breakers 1482 and 1486 16 cycles: Trip Williston 230 kV breakers 382 and 182 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F80 | Apply SLG ault near Williston 230 kV with stuck breaker, cleared by opening the Willston to Wheelock 230 kV line, and tripping the Williston 230 kV West Bus. | Apply SLG ault near Williston 230 kV with Williston 230 kV breaker 686 stuck 7 cycles: Trip Williston 230 kV breaker 582 and Wheelock 230 kV breakers 1482 and 1486 16 cycles: Trip Williston 230 kV breakers 482 and 282 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F81 | Apply SLG ault near Judson 230 kV with stuck breaker, cleared by opening the Judson 230/345 kV Transormer #1, and opening the Judson to Williston 230 kV line. | Apply SLG ault near Judson 230 kV with Judson 230 kV breaker 1082 stuck 6 cycles: Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breaker 1282 16 cycles: Trip Judson 230 kV breaker 1182 and Williston 230 kV breakers 282 and 286 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F82 | Apply SLG ault near Judson 230 kV with stuck breaker, cleared by opening the Judson 230/345 kV Transormer #1, and opening the Judson to Williston 230 kV line. | Apply SLG ault near Judson 230 kV with Judson 230 kV breaker 1282 stuck 6 cycles: Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breaker 1082 16 cycles: Trip Judson 230 kV breaker 1382 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F83 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to Patent Gate 345 kV line #1, and tripping the Judson 345 kV West Bus | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 496 stuck 6 cycles: Trip Judson 345 kV breaker 492 and Patent Gate 345 kV breakers 1492 and 1496 16 cycles: Trip Judson 345 kV breakers 592 and 192 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F84 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to Patent Gate 345 kV line #1, and tripping the Judson 345 kV East Bus | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 492 stuck 6 cycles: Trip Judson 345 kV breaker 496 and Patent Gate 345 kV breakers 1492 and 1496 16 cycles: Trip Judson 345 kV breakers 692 and 292 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F85 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to TN.LS-JD-BE3 345 kV line, and tripping the Judson 345kV East Bus. | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 292 stuck 6 cycles: Trip Judson 345 kV breaker 296 and TANDE 345 kV breakers 16 cycles: Trip Judson 345 kV breakers 492 and 692 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F86 | Apply SLG ault near Judson 345 kV with stuck breaker, cleared by opening the Judson to TN.LS-JD-BE3 345 kV line | Apply SLG ault near Judson 345 kV with Judson 345 kV breaker 296 stuck 6 cycles: Trip Judson 345 kV breaker 292 and TANDE 345 kV breakers 16 cycles: Trip Judson 345 kV breaker 192 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F87 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Patent Gate 345 kV line, and tripping the Charlie Creek 345 kV West Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3792 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3696 and Patent Gate 345 kV breakers 1892 and 1896 16 cycles: Trip Charlie Creek 345 kV breakers 3992 and 4192 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F88 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Patent Gate 345 kV line, and opening the Charlie Creek to Roundup 345 kV line. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3696 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3792 and Patent Gate 345 kV breakers 1892 and 1896 16 cycles: Trip Charlie Creek 345 kV breaker 3692 and Roundup 345 kV breakers 892 and 896 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F89 | Apply SLG ault near Charlie Creek 230 kV with stuck breaker, cleared by opening Charlie Creek 345/230 kV Transormers #1 and #2, and opening the Charlie Creek to Watord City 230 kV line. | Apply SLG ault near Charlie Creek 230 kV with Charlie Creek 230 kV breaker 382 stuck 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4092 7 cycles: Trip Charlie Creek 230 kV breaker 282 16 cycles: Trip Watord City 230 kV breakers 682 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F90 | Apply SLG ault near Charlie Creek 230 kV with stuck breaker, cleared by opening Charlie Creek 345/230 kV Transormers #1 and #2, and opening the Charlie Creek to Watord City 230 kV line. | Apply SLG ault near Charlie Creek 230 kV with Charlie Creek 230 kV breaker 282 stuck 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4092 7 cycles: Trip Charlie Creek 230 kV breaker 382 16 cycles: Trip Watord City 230 kV breakers 682 and 882 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F91 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Belield 345 kV line, and tripping the Charlie Creek 345 kV West Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 4192 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 4096 and Belield 345 kV breakers 396 and 492 16 cycles: Trip Charlie Creek 345 kV breakers 3792 and 3992 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F92 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Belield 345 kV line, and opening the Charlie Creek 345/230 kV Transormer #1. opening the Charlie Creek 345/230 kV Transormer #2. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 4096 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 4192 and Belield 345 kV breakers 396 and 492 16 cycles: Trip Charlie Creek 345 kV breaker 4092 and Charlie Creek 230 kV breakers 282 and 382 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F93 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Antelope Valley 345 kV line, and tripping the Charlie Creek 345 kV East Bus. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3892 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3896 and Antelope Valley 345 kV breakers 4796 and 4892 16 cycles: Trip Charlie Creek 345 kV breakers 3692 and 4092 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F94 | Apply SLG ault near Charlie Creek 345 kV with stuck breaker, cleared by opening the Charlie Creek to Antelope Valley 345 kV line, and opening the Charlie Creek 345/115 kV Transormer #1. | Apply SLG ault near Charlie Creek 345 kV with Charlie Creek 345 kV breaker 3896 stuck 6 cycles: Trip Charlie Creek 345 kV breaker 3892 and Antelope Valley 345 kV breakers 4796 and 4892 16 cycles: Trip Charlie Creek 345 kV breaker 3992 and Charlie Creek 115 kV breaker 962 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F95 | Prior Outage o Watord City to Williston Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F96 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Lonesome Creek 115 kV on Lonesome Creek to Lonesome Creek Switchyard 115 kV line 7 cycles: Trip Lonesome Creek 115 kV breakers and Lonesome Creek Switchyard 115 kV breaker 1466, 1562 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1466, 1562 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1466, 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F97 | Prior Outage o Watord City to Williston Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Prior Outage o Watord City to Williston Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F98 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near East Haybutte 115 kV on East Haybutte to Cherry Creek 115 kV line 7 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 27 cycles: Reclose Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 34 cycles: Trip Lonesome Creek Switchyard 115 kV breakers 1462 and 1466 and Cherry Creek 115 kV breakers CB2 and CB3 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F99 | Prior Outage o Watord City to Williston Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F100 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Roosevelt 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 27 cycles: Reclose Cherry Creek 115 kV breakers CB3 and CB4 34 cycles: Trip Cherry Creek 115 kV breakers CB3 and CB4 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F101 | Prior Outage o Watord City to Williston Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F102 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Cherry Creek 115 kV on Cherry Creek to Watord City 115 kV line 7 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 27 cycles: Reclose Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 34 cycles: Trip Cherry Creek 115 kV breakers CB1 and CB2 and Watord City 115 kV breakers 1362 and 1462 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F103 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F104 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 115 kV on Watord City to Coyote Charlie 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1162 and 1262, Coyote Charlie 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1162 and 1262, Coyote Charlie115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F105 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F106 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 115 kV on Watord City to Garden Creek 115 kV line 7 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 27 cycles: Reclose Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers 34 cycles: Trip Watord City 115 kV breakers 1062 and 1562, Garden Creek 115 kV breakers | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F107 | Prior Outage o Watord City to Williston Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F108 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Watord City 230/115 kV Transormer #1, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F109 | Prior Outage o Watord City to Williston Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F110 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Watord City 230/115 kV Transormer #2, near Watord City 115 kV or 7 cycles 7 cycles: Trip Watord City 230 kV breakers 782 and 882 and 115 kV breakers 1062, 1162, 1462, and 1562 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F111 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Watord City 230 kV on Watord City to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Watord City 230 kV on Watord City to Williston 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 27 cycles: Reclose Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 34 cycles: Trip Watord City 230 kV breakers 682 and 782 and Williston 230 kV breakers 382 and 486 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F112 | Prior Outage o Watord City to Williston Apply 3PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Watord City 230 kV on Watord City to Charlie Creek 230 kV line 7 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 27 cycles: Reclose Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 34 cycles: Trip Watord City 230 kV breakers 682 and 882 and Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F113 | Prior Outage o Watord City to Williston Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F114 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Williston 230/115 kV Transormer #1, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 182 and 286 and 115 kV breakers 2162 and 2266 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F115 | Prior Outage o Watord City to Williston Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F116 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Williston 230/115 kV Transormer #2, near Williston 230 kV or 7 cycles 7 cycles: Trip Williston 230 kV breakers 482 and 486 and 115 kV breaker 1762 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F117 | Prior Outage o Watord City to Williston Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F118 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Williston 230 kV on Williston to Judson 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Williston 230 kV on Williston to Judson 230 kV line 7 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 27 cycles: Reclose Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 34 cycles: Trip Williston 230 kV breakers 282 and 286 and Judson 230 kV breakers 1082 and 1182 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F119 | Prior Outage o Watord City to Williston Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F120 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Williston 230 kV on Wheelock to Williston 230 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 7 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Williston 230 kV on Wheelock to Williston 230 kV line 7 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 27 cycles: Reclose Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 34 cycles: Trip Wheelock 230 kV breakers 1482 and 1486 and Williston 230 kV breakers 582 and 686 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F121 | Prior Outage o Watord City to Williston Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F122 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 6 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Judson 345/230 kV Transormer #1, near Judson 230 kV or 7 cycles 6 cycles: Trip Judson 345 kV breakers 692 and 696 7 cycles: Trip Judson 230 kV breakers 1082 and 1282 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F123 | Prior Outage o Watord City to Williston Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P6 | Yes | Yes | No | Yes | Yes | No | Yes | Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and high voltage issue was still observed. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F124 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Judson 345 kV on Judson to Patent Gate 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Judson 345 kV on Judson - Patent Gate 345 kV line 6 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 26 cycles: Reclose Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 32 cycles: Trip Judson 345 kV breakers 492 and 496 and Patent Gate 345 kV breakers 1492 and 1496 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F125 | Prior Outage o Watord City to Williston Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P6 | Yes | Yes | No | Yes | Yes | No | Yes | Voltage on the 345 kV network near the TANDE substation was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and high voltage issue was still observed. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F126 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opn the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Judson 345 kV on TN.LS-JD-BE3 to Judson 345 kV line 6 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 26 cycles: Reclose TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 32 cycles: Trip TANDE 345 kV breaker and Judson 345 kV breakers 292 and 296 | P6 | Yes | Yes | No | Yes | Yes | No | Yes | Voltage of GEN-2015-046 345 kV bus was beyond 1.2 p.u. Fault was tested with GEN-2020-014 offline and high voltage issue was still observed. Machine angle damping analysis indicated SPPR1 and SPPR5 were not met. Visual inspection of the plots showed a well-damped response. Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F127 | Prior Outage o Watord City to Williston Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P6 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
16 | 21L | Sensitivity | F128 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-opne the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Patent Gate 345 kV on Patent Gate to Charlie Creek 345 kV line 6 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 26 cycles: Reclose Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 32 cycles: Trip Patent Gate 345 kV breakers 1892 and 1896 and Charlie Creek 345 kV breakers 3696 and 3792 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F129 | Prior Outage o Watord City to Williston Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F130 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles Clear ault by tripping the aulted circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault on Charlie Creek 345/230 kV Transormers #1 and #2, near Charlie Creek 230 kV or 7 cycles 6 cycles: Trip Charlie Creek 345 kV breakers 4092 and 4096 7 cycles: Trip Charlie Creek 230 kV breakers 282 and 382 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F131 | Prior Outage o Watord City to Williston Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F132 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Belield 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 26 cycles: Reclose Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 32 cycles: Trip Charlie Creek 345 kV breakers 4096 and 4192 and Belield 345 kV breakers 396 and 492 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F133 | Prior Outage o Watord City to Williston Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Williston Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation
16 | 21L | Sensitivity | F134 | Prior Outage o Watord City to Charlie Creek Apply 3PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line Clear ault by tripping the aulted circuit. Wait 20 cycles. Re-close the aulted line or 6 cycles then re-open the circuit. | Prior Outage o Watord City to Charlie Creek Apply 3 PH ault near Charlie Creek 345 kV on Charlie Creek to Antelope Valley 345 kV line 6 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 26 cycles: Reclose Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 32 cycles: Trip Charlie Creek 345 kV breakers 3892 and 3896 and Antelope Valley 345 kV breakers 4796 and 4892 | P6 | Yes | Yes | Yes | Yes | Yes | No | Yes | Modal analysis on machine power outputs indicated damping ratio below 0.81633%. Visual inspection of the plots showed a well-damped response. | No Mitigation

## Short Circuit Analysis
Group | Scenario | Season | Model Dispatch | Gen Number | Bus Number | Bus Name | Bus Voltage (kV) | Control Area | Request Not In Service 28S Fault Current 3-Phase (A) | Request In Service 28S Fault Current 3-Phase (A) | Change in Fault Current (A) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect | Case Summary:
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659154 | LC_CT4-5-BE7 | 115 | WAPA | 4954.8 | 6376.7 | 1421.9 |  |  | See Requests Sheet
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659346 | LC_SWY.S-BE7 | 115 | WAPA | 4958.8 | 6358.8 | 1400
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655887 | E.HAY_BT-MK7 | 115 | WAPA | 5008.3 | 6244.5 | 1236.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655841 | ARNEGARD-MK7 | 115 | WAPA | 5800.4 | 6540.5 | 740.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 652408 | WATFORD7 | 115 | WAPA | 7235.1 | 7782.1 | 547 |  |  | PSS(R)E-33.12.2 ASCC SHORT CIRCUIT CURRENTS TUE, AUG 31 2021 14:42
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655840 | CHRRYCRK-MK7 | 115 | WAPA | 7235.1 | 7782.1 | 547 |  |  | 2018 MDWG FINAL PF WITH 2017 MMWG FINAL (DIS1701)
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655897 | COYOTCHR-MK7 | 115 | WAPA | 5225.7 | 5504 | 278.3 |  |  | MDWG 2028S WITH MMWG 2027S. CEII DATA - DO NOT RELE; RED DYN
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655880 | SCHAFR_T-MK7 | 115 | WAPA | 4821.6 | 5057.4 | 235.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655855 | ROOSEVLT-MK7 | 115 | WAPA | 4804.6 | 5038.6 | 234 |  |  | OPTIONS USED:
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 652216 | WATFORD4 | 230 | WAPA | 6101.2 | 6306.3 | 205.1 |  |  | - SET PRE-FAULT VOLTAGE ON ALL BUSES TO 1.00 PU AT 0 PHASE SHIFT ANGLE
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655899 | FNCYBTAP-MK7 | 115 | WAPA | 4441.8 | 4641 | 199.2 |  |  | - SET SYNCHRONOUS/ASYNCHRONOUS MACHINE POWER OUTPUTS TO P=0.0, Q=0.0
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655898 | SCHAFER -MK7 | 115 | WAPA | 4287.7 | 4472.4 | 184.7 |  |  | - SET GENERATOR POSITIVE SEQUENCE REACTANCES TO SUBTRANSIENT
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655879 | OASIS___-MK7 | 115 | WAPA | 4193.8 | 4368.5 | 174.7 |  |  | - SET TRANSFORMER TAP RATIOS=1.0 PU AND PHASE SHIFT ANGLES=0.0
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655845 | GRDNCRK2-MK7 | 115 | WAPA | 4102.4 | 4269.3 | 166.9 |  |  | - SET LINE CHARGING=0.0 IN +/-/0 SEQUENCES
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655895 | GARDN-FB-MK7 | 115 | WAPA | 3803.5 | 3946.5 | 143 |  |  | - SET LINE/FIXED/SWITCHED SHUNTS=0.0 AND TRANSFORMER MAGNETIZING ADMITTANCE=0.0 IN +/-/0 SEQUENCES
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659302 | CHARL_CK-BE4 | 230 | WAPA | 10632.9 | 10725 | 92.1 |  |  | - SET LOAD=0.0 IN +/- SEQUENCES
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 652400 | WILISTN4 | 230 | WAPA | 9399.4 | 9471.6 | 72.2 |  |  | - DC LINES AND FACTS DEVICES BLOCKED
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659334 | JUDSON__-BE4 | 230 | WAPA | 9282.2 | 9348.1 | 65.9 |  |  | - IMPEDANCE CORRECTIONS NOT APPLIED TO TRANSFORMER ZERO SEQUENCE IMPEDANCES
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659183 | CHARL_CK-BE3 | 345 | WAPA | 9723.5 | 9788.1 | 64.6
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 652391 | WILLISTON27 | 115 | WAPA | 15557.3 | 15606.2 | 48.9
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 652421 | WILISTN7 | 115 | WAPA | 15561.9 | 15610.7 | 48.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659391 | PATENTGT-MK7 | 115 | WAPA | 15136.6 | 15180.6 | 44
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659466 | PG.KU17A-BE7 | 115 | WAPA | 15042.6 | 15086.4 | 43.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659467 | PG.KU19A-BE7 | 115 | WAPA | 15053.6 | 15097.4 | 43.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659333 | JUDSON__-BE3 | 345 | WAPA | 6526.8 | 6563.5 | 36.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659182 | CHARL_CK-BE7 | 115 | WAPA | 13164.8 | 13199.2 | 34.4
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659390 | PATENTGT-BE3 | 345 | WAPA | 6720 | 6751.1 | 31.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655925 | JUDSON -MW7 | 115 | WAPA | 12824.9 | 12855.1 | 30.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655833 | GRSYBTTP-MK7 | 115 | WAPA | 12302.1 | 12332.1 | 30
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659384 | ROUNDUP_-BE3 | 345 | WAPA | 7983.3 | 8011.4 | 28.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659101 | ANTELOPE-BE3 | 345 | WAPA | 16125.5 | 16151.3 | 25.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659218 | COTEAU__-RR3 | 345 | WAPA | 16125.5 | 16151.3 | 25.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659420 | AV.LS-BD-BE3 | 345 | WAPA | 16125.5 | 16151.3 | 25.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659212 | DGC_____-BE3 | 345 | WAPA | 15382.1 | 15405.6 | 23.5
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 661084 | TIOGA4 4 | 230 | WAPA | 8461.6 | 8482.3 | 20.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659138 | NESET___-BE4 | 230 | WAPA | 8461.6 | 8482.3 | 20.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659337 | TANDE___-BE4 | 230 | WAPA | 8365.8 | 8386.2 | 20.4
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659362 | WHEELOCK-BE4 | 230 | WAPA | 6328.2 | 6347 | 18.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659388 | KUMMERDG-MK7 | 115 | WAPA | 8950.7 | 8969.1 | 18.4
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655940 | MONT -MW7 | 115 | WAPA | 11256.5 | 11274.6 | 18.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659385 | ROUNDUP_-MK7 | 115 | WAPA | 10664.4 | 10681.1 | 16.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659349 | LC_SWY.N-BE7 | 115 | WAPA | 11454.1 | 11470.7 | 16.6
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 652424 | BELFELD3 | 345 | WAPA | 6204.5 | 6221.1 | 16.6
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659348 | LC_CT1-3-BE7 | 115 | WAPA | 11454 | 11470.6 | 16.6
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 588874 | G17-048-TAP | 230 | WAPA | 6406.4 | 6422.4 | 16
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 652425 | BELFELD4 | 230 | WAPA | 8609.5 | 8624.4 | 14.9
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659309 | S.HEART_-RR4 | 230 | WAPA | 8609.5 | 8624.4 | 14.9
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655935 | NW.WLSTN-MW7 | 115 | WAPA | 8981 | 8995.5 | 14.5
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655924 | STATELIN-MW7 | 115 | WAPA | 12853.3 | 12867.6 | 14.3
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659347 | PIONEER1-BE7 | 115 | WAPA | 12853.3 | 12867.6 | 14.3
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655934 | N.WLST_T-MW7 | 115 | WAPA | 9010.7 | 9024.7 | 14
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659427 | TN.LS-JD-BE3 | 345 | WAPA | 5423.8 | 5437.7 | 13.9
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659336 | TANDE___-BE3 | 345 | WAPA | 5423.8 | 5437.7 | 13.9
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655844 | TIMBERCK-MK7 | 115 | WAPA | 8495.6 | 8509.3 | 13.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655933 | N.MISRDG-MW7 | 115 | WAPA | 9074.4 | 9087.8 | 13.4
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655936 | N.WILSTN-MW7 | 115 | WAPA | 8763.1 | 8776.4 | 13.3
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659105 | LELAND_O-BE3 | 345 | WAPA | 16936.1 | 16948.9 | 12.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659422 | LO.LS-GR-BE3 | 345 | WAPA | 16936.1 | 16948.9 | 12.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659424 | LO.LS-FT-BE3 | 345 | WAPA | 16936.1 | 16948.9 | 12.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655842 | HAYBUTTE-MK7 | 115 | WAPA | 8179 | 8191.8 | 12.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659430 | PIONEER2-BE7 | 115 | WAPA | 12257.8 | 12270.4 | 12.6
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 587130 | GEN-2016-017 | 345 | WAPA | 16881 | 16893.6 | 12.6
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655882 | GALAXYTP-MK7 | 115 | WAPA | 7388.8 | 7401.3 | 12.5
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659139 | NESET___-BE7 | 115 | WAPA | 9790.1 | 9802.5 | 12.4
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655889 | LC_GAS_P-MK7 | 115 | WAPA | 7939.1 | 7951.1 | 12
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 661085 | TIOGA4 7 | 115 | MDU | 9469.9 | 9481.8 | 11.9
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659106 | LELAND_O-BE4 | 230 | WAPA | 23018.4 | 23030.3 | 11.9
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659363 | WHEELOCK-BE7 | 115 | WAPA | 7659.2 | 7670.2 | 11
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655892 | ALEXANDR-MK7 | 115 | WAPA | 7600.4 | 7611.4 | 11
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655926 | SW.WLSTN-MW7 | 115 | WAPA | 7678.1 | 7688.8 | 10.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659404 | BURKE___-PP3 | 345 | WAPA | 4755.2 | 4765.6 | 10.4
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659387 | KUMMERDG-BE3 | 345 | WAPA | 3888.5 | 3898.9 | 10.4
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655945 | WHEELS_T-MW7 | 115 | WAPA | 7470.8 | 7480.9 | 10.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659199 | BASIN___-BE4 | 230 | WAPA | 20875.5 | 20885.2 | 9.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655835 | LITTLKNF-MK7 | 115 | WAPA | 6754 | 6763 | 9
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 584870 | GEN-2015-046 | 345 | WAPA | 4412.9 | 4421.5 | 8.6
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655856 | STNJOHNY-MK7 | 115 | WAPA | 6573.1 | 6581.3 | 8.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 661086 | TIOGA7 7 | 115 | MDU | 7839.6 | 7847.8 | 8.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655959 | EPPING -MW7 | 115 | WAPA | 6695.7 | 6703.8 | 8.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655834 | GRASSYBT-MK7 | 115 | WAPA | 6406.7 | 6414.8 | 8.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655853 | BEARCREK-MK7 | 115 | WAPA | 7258.8 | 7266.5 | 7.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 661089 | LTLMUDY7 | 115 | MDU | 6283.3 | 6290.3 | 7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 587750 | GEN-2016-092 | 345 | 0 | 12678.2 | 12685.2 | 7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655838 | INDIANHL-MK7 | 115 | WAPA | 5839.8 | 5846.2 | 6.4
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655943 | FARMVL_T-MW7 | 115 | WAPA | 6211.6 | 6217.8 | 6.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655793 | MARLEY -LY7 | 115 | WAPA | 5473.7 | 5479.6 | 5.9
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655956 | TYRONE -MW7 | 115 | WAPA | 5846.8 | 5852.6 | 5.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659124 | DICKINSN-BE4 | 230 | WAPA | 6445.3 | 6451.1 | 5.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 588210 | GEN-2016-130 | 345 | WAPA | 11445 | 11450.7 | 5.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659448 | DAGLUM__-BE4 | 230 | WAPA | 5997.3 | 6002.8 | 5.5
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655863 | CARTWRIT-MK7 | 115 | WAPA | 5175.8 | 5180.9 | 5.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659143 | BLAISDEL-BE4 | 230 | WAPA | 5038.5 | 5042.6 | 4.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655954 | ELLISVIL-MW7 | 115 | WAPA | 4796.3 | 4800.4 | 4.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655955 | ZAHL -MW7 | 115 | WAPA | 4785.4 | 4789.4 | 4
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 661087 | RAY JCT7 | 115 | MDU | 5083.5 | 5087.3 | 3.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659247 | MEDORA__-UM4 | 230 | WAPA | 4781.8 | 4785.6 | 3.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655836 | OAKDALE -MK7 | 115 | WAPA | 4942.3 | 4945.8 | 3.5
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659233 | DGC_____-BE4 | 230 | WAPA | 6973.5 | 6976.8 | 3.3
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655941 | STRNDAHL-MW7 | 115 | WAPA | 5007.8 | 5011 | 3.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655846 | F9______-MK7 | 115 | WAPA | 4066.3 | 4069.5 | 3.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655862 | G4______-MK7 | 115 | WAPA | 4046.4 | 4049.5 | 3.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655893 | DUNNCNTR-MK7 | 115 | WAPA | 4642.3 | 4645.4 | 3.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659184 | ROUGHRDR-BE7 | 115 | WAPA | 4143.8 | 4146.5 | 2.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 652419 | KILDEER7 | 115 | WAPA | 4841.6 | 4844.2 | 2.6
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659185 | FOUREYES-RR7 | 115 | WAPA | 3535.7 | 3538.2 | 2.5
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655891 | KILLDEER-MK7 | 115 | WAPA | 4683.6 | 4686 | 2.4
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655888 | BANKS -MK7 | 115 | WAPA | 3347.1 | 3349.3 | 2.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 652651 | FAIRVIEW 7 | 115 | WAPA | 4553.3 | 4555.5 | 2.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659151 | RICHLAND-BE7 | 115 | WAPA | 5034.8 | 5036.8 | 2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659108 | LOGAN___-BE4 | 230 | WAPA | 5333.7 | 5335.6 | 1.9
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655790 | HELMUT -LY7 | 115 | WAPA | 5002.3 | 5004.2 | 1.9
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 672603 | BDV 4 | 230 | SPC | 4184.9 | 4186.7 | 1.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 652456 | WASHBRN4 | 230 | WAPA | 9963.1 | 9964.9 | 1.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655915 | BARRBUTE-MW7 | 115 | WAPA | 3777.2 | 3778.9 | 1.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 661056 | LEWIS 7 | 115 | MDU | 5014.1 | 5015.8 | 1.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659222 | COTEAU_1-RR8 | 69 | WAPA | 9223.7 | 9225.4 | 1.7
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659262 | CULBSN.E-BE7 | 115 | WAPA | 5568.2 | 5569.7 | 1.5
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659186 | E.SIDNEY-LY7 | 115 | WAPA | 3871 | 3872.3 | 1.3
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659181 | BICNTNIL-BE7 | 115 | WAPA | 3203.1 | 3204.4 | 1.3
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659269 | CULB_GEN-BE7 | 115 | WAPA | 5497.4 | 5498.6 | 1.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 652441 | GARRISN4 | 230 | WAPA | 11555.4 | 11556.6 | 1.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655792 | NOHLEY -LY7 | 115 | WAPA | 3276.4 | 3277.6 | 1.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655894 | HALLIDAY-MK7 | 115 | WAPA | 2890.9 | 2892.1 | 1.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655896 | KEENECRN-MK7 | 115 | WAPA | 2409.2 | 2410.3 | 1.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655867 | TWNVLYTP-MK7 | 115 | WAPA | 2395.8 | 2396.9 | 1.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659191 | SQUAWGAP-BE7 | 115 | WAPA | 3173.5 | 3174.6 | 1.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 587030 | GEN-2016-004 | 230 | WAPA | 7374.8 | 7375.9 | 1.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659236 | DGC UREA-BE8 | 69 | WAPA | 6949.7 | 6950.7 | 1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659248 | HALLIDAY-UM7 | 115 | WAPA | 3990.9 | 3991.8 | 0.9
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659112 | CULBRTSN-UM7 | 115 | WAPA | 4263.3 | 4264.1 | 0.8
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 615901 | GRE-STANTON4 | 230 | GRE | 17238.8 | 17239.4 | 0.6
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655839 | SATHERDM-MK7 | 115 | WAPA | 2183.2 | 2183.7 | 0.5
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659306 | S.HEART_-RR7 | 115 | WAPA | 2181.1 | 2181.6 | 0.5
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655791 | SPRINGLK-LY7 | 115 | WAPA | 1851.7 | 1852 | 0.3
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659205 | BROADLND-BE4 | 230 | WAPA | 9715.5 | 9715.8 | 0.3
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 655843 | TRUEOIL -MK7 | 115 | WAPA | 1533.2 | 1533.4 | 0.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 661075 | POPLAR 7 | 115 | WAPA | 2620.3 | 2620.5 | 0.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659421 | BD.LS-AV-BE3 | 345 | WAPA | 3980.5 | 3980.7 | 0.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659120 | BROADLND-BE3 | 345 | WAPA | 3980.5 | 3980.7 | 0.2
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 659423 | GR.LS-LO-BE3 | 345 | WAPA | 5825.4 | 5825.5 | 0.1
16 | Scenario 1 | 28S | Normal | GEN_2020-014 | 652806 | FTTHOM1-LNX3 | 345 | WAPA | 8008.6 | 8008.7 | 0.1